## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-4_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-4_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-4_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-4_0_5_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_1054-4_0_5_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_1054-4_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1054-4_0_5_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1054-4_0_5_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_1054-4_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1054-4_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1054-4_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1054-4_0_5_node_3 | 0.4 | n |  | TRUE
12 | bus_LV_1054-4_0_5_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_1054-4_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1054-4_0_5_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1054-4_0_5_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1054-4_0_5_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1054-4_0_5_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1054-4_0_5_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1054-4_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1054-4_0_5_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1054-4_0_5_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1054-4_0_5_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_1054-4_0_5_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1054-4_0_5_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1054-4_0_5_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_1054-4_0_5_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_1054-4_0_5_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1054-4_0_5_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_1054-4_0_5_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_1054-4_0_5_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_1054-4_0_5_node_121 | 0.4 | n |  | TRUE
32 | bus_LV_1054-4_0_5_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_1054-4_0_5_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1054-4_0_5_node_65 | 0.4 | n |  | TRUE
35 | bus_LV_1054-4_0_5_node_12 | 0.4 | n |  | TRUE
36 | bus_LV_1054-4_0_5_node_13 | 0.4 | n |  | TRUE
37 | bus_LV_1054-4_0_5_node_14 | 0.4 | n |  | TRUE
38 | bus_LV_1054-4_0_5_node_10 | 0.4 | n |  | TRUE
39 | bus_LV_1054-4_0_5_node_11 | 0.4 | n |  | TRUE
40 | bus_LV_1054-4_0_5_node_15 | 0.4 | n |  | TRUE
41 | bus_LV_1054-4_0_5_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_1054-4_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_1054-4_0_5_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_1054-4_0_5_node_106 | 0.4 | n |  | TRUE
45 | bus_LV_1054-4_0_5_node_73 | 0.4 | n |  | TRUE
46 | bus_LV_1054-4_0_5_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_1054-4_0_5_node_107 | 0.4 | n |  | TRUE
48 | bus_LV_1054-4_0_5_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_1054-4_0_5_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_1054-4_0_5_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1054-4_0_5_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_1054-4_0_5_node_63 | 0.4 | n |  | TRUE
53 | bus_LV_1054-4_0_5_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_1054-4_0_5_node_117 | 0.4 | n |  | TRUE
55 | bus_LV_1054-4_0_5_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_1054-4_0_5_node_61 | 0.4 | n |  | TRUE
57 | bus_LV_1054-4_0_5_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_1054-4_0_5_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_1054-4_0_5_node_71 | 0.4 | n |  | TRUE
60 | bus_LV_1054-4_0_5_node_118 | 0.4 | n |  | TRUE
61 | bus_LV_1054-4_0_5_node_119 | 0.4 | n |  | TRUE
62 | bus_LV_1054-4_0_5_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1054-4_0_5_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1054-4_0_5_node_29 | 0.4 | n |  | TRUE
65 | bus_LV_1054-4_0_5_node_30 | 0.4 | n |  | TRUE
66 | bus_LV_1054-4_0_5_node_31 | 0.4 | n |  | TRUE
67 | bus_LV_1054-4_0_5_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_1054-4_0_5_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1054-4_0_5_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_1054-4_0_5_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_1054-4_0_5_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_1054-4_0_5_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_1054-4_0_5_node_69 | 0.4 | n |  | TRUE
74 | bus_LV_1054-4_0_5_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_1054-4_0_5_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_1054-4_0_5_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_1054-4_0_5_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_1054-4_0_5_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_1054-4_0_5_node_80 | 0.4 | n |  | TRUE
80 | bus_LV_1054-4_0_5_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_1054-4_0_5_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_1054-4_0_5_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_1054-4_0_5_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_1054-4_0_5_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_1054-4_0_5_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_1054-4_0_5_node_108 | 0.4 | n |  | TRUE
87 | bus_LV_1054-4_0_5_node_95 | 0.4 | n |  | TRUE
88 | bus_LV_1054-4_0_5_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_1054-4_0_5_node_109 | 0.4 | n |  | TRUE
90 | bus_LV_1054-4_0_5_node_97 | 0.4 | n |  | TRUE
91 | bus_LV_1054-4_0_5_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_1054-4_0_5_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_1054-4_0_5_node_82 | 0.4 | n |  | TRUE
94 | bus_LV_1054-4_0_5_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_1054-4_0_5_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_1054-4_0_5_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_1054-4_0_5_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1054-4_0_5_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_1054-4_0_5_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_1054-4_0_5_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_1054-4_0_5_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_1054-4_0_5_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_1054-4_0_5_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_1054-4_0_5_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_1054-4_0_5_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_1054-4_0_5_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_1054-4_0_5_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_1054-4_0_5_node_102 | 0.4 | n |  | TRUE
109 | bus_LV_1054-4_0_5_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_1054-4_0_5_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1054-4_0_5_node_110 | 0.4 | n |  | TRUE
112 | bus_LV_1054-4_0_5_node_111 | 0.4 | n |  | TRUE
113 | bus_LV_1054-4_0_5_node_116 | 0.4 | n |  | TRUE
114 | bus_LV_1054-4_0_5_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_1054-4_0_5_node_112 | 0.4 | n |  | TRUE
116 | bus_LV_1054-4_0_5_node_114 | 0.4 | n |  | TRUE
117 | bus_MV_211_0_node_51 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-4_0_5_load_0 | 0 | 0.002264 | 0.00056741 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-4_0_5_load_1 | 1 | 0.0021324 | 0.00053444 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-4_0_5_load_17 | 3 | 0.0025063 | 0.00062813 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-4_0_5_load_18 | 4 | 0.027783 | 0.0069631 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-4_0_5_load_7 | 5 | 0.0021392 | 0.00053613 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-4_0_5_load_19 | 6 | 0.0084304 | 0.0021129 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-4_0_5_load_39 | 7 | 0.0032119 | 0.00080498 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-4_0_5_load_3 | 11 | 0.00208 | 0.0005213 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-4_0_5_load_4 | 12 | 0.0021425 | 0.00053696 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-4_0_5_load_6 | 13 | 0.00099559 | 0.00024952 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-4_0_5_load_8 | 14 | 0.00079084 | 0.0001982 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-4_0_5_load_21 | 15 | 0.0097663 | 0.0024477 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-4_0_5_load_26 | 17 | 0.014698 | 0.0036836 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-4_0_5_load_25 | 18 | 0.0064879 | 0.001626 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-4_0_5_load_16 | 19 | 0.0018174 | 0.00045548 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-4_0_5_load_34 | 20 | 0.0038321 | 0.00096041 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-4_0_5_load_38 | 24 | 0.002893 | 0.00072504 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-4_0_5_load_54 | 25 | 0.0071247 | 0.0017856 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-4_0_5_load_40 | 26 | 0.00059856 | 0.00015001 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-4_0_5_load_41 | 27 | 0.0018555 | 0.00046504 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-4_0_5_load_53 | 28 | 0.0052113 | 0.0013061 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-4_0_5_load_121 | 31 | 0.017802 | 0.0044616 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-4_0_5_load_27 | 33 | 0.0052479 | 0.0013152 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-4_0_5_load_65 | 34 | 0.00050735 | 0.00012715 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-4_0_5_load_12 | 35 | 0.0072337 | 0.0018129 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-4_0_5_load_13 | 36 | 0.0021147 | 0.00053 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-4_0_5_load_14 | 37 | 0.0039684 | 0.00099456 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-4_0_5_load_10 | 38 | 0.0025292 | 0.00063388 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-4_0_5_load_11 | 39 | 0.0069208 | 0.0017345 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-4_0_5_load_15 | 40 | 0.0036013 | 0.00090258 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-4_0_5_load_23 | 41 | 0.0033671 | 0.00084387 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-4_0_5_load_24 | 42 | 0.00058011 | 0.00014539 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-4_0_5_load_106 | 44 | 0.01289 | 0.0032305 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-4_0_5_load_73 | 45 | 0.012948 | 0.003245 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-4_0_5_load_32 | 46 | 0.0077983 | 0.0019544 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-4_0_5_load_107 | 47 | 0.0078234 | 0.0019607 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-4_0_5_load_33 | 48 | 0.01006 | 0.0025212 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-4_0_5_load_42 | 49 | 0.00045406 | 0.0001138 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-4_0_5_load_44 | 50 | 0.00046678 | 0.00011699 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-4_0_5_load_43 | 51 | 0.0068405 | 0.0017144 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-4_0_5_load_63 | 52 | 0.0032561 | 0.00081605 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-4_0_5_load_28 | 53 | 0.0027443 | 0.0006878 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-4_0_5_load_52 | 55 | 0.003279 | 0.0008218 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-4_0_5_load_61 | 56 | 0.001471 | 0.00036867 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-4_0_5_load_62 | 57 | 0.004181 | 0.0010478 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-4_0_5_load_64 | 58 | 0.0014717 | 0.00036885 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-4_0_5_load_71 | 59 | 0.001324 | 0.00033184 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-4_0_5_load_118 | 60 | 0.012702 | 0.0031835 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-4_0_5_load_119 | 61 | 0.018733 | 0.0046948 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-4_0_5_load_50 | 62 | 0.0011118 | 0.00027865 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-4_0_5_load_48 | 63 | 0.0034355 | 0.00086102 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-4_0_5_load_29 | 64 | 0.027572 | 0.0069101 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-4_0_5_load_30 | 65 | 0.010096 | 0.0025303 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-4_0_5_load_31 | 66 | 0.012915 | 0.0032367 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-4_0_5_load_45 | 67 | 0.0022468 | 0.00056311 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-4_0_5_load_47 | 68 | 0.0038712 | 0.00097022 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-4_0_5_load_59 | 69 | 0.0036684 | 0.00091938 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-4_0_5_load_57 | 70 | 0.0039562 | 0.00099152 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-4_0_5_load_66 | 71 | 0.0010704 | 0.00026826 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-4_0_5_load_69 | 73 | 0.00049769 | 0.00012473 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-4_0_5_load_49 | 74 | 0.0039815 | 0.00099786 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-4_0_5_load_51 | 75 | 0.0054794 | 0.0013733 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-4_0_5_load_60 | 76 | 0.0040426 | 0.0010132 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-4_0_5_load_58 | 77 | 0.002928 | 0.00073383 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-4_0_5_load_80 | 79 | 0.013607 | 0.0034103 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-4_0_5_load_75 | 80 | 0.0099352 | 0.00249 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-4_0_5_load_74 | 81 | 0.0071177 | 0.0017839 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-4_0_5_load_78 | 83 | 0.00355 | 0.00088971 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-4_0_5_load_79 | 84 | 0.0091682 | 0.0022978 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-4_0_5_load_87 | 85 | 0.0096366 | 0.0024152 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-4_0_5_load_108 | 86 | 0.0016777 | 0.00042047 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-4_0_5_load_85 | 88 | 0.0091955 | 0.0023046 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-4_0_5_load_97 | 90 | 0.0027977 | 0.00070118 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-4_0_5_load_93 | 91 | 0.0027972 | 0.00070105 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-4_0_5_load_81 | 92 | 0.014668 | 0.0036761 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-4_0_5_load_82 | 93 | 0.0042455 | 0.001064 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-4_0_5_load_84 | 95 | 0.011603 | 0.002908 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-4_0_5_load_86 | 96 | 0.013499 | 0.0033831 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-4_0_5_load_88 | 97 | 0.013357 | 0.0033476 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-4_0_5_load_89 | 98 | 0.013359 | 0.0033482 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-4_0_5_load_90 | 99 | 0.0043001 | 0.0010777 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-4_0_5_load_94 | 101 | 0.0032171 | 0.00080627 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1054-4_0_5_load_96 | 102 | 0.0032196 | 0.0008069 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1054-4_0_5_load_100 | 103 | 0.012158 | 0.0030471 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1054-4_0_5_load_98 | 104 | 0.0027993 | 0.00070157 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1054-4_0_5_load_101 | 105 | 0.0032182 | 0.00080656 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1054-4_0_5_load_99 | 106 | 0.010034 | 0.0025147 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1054-4_0_5_load_105 | 107 | 0.0059337 | 0.0014871 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1054-4_0_5_load_102 | 108 | 0.0032174 | 0.00080636 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1054-4_0_5_load_103 | 109 | 0.011335 | 0.0028409 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1054-4_0_5_load_104 | 110 | 0.0032174 | 0.00080636 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1054-4_0_5_load_111 | 112 | 0.0018436 | 0.00046204 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1054-4_0_5_load_116 | 113 | 0.0034484 | 0.00086424 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1054-4_0_5_load_113 | 114 | 0.0088362 | 0.0022146 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1054-4_0_5_load_112 | 115 | 0.0014472 | 0.00036269 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1054-4_0_5_load_114 | 116 | 0.0015309 | 0.00038368 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-4_0_5_line_0 |  | 0 | 1 | 0.023752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-4_0_5_line_1 |  | 1 | 2 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-4_0_5_line_2 |  | 2 | 5 | 0.018453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-4_0_5_line_3 |  | 3 | 4 | 0.03613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-4_0_5_line_4 |  | 4 | 6 | 0.01534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-4_0_5_line_5 |  | 5 | 7 | 0.36883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_1054-4_0_5_line_6 |  | 5 | 8 | 0.10916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1054-4_0_5_line_7 |  | 6 | 9 | 0.028754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1054-4_0_5_line_8 |  | 6 | 10 | 0.044174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1054-4_0_5_line_9 |  | 7 | 22 | 0.025932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1054-4_0_5_line_10 |  | 8 | 14 | 0.056659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-4_0_5_line_11 |  | 8 | 11 | 0.10417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1054-4_0_5_line_12 |  | 9 | 15 | 0.025083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1054-4_0_5_line_13 |  | 9 | 16 | 0.054713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1054-4_0_5_line_14 |  | 10 | 19 | 0.012926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-4_0_5_line_15 |  | 10 | 13 | 0.020097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1054-4_0_5_line_16 |  | 11 | 12 | 0.0055707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_1054-4_0_5_line_17 |  | 12 | 13 | 0.017258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1054-4_0_5_line_18 |  | 15 | 36 | 0.042886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1054-4_0_5_line_19 |  | 16 | 43 | 0.022174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_1054-4_0_5_line_20 |  | 16 | 44 | 0.020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1054-4_0_5_line_21 |  | 17 | 18 | 0.020328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_1054-4_0_5_line_22 |  | 18 | 33 | 0.0049775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-4_0_5_line_23 |  | 18 | 34 | 0.037865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_1054-4_0_5_line_24 |  | 19 | 35 | 0.014297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-4_0_5_line_25 |  | 20 | 21 | 0.0068903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-4_0_5_line_26 |  | 20 | 22 | 0.023788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-4_0_5_line_27 |  | 21 | 23 | 0.034887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-4_0_5_line_28 |  | 21 | 24 | 0.021449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-4_0_5_line_29 |  | 22 | 25 | 0.1633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1054-4_0_5_line_30 |  | 23 | 26 | 0.0045102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-4_0_5_line_31 |  | 25 | 28 | 0.011308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1054-4_0_5_line_32 |  | 26 | 27 | 0.0069536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-4_0_5_line_33 |  | 28 | 29 | 0.036053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_1054-4_0_5_line_34 |  | 29 | 30 | 0.043685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_1054-4_0_5_line_35 |  | 30 | 31 | 0.047397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_1054-4_0_5_line_36 |  | 30 | 32 | 0.071312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_1054-4_0_5_line_37 |  | 32 | 72 | 0.024315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1054-4_0_5_line_38 |  | 32 | 71 | 0.044135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1054-4_0_5_line_39 |  | 34 | 52 | 0.0084877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_1054-4_0_5_line_40 |  | 34 | 50 | 0.012315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_1054-4_0_5_line_41 |  | 35 | 39 | 0.0057056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1054-4_0_5_line_42 |  | 36 | 37 | 0.026571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_1054-4_0_5_line_43 |  | 37 | 40 | 0.016617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_1054-4_0_5_line_44 |  | 38 | 39 | 0.031419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1054-4_0_5_line_45 |  | 40 | 41 | 0.01038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_1054-4_0_5_line_46 |  | 41 | 42 | 0.023633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_1054-4_0_5_line_47 |  | 42 | 48 | 0.00090988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_1054-4_0_5_line_48 |  | 43 | 45 | 0.0090644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_1054-4_0_5_line_49 |  | 43 | 46 | 0.048851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1054-4_0_5_line_50 |  | 44 | 47 | 0.016666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_1054-4_0_5_line_51 |  | 45 | 78 | 0.036668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_1054-4_0_5_line_52 |  | 46 | 65 | 0.0088491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1054-4_0_5_line_53 |  | 48 | 49 | 0.01195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_1054-4_0_5_line_54 |  | 49 | 51 | 0.016856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_1054-4_0_5_line_55 |  | 50 | 51 | 0.0054971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_1054-4_0_5_line_56 |  | 52 | 56 | 0.01615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1054-4_0_5_line_57 |  | 53 | 54 | 0.032252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_1054-4_0_5_line_58 |  | 53 | 55 | 0.036797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_1054-4_0_5_line_59 |  | 54 | 60 | 0.025345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_1054-4_0_5_line_60 |  | 54 | 61 | 0.037562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1054-4_0_5_line_61 |  | 55 | 59 | 0.024704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1054-4_0_5_line_62 |  | 55 | 62 | 0.00069688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1054-4_0_5_line_63 |  | 56 | 57 | 0.010251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_1054-4_0_5_line_64 |  | 57 | 58 | 0.001264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1054-4_0_5_line_65 |  | 58 | 59 | 0.023178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_1054-4_0_5_line_66 |  | 60 | 100 | 0.00057453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1054-4_0_5_line_67 |  | 62 | 63 | 0.027404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_1054-4_0_5_line_68 |  | 63 | 74 | 0.016632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_1054-4_0_5_line_69 |  | 64 | 65 | 0.010704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1054-4_0_5_line_70 |  | 64 | 66 | 0.01442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1054-4_0_5_line_71 |  | 67 | 68 | 0.012431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1054-4_0_5_line_72 |  | 68 | 69 | 0.045741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_1054-4_0_5_line_73 |  | 69 | 70 | 0.012849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_1054-4_0_5_line_74 |  | 70 | 77 | 0.011026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_1054-4_0_5_line_75 |  | 72 | 73 | 0.041611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_1054-4_0_5_line_76 |  | 74 | 75 | 0.021353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_1054-4_0_5_line_77 |  | 75 | 76 | 0.0048247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_1054-4_0_5_line_78 |  | 76 | 77 | 0.019289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_1054-4_0_5_line_79 |  | 78 | 79 | 0.059465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_1054-4_0_5_line_80 |  | 78 | 80 | 0.018682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_1054-4_0_5_line_81 |  | 79 | 87 | 0.013844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_1054-4_0_5_line_82 |  | 80 | 81 | 0.016195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_1054-4_0_5_line_83 |  | 81 | 82 | 0.035223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_1054-4_0_5_line_84 |  | 82 | 83 | 0.0047443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_1054-4_0_5_line_85 |  | 82 | 84 | 0.023582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_1054-4_0_5_line_86 |  | 83 | 85 | 0.013215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_1054-4_0_5_line_87 |  | 84 | 86 | 0.047055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_1054-4_0_5_line_88 |  | 85 | 88 | 0.043826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_1054-4_0_5_line_89 |  | 86 | 89 | 0.016616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_1054-4_0_5_line_90 |  | 87 | 90 | 0.015289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_1054-4_0_5_line_91 |  | 87 | 91 | 0.017246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_1054-4_0_5_line_92 |  | 88 | 94 | 0.0086052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_1054-4_0_5_line_93 |  | 89 | 111 | 0.051995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_1054-4_0_5_line_94 |  | 89 | 112 | 0.026309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_1054-4_0_5_line_95 |  | 90 | 104 | 0.0093914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_1054-4_0_5_line_96 |  | 91 | 101 | 0.0093671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_1054-4_0_5_line_97 |  | 92 | 93 | 0.0419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_1054-4_0_5_line_98 |  | 92 | 94 | 0.015833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_1054-4_0_5_line_99 |  | 93 | 95 | 0.0051166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_1054-4_0_5_line_100 |  | 95 | 96 | 0.051181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_1054-4_0_5_line_101 |  | 97 | 98 | 0.021588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_1054-4_0_5_line_102 |  | 97 | 99 | 0.00081761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-4_0_5_line_103 |  | 98 | 100 | 0.015477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_1054-4_0_5_line_104 |  | 101 | 102 | 0.026532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_1054-4_0_5_line_105 |  | 102 | 103 | 0.0043454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_1054-4_0_5_line_106 |  | 103 | 105 | 0.0091037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_1054-4_0_5_line_107 |  | 104 | 106 | 0.014558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_1054-4_0_5_line_108 |  | 105 | 108 | 0.029045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_1054-4_0_5_line_109 |  | 106 | 107 | 0.010714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_1054-4_0_5_line_110 |  | 108 | 109 | 0.00048289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_1054-4_0_5_line_111 |  | 109 | 110 | 0.0089158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_1054-4_0_5_line_112 |  | 111 | 113 | 0.039345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_1054-4_0_5_line_113 |  | 112 | 114 | 0.019157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_1054-4_0_5_line_114 |  | 114 | 115 | 0.013736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_1054-4_0_5_line_115 |  | 115 | 116 | 2.2028e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-4_0_5_trafo_26 | 0.63 MVA 20/0.4 kV | 117 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2667485.0828 | 1214127.0315 | 2667501.6979 | 1214141.0147 | 2667503.1959 | 1214142.3936
1 | 2667511.0041 | 1214149.5809 | 2667503.1959 | 1214142.3936
2 | 2667511.0041 | 1214149.5809 | 2667524.5774 | 1214162.082
3 | 2667576.7034 | 1214057.0569 | 2667549.8639 | 1214032.8698
4 | 2667576.7034 | 1214057.0569 | 2667588.0986 | 1214067.3259
5 | 2667524.5774 | 1214162.082 | 2667309.7864 | 1214461.916
6 | 2667608.0264 | 1214232.2093 | 2667585.4647 | 1214213.7421 | 2667558.8348 | 1214194.3394 | 2667540.1779 | 1214176.4502 | 2667524.5774 | 1214162.082
7 | 2667609.4656 | 1214086.568 | 2667605.2775 | 1214082.807 | 2667588.0986 | 1214067.3259
8 | 2667588.0986 | 1214067.3259 | 2667557.821 | 1214099.4909
9 | 2667330.4992 | 1214477.4787 | 2667313.997 | 1214464.5288 | 2667309.7864 | 1214461.916
10 | 2667608.0264 | 1214232.2093 | 2667616.2744 | 1214238.9626 | 2667651.5868 | 1214268.4411
11 | 2667608.0264 | 1214232.2093 | 2667603.236 | 1214206.5612 | 2667575.7412 | 1214162.2775 | 2667566.8501 | 1214149.2575 | 2667561.0126 | 1214140.9096
12 | 2667609.4656 | 1214086.568 | 2667628.0461 | 1214103.4184
13 | 2667643.272 | 1214047.8938 | 2667636.6929 | 1214054.7012 | 2667639.1639 | 1214056.497 | 2667609.4656 | 1214086.568
14 | 2667557.821 | 1214099.4909 | 2667548.004 | 1214091.082
15 | 2667557.821 | 1214099.4909 | 2667558.6321 | 1214119.5719
16 | 2667561.0126 | 1214140.9096 | 2667557.8202 | 1214136.3444
17 | 2667557.8202 | 1214136.3444 | 2667556.8269 | 1214134.9239 | 2667558.7937 | 1214123.5725 | 2667558.6321 | 1214119.5719
18 | 2667628.0461 | 1214103.4184 | 2667603.2211 | 1214138.3885
19 | 2667664.432 | 1214054.7158 | 2667643.272 | 1214047.8938
20 | 2667643.272 | 1214047.8938 | 2667641.4633 | 1214047.3062 | 2667624.9943 | 1214037.9593
21 | 2667721.0044 | 1214190.7093 | 2667705.9056 | 1214177.0987
22 | 2667721.0044 | 1214190.7093 | 2667724.7016 | 1214194.042
23 | 2667721.0044 | 1214190.7093 | 2667697.3229 | 1214220.2545
24 | 2667548.004 | 1214091.082 | 2667537.1458 | 1214081.7815
25 | 2667303.2664 | 1214487.9557 | 2667310.0412 | 1214486.6995
26 | 2667330.4992 | 1214477.4787 | 2667325.4221 | 1214483.8476 | 2667310.0412 | 1214486.6995
27 | 2667277.9503 | 1214463.8772 | 2667303.2664 | 1214487.9557
28 | 2667303.2664 | 1214487.9557 | 2667288.6284 | 1214503.6336
29 | 2667412.5698 | 1214618.6571 | 2667330.4992 | 1214477.4787
30 | 2667277.9503 | 1214463.8772 | 2667274.2258 | 1214466.4207
31 | 2667422.3615 | 1214613.4694 | 2667417.3447 | 1214614.8568 | 2667412.5698 | 1214618.6571
32 | 2667274.2258 | 1214466.4207 | 2667273.2737 | 1214467.0709 | 2667268.7907 | 1214470.7522
33 | 2667452.5103 | 1214594.6306 | 2667443.3557 | 1214602.2541 | 2667436.9789 | 1214607.3629 | 2667431.648 | 1214610.6492 | 2667425.1082 | 1214612.7098 | 2667422.3615 | 1214613.4694
34 | 2667482.5529 | 1214626.4237 | 2667452.5103 | 1214594.6306
35 | 2667482.5529 | 1214626.4237 | 2667478.4596 | 1214629.7461 | 2667468.6016 | 1214636.4388 | 2667455.6434 | 1214647.9661 | 2667447.7804 | 1214658.2391
36 | 2667482.5529 | 1214626.4237 | 2667508.3952 | 1214649.5083 | 2667520.5871 | 1214658.7077 | 2667538.0651 | 1214671.2467
37 | 2667556.5621 | 1214687.0217 | 2667544.8529 | 1214676.1156 | 2667538.0651 | 1214671.2467
38 | 2667538.0651 | 1214671.2467 | 2667514.8169 | 1214708.7623
39 | 2667703.724 | 1214225.8283 | 2667697.3229 | 1214220.2545
40 | 2667688.0351 | 1214212.1674 | 2667697.3229 | 1214220.2545
41 | 2667537.1458 | 1214081.7815 | 2667532.8126 | 1214078.0698
42 | 2667623.2952 | 1214155.7959 | 2667608.3721 | 1214142.8018 | 2667603.2211 | 1214138.3885
43 | 2667635.8269 | 1214166.7077 | 2667623.2952 | 1214155.7959
44 | 2667532.8126 | 1214078.0698 | 2667508.9508 | 1214057.6308
45 | 2667635.8269 | 1214166.7077 | 2667643.6555 | 1214173.5243
46 | 2667643.6555 | 1214173.5243 | 2667661.4784 | 1214189.0435
47 | 2667662.1646 | 1214189.641 | 2667661.4784 | 1214189.0435
48 | 2667664.432 | 1214054.7158 | 2667673.4958 | 1214054.8187
49 | 2667664.432 | 1214054.7158 | 2667663.8669 | 1214061.6804 | 2667669.8086 | 1214073.5552 | 2667687.8846 | 1214089.0811 | 2667691.426 | 1214092.2565
50 | 2667624.9943 | 1214037.9593 | 2667622.6334 | 1214036.6194 | 2667611.8172 | 1214027.8073
51 | 2667710.0396 | 1214052.4208 | 2667684.3984 | 1214054.9425 | 2667673.4958 | 1214054.8187
52 | 2667691.426 | 1214092.2565 | 2667698.0145 | 1214098.1639
53 | 2667671.177 | 1214197.4884 | 2667662.1646 | 1214189.641
54 | 2667671.177 | 1214197.4884 | 2667683.8893 | 1214208.5575
55 | 2667688.0351 | 1214212.1674 | 2667683.8893 | 1214208.5575
56 | 2667715.9039 | 1214236.4338 | 2667703.724 | 1214225.8283
57 | 2667810.0323 | 1214268.4474 | 2667785.0058 | 1214248.1039
58 | 2667785.0058 | 1214248.1039 | 2667760.5502 | 1214275.5976
59 | 2667810.0323 | 1214268.4474 | 2667826.8842 | 1214249.5159
60 | 2667810.0323 | 1214268.4474 | 2667838.4956 | 1214292.9569
61 | 2667742.0683 | 1214259.2161 | 2667758.5608 | 1214273.5767 | 2667760.5502 | 1214275.5976
62 | 2667761.0391 | 1214276.0943 | 2667760.5502 | 1214275.5976
63 | 2667715.9039 | 1214236.4338 | 2667723.6348 | 1214243.1653
64 | 2667723.6348 | 1214243.1653 | 2667724.5881 | 1214243.9954
65 | 2667742.0683 | 1214259.2161 | 2667724.5881 | 1214243.9954
66 | 2667826.8842 | 1214249.5159 | 2667827.2662 | 1214249.0868
67 | 2667779.9082 | 1214295.9412 | 2667776.7242 | 1214292.028 | 2667761.0391 | 1214276.0943
68 | 2667779.9082 | 1214295.9412 | 2667790.4049 | 1214308.8422
69 | 2667705.9839 | 1214105.3095 | 2667698.0145 | 1214098.1639
70 | 2667716.72 | 1214114.9357 | 2667705.9839 | 1214105.3095
71 | 2667810.9015 | 1214393.0018 | 2667820.5681 | 1214400.8174
72 | 2667839.5563 | 1214357.3487 | 2667810.9015 | 1214393.0018
73 | 2667829.5561 | 1214349.3014 | 2667834.4318 | 1214353.6003 | 2667839.5563 | 1214357.3487
74 | 2667829.5561 | 1214349.3014 | 2667821.2855 | 1214342.0091
75 | 2667556.5621 | 1214687.0217 | 2667537.2526 | 1214711.4516 | 2667531.1095 | 1214719.9312
76 | 2667803.8813 | 1214325.4055 | 2667790.4049 | 1214308.8422
77 | 2667806.9262 | 1214329.1479 | 2667803.8813 | 1214325.4055
78 | 2667821.2855 | 1214342.0091 | 2667807.5032 | 1214329.857 | 2667806.9262 | 1214329.1479
79 | 2667710.0396 | 1214052.4208 | 2667709.04 | 1214038.7787 | 2667705.9982 | 1214024.3796 | 2667698.5011 | 1214008.3401 | 2667689.9696 | 1213998.0528
80 | 2667710.0396 | 1214052.4208 | 2667728.7109 | 1214053.0667
81 | 2667681.1321 | 1213987.3966 | 2667689.9696 | 1213998.0528
82 | 2667744.8867 | 1214053.7571 | 2667743.0601 | 1214053.5631 | 2667728.7109 | 1214053.0667
83 | 2667779.3483 | 1214060.5798 | 2667773.9884 | 1214059.0179 | 2667758.4228 | 1214055.1942 | 2667744.8867 | 1214053.7571
84 | 2667779.3483 | 1214060.5798 | 2667783.6567 | 1214062.5662
85 | 2667779.3483 | 1214060.5798 | 2667780.8181 | 1214056.2382 | 2667787.5481 | 1214053.5463 | 2667789.8148 | 1214049.2583 | 2667790.9144 | 1214046.0688 | 2667791.3644 | 1214042.5717 | 2667791.3644 | 1214042.5717
86 | 2667783.6567 | 1214062.5662 | 2667789.1636 | 1214065.1053 | 2667795.2099 | 1214068.9237
87 | 2667791.3644 | 1214042.5717 | 2667789.3446 | 1214036.5005 | 2667786.9568 | 1214031.4036 | 2667786.3347 | 1214027.9944 | 2667786.6772 | 1214024.5961 | 2667787.9877 | 1214021.5647 | 2667792.0505 | 1214018.3088 | 2667796.9772 | 1214014.5514 | 2667800.4428 | 1214010.377 | 2667804.2374 | 1214003.3158
88 | 2667832.2647 | 1214092.3252 | 2667795.2099 | 1214068.9237
89 | 2667803.0728 | 1213986.8367 | 2667803.5824 | 1213989.4441 | 2667804.6896 | 1213999.6186 | 2667804.2374 | 1214003.3158
90 | 2667681.1321 | 1213987.3966 | 2667669.6859 | 1213977.2611
91 | 2667681.1321 | 1213987.3966 | 2667686.2798 | 1213984.909 | 2667693.5994 | 1213988.4943 | 2667695.989 | 1213990.8825
92 | 2667839.5404 | 1214096.9201 | 2667832.2647 | 1214092.3252
93 | 2667803.0728 | 1213986.8367 | 2667805.2897 | 1213966.2268 | 2667818.1773 | 1213937.7333
94 | 2667803.0728 | 1213986.8367 | 2667818.8071 | 1213987.1935 | 2667828.6491 | 1213991.0488
95 | 2667669.6859 | 1213977.2611 | 2667662.6548 | 1213971.0352
96 | 2667695.989 | 1213990.8825 | 2667702.6144 | 1213997.5041
97 | 2667828.6892 | 1214108.0148 | 2667820.3078 | 1214110.3209 | 2667815.6616 | 1214112.1247 | 2667815.0911 | 1214114.8644 | 2667817.3751 | 1214117.7366 | 2667809.0028 | 1214126.5914 | 2667803.1366 | 1214134.1517 | 2667803.1366 | 1214134.1517
98 | 2667839.5404 | 1214096.9201 | 2667832.9 | 1214105.7612 | 2667828.6892 | 1214108.0148 | 2667828.6892 | 1214108.0148
99 | 2667803.1366 | 1214134.1517 | 2667807.5684 | 1214136.7086
100 | 2667843.9523 | 1214170.4274 | 2667842.2842 | 1214164.1711 | 2667840.5726 | 1214161.7279 | 2667835.5591 | 1214159.7697 | 2667811.6485 | 1214139.0626 | 2667807.5684 | 1214136.7086
101 | 2667799.0774 | 1214225.0192 | 2667815.4956 | 1214239.037
102 | 2667799.0774 | 1214225.0192 | 2667798.4556 | 1214224.4883
103 | 2667827.2662 | 1214249.0868 | 2667815.4956 | 1214239.037
104 | 2667724.467 | 1214012.0199 | 2667709.4315 | 1214004.3172 | 2667702.6144 | 1213997.5041
105 | 2667724.467 | 1214012.0199 | 2667727.2536 | 1214013.4475 | 2667728.4504 | 1214013.6538
106 | 2667737.4217 | 1214015.2009 | 2667728.4504 | 1214013.6538
107 | 2667662.6548 | 1213971.0352 | 2667651.7553 | 1213961.3838
108 | 2667766.2883 | 1214018.0348 | 2667747.0624 | 1214016.8634 | 2667737.4217 | 1214015.2009
109 | 2667643.6843 | 1213954.3397 | 2667644.9976 | 1213955.4 | 2667651.7553 | 1213961.3838
110 | 2667766.7703 | 1214018.0642 | 2667766.2883 | 1214018.0348
111 | 2667775.6696 | 1214018.6064 | 2667766.7703 | 1214018.0642
112 | 2667818.1773 | 1213937.7333 | 2667825.2651 | 1213941.6607 | 2667840.3061 | 1213950.2149 | 2667852.0668 | 1213957.6968
113 | 2667845.2064 | 1214000.5513 | 2667832.9557 | 1213992.7357 | 2667828.6491 | 1213991.0488
114 | 2667856.7862 | 1214007.9389 | 2667845.2064 | 1214000.5513
115 | 2667856.7862 | 1214007.9389 | 2667856.8048 | 1214007.9508

## bus_geodata
| x | y | coords
0 | 2667485.0828 | 1214127.0315
1 | 2667503.1959 | 1214142.3936
2 | 2667511.0041 | 1214149.5809
3 | 2667549.8639 | 1214032.8698
4 | 2667576.7034 | 1214057.0569
5 | 2667524.5774 | 1214162.082
6 | 2667588.0986 | 1214067.3259
7 | 2667309.7864 | 1214461.916
8 | 2667608.0264 | 1214232.2093
9 | 2667609.4656 | 1214086.568
10 | 2667557.821 | 1214099.4909
11 | 2667561.0126 | 1214140.9096
12 | 2667557.8202 | 1214136.3444
13 | 2667558.6321 | 1214119.5719
14 | 2667651.5868 | 1214268.4411
15 | 2667628.0461 | 1214103.4184
16 | 2667643.272 | 1214047.8938
17 | 2667705.9056 | 1214177.0987
18 | 2667721.0044 | 1214190.7093
19 | 2667548.004 | 1214091.082
20 | 2667310.0412 | 1214486.6995
21 | 2667303.2664 | 1214487.9557
22 | 2667330.4992 | 1214477.4787
23 | 2667277.9503 | 1214463.8772
24 | 2667288.6284 | 1214503.6336
25 | 2667412.5698 | 1214618.6571
26 | 2667274.2258 | 1214466.4207
27 | 2667268.7907 | 1214470.7522
28 | 2667422.3615 | 1214613.4694
29 | 2667452.5103 | 1214594.6306
30 | 2667482.5529 | 1214626.4237
31 | 2667447.7804 | 1214658.2391
32 | 2667538.0651 | 1214671.2467
33 | 2667724.7016 | 1214194.042
34 | 2667697.3229 | 1214220.2545
35 | 2667537.1458 | 1214081.7815
36 | 2667603.2211 | 1214138.3885
37 | 2667623.2952 | 1214155.7959
38 | 2667508.9508 | 1214057.6308
39 | 2667532.8126 | 1214078.0698
40 | 2667635.8269 | 1214166.7077
41 | 2667643.6555 | 1214173.5243
42 | 2667661.4784 | 1214189.0435
43 | 2667664.432 | 1214054.7158
44 | 2667624.9943 | 1214037.9593
45 | 2667673.4958 | 1214054.8187
46 | 2667691.426 | 1214092.2565
47 | 2667611.8172 | 1214027.8073
48 | 2667662.1646 | 1214189.641
49 | 2667671.177 | 1214197.4884
50 | 2667688.0351 | 1214212.1674
51 | 2667683.8893 | 1214208.5575
52 | 2667703.724 | 1214225.8283
53 | 2667785.0058 | 1214248.1039
54 | 2667810.0323 | 1214268.4474
55 | 2667760.5502 | 1214275.5976
56 | 2667715.9039 | 1214236.4338
57 | 2667723.6348 | 1214243.1653
58 | 2667724.5881 | 1214243.9954
59 | 2667742.0683 | 1214259.2161
60 | 2667826.8842 | 1214249.5159
61 | 2667838.4956 | 1214292.9569
62 | 2667761.0391 | 1214276.0943
63 | 2667779.9082 | 1214295.9413
64 | 2667705.9839 | 1214105.3095
65 | 2667698.0145 | 1214098.1639
66 | 2667716.72 | 1214114.9357
67 | 2667820.5681 | 1214400.8174
68 | 2667810.9015 | 1214393.0018
69 | 2667839.5563 | 1214357.3487
70 | 2667829.5561 | 1214349.3014
71 | 2667514.8169 | 1214708.7623
72 | 2667556.5621 | 1214687.0217
73 | 2667531.1095 | 1214719.9312
74 | 2667790.4049 | 1214308.8422
75 | 2667803.8813 | 1214325.4055
76 | 2667806.9262 | 1214329.1479
77 | 2667821.2855 | 1214342.0091
78 | 2667710.0396 | 1214052.4208
79 | 2667689.9696 | 1213998.0528
80 | 2667728.7109 | 1214053.0667
81 | 2667744.8867 | 1214053.7571
82 | 2667779.3483 | 1214060.5798
83 | 2667783.6567 | 1214062.5662
84 | 2667791.3644 | 1214042.5717
85 | 2667795.2099 | 1214068.9237
86 | 2667804.2374 | 1214003.3157
87 | 2667681.1321 | 1213987.3966
88 | 2667832.2647 | 1214092.3252
89 | 2667803.0728 | 1213986.8367
90 | 2667669.6859 | 1213977.2611
91 | 2667695.989 | 1213990.8825
92 | 2667828.6892 | 1214108.0148
93 | 2667803.1366 | 1214134.1517
94 | 2667839.5404 | 1214096.9201
95 | 2667807.5684 | 1214136.7086
96 | 2667843.9523 | 1214170.4274
97 | 2667799.0774 | 1214225.0192
98 | 2667815.4956 | 1214239.037
99 | 2667798.4556 | 1214224.4883
100 | 2667827.2662 | 1214249.0868
101 | 2667702.6144 | 1213997.5041
102 | 2667724.467 | 1214012.0199
103 | 2667728.4504 | 1214013.6538
104 | 2667662.6548 | 1213971.0352
105 | 2667737.4217 | 1214015.2009
106 | 2667651.7553 | 1213961.3838
107 | 2667643.6843 | 1213954.3397
108 | 2667766.2883 | 1214018.0348
109 | 2667766.7703 | 1214018.0642
110 | 2667775.6696 | 1214018.6064
111 | 2667818.1773 | 1213937.7333
112 | 2667828.6491 | 1213991.0487
113 | 2667852.0668 | 1213957.6968
114 | 2667845.2064 | 1214000.5513
115 | 2667856.7862 | 1214007.9389
116 | 2667856.8048 | 1214007.9508
117 | 2667609.4656 | 1214086.568

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97529 | -0.47469 | 0.002264 | 0.00056741
1 | 0.97534 | -0.47371 | 0.0021324 | 0.00053444
2 | 0.97538 | -0.47285 | 0 | 0
3 | 0.97804 | -0.42068 | 0.0025063 | 0.00062813
4 | 0.97812 | -0.41903 | 0.027783 | 0.0069631
5 | 0.97546 | -0.47137 | 0.0021392 | 0.00053613
6 | 0.97856 | -0.41057 | 0.0084304 | 0.0021129
7 | 0.97242 | -0.53128 | 0.0032119 | 0.00080498
8 | 0.97649 | -0.45108 | 0 | 0
9 | 0.97916 | -0.39863 | 0 | 0
10 | 0.97794 | -0.42269 | 0 | 0
11 | 0.97749 | -0.43145 | 0.00208 | 0.0005213
12 | 0.97755 | -0.43036 | 0.0021425 | 0.00053696
13 | 0.97773 | -0.42685 | 0.00099559 | 0.00024952
14 | 0.97645 | -0.4519 | 0.00079084 | 0.0001982
15 | 0.98101 | -0.36266 | 0.0097663 | 0.0024477
16 | 0.9763 | -0.45472 | 0 | 0
17 | 1 | 0 | -0.57619 | -0.14823
18 | 0.99787 | -0.040027 | 0.0064879 | 0.001626
19 | 0.97772 | -0.42705 | 0.0018174 | 0.00045548
20 | 0.97202 | -0.53922 | 0.0038321 | 0.00096041
21 | 0.97199 | -0.5399 | 0 | 0
22 | 0.97223 | -0.53519 | 0 | 0
23 | 0.97191 | -0.54148 | 0 | 0
24 | 0.97193 | -0.54105 | 0.002893 | 0.00072504
25 | 0.97126 | -0.55434 | 0.0071247 | 0.0017856
26 | 0.9719 | -0.54169 | 0.00059856 | 0.00015001
27 | 0.97189 | -0.54193 | 0.0018555 | 0.00046504
28 | 0.97121 | -0.55537 | 0.0052113 | 0.0013061
29 | 0.97108 | -0.55796 | 0 | 0
30 | 0.97092 | -0.56109 | 0 | 0
31 | 0.97076 | -0.56421 | 0.017802 | 0.0044616
32 | 0.9709 | -0.56151 | 0 | 0
33 | 0.99785 | -0.040484 | 0.0052479 | 0.0013152
34 | 0.994 | -0.11347 | 0.00050735 | 0.00012715
35 | 0.97749 | -0.4314 | 0.0072337 | 0.0018129
36 | 0.98425 | -0.29996 | 0.0021147 | 0.00053
37 | 0.98626 | -0.26112 | 0.0039684 | 0.00099456
38 | 0.97737 | -0.43383 | 0.0025292 | 0.00063388
39 | 0.97744 | -0.43238 | 0.0069208 | 0.0017345
40 | 0.98753 | -0.23667 | 0.0036013 | 0.00090258
41 | 0.98834 | -0.2213 | 0.0033671 | 0.00084387
42 | 0.99018 | -0.18611 | 0.00058011 | 0.00014539
43 | 0.97522 | -0.47587 | 0 | 0
44 | 0.97622 | -0.4563 | 0.01289 | 0.0032305
45 | 0.97488 | -0.48258 | 0.012948 | 0.003245
46 | 0.97256 | -0.52828 | 0.0077983 | 0.0019544
47 | 0.97619 | -0.45678 | 0.0078234 | 0.0019607
48 | 0.99025 | -0.18475 | 0.01006 | 0.0025212
49 | 0.9912 | -0.16656 | 0.00045406 | 0.0001138
50 | 0.99299 | -0.13245 | 0.00046678 | 0.00011699
51 | 0.99255 | -0.14093 | 0.0068405 | 0.0017144
52 | 0.99382 | -0.11692 | 0.0032561 | 0.00081605
53 | 0.99191 | -0.15384 | 0.0027443 | 0.0006878
54 | 0.99154 | -0.16098 | 0 | 0
55 | 0.99235 | -0.14534 | 0.003279 | 0.0008218
56 | 0.99349 | -0.12328 | 0.001471 | 0.00036867
57 | 0.99328 | -0.12728 | 0.004181 | 0.0010478
58 | 0.99326 | -0.12775 | 0.0014717 | 0.00036885
59 | 0.99281 | -0.13632 | 0.001324 | 0.00033184
60 | 0.99134 | -0.16491 | 0.012702 | 0.0031835
61 | 0.99141 | -0.16348 | 0.018733 | 0.0046948
62 | 0.99234 | -0.14543 | 0.0011118 | 0.00027865
63 | 0.99218 | -0.14869 | 0.0034355 | 0.00086102
64 | 0.97174 | -0.54452 | 0.027572 | 0.0069101
65 | 0.97214 | -0.53653 | 0.010096 | 0.0025303
66 | 0.97156 | -0.54796 | 0.012915 | 0.0032367
67 | 0.9917 | -0.1579 | 0.0022468 | 0.00056311
68 | 0.99173 | -0.15741 | 0.0038712 | 0.00097022
69 | 0.99185 | -0.15493 | 0.0036684 | 0.00091938
70 | 0.99188 | -0.15448 | 0.0039562 | 0.00099152
71 | 0.97088 | -0.56194 | 0.0010704 | 0.00026826
72 | 0.9709 | -0.56155 | 0 | 0
73 | 0.97089 | -0.56174 | 0.00049769 | 0.00012473
74 | 0.99208 | -0.15047 | 0.0039815 | 0.00099786
75 | 0.99198 | -0.15245 | 0.0054794 | 0.0013733
76 | 0.99196 | -0.15281 | 0.0040426 | 0.0010132
77 | 0.9919 | -0.15395 | 0.002928 | 0.00073383
78 | 0.97359 | -0.50804 | 0 | 0
79 | 0.97273 | -0.52502 | 0.013607 | 0.0034103
80 | 0.9732 | -0.5157 | 0.0099352 | 0.00249
81 | 0.97289 | -0.52176 | 0.0071177 | 0.0017839
82 | 0.97227 | -0.53401 | 0 | 0
83 | 0.97221 | -0.53518 | 0.00355 | 0.00088971
84 | 0.97215 | -0.53645 | 0.0091682 | 0.0022978
85 | 0.97206 | -0.53824 | 0.0096366 | 0.0024152
86 | 0.97198 | -0.53971 | 0.0016777 | 0.00042047
87 | 0.97256 | -0.52829 | 0 | 0
88 | 0.97162 | -0.54685 | 0.0091955 | 0.0023046
89 | 0.97193 | -0.54077 | 0 | 0
90 | 0.9725 | -0.5295 | 0.0027977 | 0.00070118
91 | 0.97242 | -0.53098 | 0.0027972 | 0.00070105
92 | 0.97142 | -0.55083 | 0.014668 | 0.0036761
93 | 0.97119 | -0.55537 | 0.0042455 | 0.001064
94 | 0.97155 | -0.54825 | 0 | 0
95 | 0.97117 | -0.55585 | 0.011603 | 0.002908
96 | 0.97104 | -0.5584 | 0.013499 | 0.0033831
97 | 0.99118 | -0.16803 | 0.013357 | 0.0033476
98 | 0.99125 | -0.16668 | 0.013359 | 0.0033482
99 | 0.99117 | -0.16809 | 0.0043001 | 0.0010777
100 | 0.99133 | -0.16498 | 0 | 0
101 | 0.97235 | -0.53235 | 0.0032171 | 0.00080627
102 | 0.97218 | -0.53591 | 0.0032196 | 0.0008069
103 | 0.97215 | -0.53644 | 0.012158 | 0.0030471
104 | 0.97247 | -0.53015 | 0.0027993 | 0.00070157
105 | 0.97211 | -0.53714 | 0.0032182 | 0.00080656
106 | 0.97242 | -0.53101 | 0.010034 | 0.0025147
107 | 0.97241 | -0.53124 | 0.0059337 | 0.0014871
108 | 0.97202 | -0.53905 | 0.0032174 | 0.00080636
109 | 0.97201 | -0.53907 | 0.011335 | 0.0028409
110 | 0.97201 | -0.53925 | 0.0032174 | 0.00080636
111 | 0.9719 | -0.54143 | 0 | 0
112 | 0.97186 | -0.54209 | 0.0018436 | 0.00046204
113 | 0.97187 | -0.54193 | 0.0034484 | 0.00086424
114 | 0.97182 | -0.54293 | 0.0088362 | 0.0022146
115 | 0.97181 | -0.54308 | 0.0014472 | 0.00036269
116 | 0.97181 | -0.54308 | 0.0015309 | 0.00038368
117 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.002264 | -0.00056741 | 0.0022641 | 0.00056718 | 1.0627e-07 | -2.2841e-07 | 0.0034542 | 0.0034541 | 0.0034542 | 0.97529 | -0.47469 | 0.97534 | -0.47371 | 0.94895
1 | -0.0043965 | -0.0011016 | 0.0043967 | 0.0011016 | 1.7904e-07 | -1.7866e-08 | 0.0067074 | 0.0067073 | 0.0067074 | 0.97534 | -0.47371 | 0.97538 | -0.47285 | 1.8427
2 | -0.0043967 | -0.0011016 | 0.004397 | 0.0011016 | 3.1131e-07 | -3.1097e-08 | 0.0067073 | 0.0067073 | 0.0067073 | 0.97538 | -0.47285 | 0.97546 | -0.47137 | 1.8427
3 | -0.0025063 | -0.00062813 | 0.0025065 | 0.0006278 | 1.9699e-07 | -3.2738e-07 | 0.0038131 | 0.0038129 | 0.0038131 | 0.97804 | -0.42068 | 0.97812 | -0.41903 | 1.0476
4 | -0.03029 | -0.007591 | 0.030302 | 0.0075986 | 1.2214e-05 | 7.6244e-06 | 0.04608 | 0.046079 | 0.04608 | 0.97812 | -0.41903 | 0.97856 | -0.41057 | 12.6592
5 | 0.044271 | 0.011111 | -0.044145 | -0.011053 | 0.0001262 | 5.7818e-05 | 0.067539 | 0.067548 | 0.067548 | 0.97546 | -0.47137 | 0.97242 | -0.53128 | 3.7114
6 | -0.050808 | -0.012749 | 0.050857 | 0.012773 | 4.9185e-05 | 2.4658e-05 | 0.07751 | 0.077507 | 0.07751 | 0.97546 | -0.47137 | 0.97649 | -0.45108 | 4.2588
7 | -0.11422 | -0.028693 | 0.11429 | 0.028733 | 6.5077e-05 | 3.9842e-05 | 0.17371 | 0.17371 | 0.17371 | 0.97856 | -0.41057 | 0.97916 | -0.39863 | 9.5447
8 | 0.07549 | 0.018982 | -0.075447 | -0.018956 | 4.3674e-05 | 2.5179e-05 | 0.11481 | 0.11482 | 0.11482 | 0.97856 | -0.41057 | 0.97794 | -0.42269 | 6.3086
9 | 0.040933 | 0.010248 | -0.040926 | -0.010245 | 7.6297e-06 | 3.2748e-06 | 0.062633 | 0.062633 | 0.062633 | 0.97242 | -0.53128 | 0.97223 | -0.53519 | 3.4414
10 | 0.00079087 | 0.00019751 | -0.00079084 | -0.0001982 | 3.0853e-08 | -6.8902e-07 | 0.0012049 | 0.0012052 | 0.0012052 | 0.97649 | -0.45108 | 0.97645 | -0.4519 | 0.33109
11 | -0.051648 | -0.012971 | 0.051696 | 0.012995 | 4.8403e-05 | 2.4456e-05 | 0.078712 | 0.07871 | 0.078712 | 0.97649 | -0.45108 | 0.97749 | -0.43145 | 4.3249
12 | -0.39706 | -0.10024 | 0.39775 | 0.10068 | 0.00068556 | 0.00043718 | 0.60367 | 0.60367 | 0.60367 | 0.97916 | -0.39863 | 0.98101 | -0.36266 | 33.1688
13 | 0.28278 | 0.071509 | -0.28202 | -0.071027 | 0.00075859 | 0.00048207 | 0.42996 | 0.42996 | 0.42996 | 0.97916 | -0.39863 | 0.9763 | -0.45472 | 23.6242
14 | 0.018509 | 0.0046411 | -0.018505 | -0.0046388 | 3.8449e-06 | 2.2986e-06 | 0.028164 | 0.028164 | 0.028164 | 0.97794 | -0.42269 | 0.97772 | -0.42705 | 7.7374
15 | 0.056938 | 0.014315 | -0.056926 | -0.014309 | 1.1318e-05 | 5.9828e-06 | 0.086652 | 0.086652 | 0.086652 | 0.97794 | -0.42269 | 0.97773 | -0.42685 | 4.7611
16 | -0.053776 | -0.013516 | 0.053779 | 0.013518 | 2.8008e-06 | 1.4434e-06 | 0.081876 | 0.081876 | 0.081876 | 0.97749 | -0.43145 | 0.97755 | -0.43036 | 4.4987
17 | -0.055921 | -0.014055 | 0.055931 | 0.01406 | 9.3817e-06 | 4.9223e-06 | 0.085137 | 0.085137 | 0.085137 | 0.97755 | -0.43036 | 0.97773 | -0.42685 | 4.6779
18 | -0.40752 | -0.10313 | 0.40875 | 0.10391 | 0.0012304 | 0.00078472 | 0.61849 | 0.61848 | 0.61849 | 0.98101 | -0.36266 | 0.98425 | -0.29996 | 33.9827
19 | 0.2613 | 0.065837 | -0.26104 | -0.065669 | 0.00026395 | 0.00016754 | 0.39839 | 0.39839 | 0.39839 | 0.9763 | -0.45472 | 0.97522 | -0.47587 | 21.8895
20 | 0.020715 | 0.00519 | -0.020713 | -0.0051903 | 1.5579e-06 | -3.0573e-07 | 0.031572 | 0.031573 | 0.031573 | 0.9763 | -0.45472 | 0.97622 | -0.4563 | 1.7348
21 | 0.57454 | 0.14823 | -0.57342 | -0.14751 | 0.0011182 | 0.00071435 | 0.85643 | 0.85643 | 0.85643 | 1 | 0 | 0.99787 | -0.040027 | 47.0566
22 | 0.005248 | 0.0013152 | -0.0052479 | -0.0013152 | 1.1431e-07 | 8.1374e-09 | 0.0078257 | 0.0078257 | 0.0078257 | 0.99787 | -0.040027 | 0.99785 | -0.040484 | 2.1499
23 | 0.56168 | 0.14457 | -0.55969 | -0.14329 | 0.0019987 | 0.0012767 | 0.83893 | 0.83893 | 0.83893 | 0.99787 | -0.040027 | 0.994 | -0.11347 | 46.0951
24 | 0.016688 | 0.0041833 | -0.016684 | -0.0041813 | 3.4584e-06 | 2.0341e-06 | 0.025398 | 0.025398 | 0.025398 | 0.97772 | -0.42705 | 0.97749 | -0.4314 | 6.9775
25 | 0.0053476 | 0.0013395 | -0.0053474 | -0.0013395 | 1.7315e-07 | 2.5412e-08 | 0.0081861 | 0.0081861 | 0.0081861 | 0.97202 | -0.53922 | 0.97199 | -0.5399 | 2.2489
26 | -0.0091797 | -0.0022999 | 0.0091815 | 0.0023008 | 1.7615e-06 | 8.3245e-07 | 0.014052 | 0.014052 | 0.014052 | 0.97202 | -0.53922 | 0.97223 | -0.53519 | 3.8606
27 | 0.0024543 | 0.00061463 | -0.0024541 | -0.00061494 | 1.8469e-07 | -3.1418e-07 | 0.0037572 | 0.0037573 | 0.0037573 | 0.97199 | -0.5399 | 0.97191 | -0.54148 | 1.0322
28 | 0.0028931 | 0.00072488 | -0.002893 | -0.00072504 | 1.5778e-07 | -1.6486e-07 | 0.004429 | 0.0044291 | 0.0044291 | 0.97199 | -0.5399 | 0.97193 | -0.54105 | 1.2168
29 | 0.031744 | 0.007944 | -0.031715 | -0.0079356 | 2.8908e-05 | 8.3858e-06 | 0.048581 | 0.048585 | 0.048585 | 0.97223 | -0.53519 | 0.97126 | -0.55434 | 2.6695
30 | 0.0024541 | 0.00061494 | -0.0024541 | -0.00061498 | 2.3877e-08 | -4.0611e-08 | 0.0037573 | 0.0037573 | 0.0037573 | 0.97191 | -0.54148 | 0.9719 | -0.54169 | 1.0322
31 | 0.024591 | 0.0061499 | -0.024589 | -0.0061499 | 1.2034e-06 | 7.0492e-08 | 0.037669 | 0.037669 | 0.037669 | 0.97126 | -0.55434 | 0.97121 | -0.55537 | 2.0697
32 | 0.0018556 | 0.00046497 | -0.0018555 | -0.00046504 | 2.1046e-08 | -7.2701e-08 | 0.0028409 | 0.0028409 | 0.0028409 | 0.9719 | -0.54169 | 0.97189 | -0.54193 | 0.78048
33 | 0.019378 | 0.0048438 | -0.019376 | -0.0048445 | 2.3828e-06 | -7.0542e-07 | 0.029685 | 0.029686 | 0.029686 | 0.97121 | -0.55537 | 0.97108 | -0.55796 | 1.6311
34 | 0.019376 | 0.0048445 | -0.019373 | -0.0048454 | 2.8874e-06 | -8.5384e-07 | 0.029686 | 0.029687 | 0.029687 | 0.97108 | -0.55796 | 0.97092 | -0.56109 | 1.6311
35 | 0.017805 | 0.0044604 | -0.017802 | -0.0044616 | 2.6468e-06 | -1.2364e-06 | 0.027286 | 0.027288 | 0.027288 | 0.97092 | -0.56109 | 0.97076 | -0.56421 | 1.4993
36 | 0.0015681 | 0.000385 | -0.0015681 | -0.00038939 | 3.0838e-08 | -4.3899e-06 | 0.0024004 | 0.002402 | 0.002402 | 0.97092 | -0.56109 | 0.9709 | -0.56151 | 0.13198
37 | 0.0004977 | 0.0001222 | -0.0004977 | -0.00012371 | 1.0593e-09 | -1.5028e-06 | 0.00076187 | 0.00076241 | 0.00076241 | 0.9709 | -0.56151 | 0.9709 | -0.56155 | 0.041891
38 | 0.0010704 | 0.00026719 | -0.0010704 | -0.00026826 | 2.2266e-08 | -1.0773e-06 | 0.0016401 | 0.0016405 | 0.0016405 | 0.9709 | -0.56151 | 0.97088 | -0.56194 | 0.22535
39 | 0.11514 | 0.028924 | -0.11512 | -0.028913 | 1.8917e-05 | 1.1557e-05 | 0.17239 | 0.17239 | 0.17239 | 0.994 | -0.11347 | 0.99382 | -0.11692 | 9.4718
40 | 0.44404 | 0.11424 | -0.44363 | -0.11398 | 0.00040942 | 0.00026123 | 0.66579 | 0.66579 | 0.66579 | 0.994 | -0.11347 | 0.99299 | -0.13245 | 36.5817
41 | 0.0094506 | 0.0023683 | -0.0094502 | -0.0023681 | 4.4283e-07 | 2.1189e-07 | 0.014386 | 0.014386 | 0.014386 | 0.97749 | -0.4314 | 0.97744 | -0.43238 | 3.9523
42 | -0.41086 | -0.10444 | 0.41163 | 0.10493 | 0.00077019 | 0.00049123 | 0.62168 | 0.62168 | 0.62168 | 0.98425 | -0.29996 | 0.98626 | -0.26112 | 34.1584
43 | -0.4156 | -0.10593 | 0.41609 | 0.10624 | 0.00049098 | 0.00031317 | 0.62767 | 0.62767 | 0.62767 | 0.98626 | -0.26112 | 0.98753 | -0.23667 | 34.4873
44 | -0.0025292 | -0.00063388 | 0.0025294 | 0.0006336 | 1.7469e-07 | -2.8197e-07 | 0.0038507 | 0.0038505 | 0.0038507 | 0.97737 | -0.43383 | 0.97744 | -0.43238 | 1.0579
45 | -0.41969 | -0.10714 | 0.42 | 0.10734 | 0.00031204 | 0.00019904 | 0.63309 | 0.63309 | 0.63309 | 0.98753 | -0.23667 | 0.98834 | -0.2213 | 34.7854
46 | -0.42337 | -0.10819 | 0.42409 | 0.10865 | 0.00072183 | 0.00046046 | 0.63816 | 0.63816 | 0.63816 | 0.98834 | -0.2213 | 0.99018 | -0.18611 | 35.0639
47 | -0.42467 | -0.10879 | 0.4247 | 0.10881 | 2.7867e-05 | 1.7777e-05 | 0.63903 | 0.63903 | 0.63903 | 0.99018 | -0.18611 | 0.99025 | -0.18475 | 35.1118
48 | 0.20247 | 0.050921 | -0.20241 | -0.05088 | 6.4913e-05 | 4.0979e-05 | 0.309 | 0.30901 | 0.30901 | 0.97522 | -0.47587 | 0.97488 | -0.48258 | 16.9783
49 | 0.058564 | 0.014748 | -0.058418 | -0.014655 | 0.00014636 | 9.3064e-05 | 0.089385 | 0.089385 | 0.089385 | 0.97522 | -0.47587 | 0.97256 | -0.52828 | 24.5563
50 | 0.0078236 | 0.0019598 | -0.0078234 | -0.0019607 | 1.7775e-07 | -9.2807e-07 | 0.011925 | 0.011925 | 0.011925 | 0.97622 | -0.4563 | 0.97619 | -0.45678 | 0.65523
51 | 0.18946 | 0.047635 | -0.18923 | -0.04749 | 0.00023008 | 0.00014497 | 0.28924 | 0.28924 | 0.28924 | 0.97488 | -0.48258 | 0.97359 | -0.50804 | 15.8925
52 | 0.05062 | 0.012701 | -0.0506 | -0.012688 | 1.9907e-05 | 1.2631e-05 | 0.077453 | 0.077453 | 0.077453 | 0.97256 | -0.52828 | 0.97214 | -0.53653 | 21.2784
53 | -0.43476 | -0.11133 | 0.43514 | 0.11157 | 0.00038352 | 0.00024468 | 0.65415 | 0.65415 | 0.65415 | 0.99025 | -0.18475 | 0.9912 | -0.16656 | 35.9424
54 | -0.4356 | -0.11169 | 0.43614 | 0.11203 | 0.0005421 | 0.00034586 | 0.65483 | 0.65483 | 0.65483 | 0.9912 | -0.16656 | 0.99255 | -0.14093 | 35.9798
55 | 0.44316 | 0.11387 | -0.44298 | -0.11375 | 0.00018237 | 0.00011636 | 0.66509 | 0.66509 | 0.66509 | 0.99299 | -0.13245 | 0.99255 | -0.14093 | 36.5432
56 | 0.11186 | 0.028097 | -0.11183 | -0.028076 | 3.3988e-05 | 2.0707e-05 | 0.16751 | 0.16751 | 0.16751 | 0.99382 | -0.11692 | 0.99349 | -0.12328 | 9.204
57 | 0.062487 | 0.015666 | -0.062466 | -0.015654 | 2.1256e-05 | 1.1523e-05 | 0.093742 | 0.093743 | 0.093743 | 0.99191 | -0.15384 | 0.99154 | -0.16098 | 5.1507
58 | -0.065231 | -0.016354 | 0.065258 | 0.016368 | 2.6428e-05 | 1.4538e-05 | 0.097859 | 0.097858 | 0.097859 | 0.99191 | -0.15384 | 0.99235 | -0.14534 | 5.3769
59 | 0.043731 | 0.010961 | -0.043723 | -0.010957 | 8.1872e-06 | 3.6056e-06 | 0.065628 | 0.065628 | 0.065628 | 0.99154 | -0.16098 | 0.99134 | -0.16491 | 3.6059
60 | 0.018735 | 0.0046938 | -0.018733 | -0.0046948 | 2.2269e-06 | -9.9689e-07 | 0.028115 | 0.028116 | 0.028116 | 0.99154 | -0.16098 | 0.99141 | -0.16348 | 1.5448
61 | -0.10327 | -0.025892 | 0.10332 | 0.025919 | 4.4432e-05 | 2.684e-05 | 0.15486 | 0.15486 | 0.15486 | 0.99235 | -0.14534 | 0.99281 | -0.13632 | 8.5087
62 | 0.034735 | 0.0087016 | -0.034734 | -0.0087016 | 1.4178e-07 | 4.5722e-08 | 0.052083 | 0.052083 | 0.052083 | 0.99235 | -0.14534 | 0.99234 | -0.14543 | 2.8617
63 | 0.11036 | 0.027707 | -0.11034 | -0.027694 | 2.101e-05 | 1.2783e-05 | 0.16531 | 0.16531 | 0.16531 | 0.99349 | -0.12328 | 0.99328 | -0.12728 | 9.0829
64 | 0.10616 | 0.026647 | -0.10615 | -0.026645 | 2.3981e-06 | 1.453e-06 | 0.15905 | 0.15905 | 0.15905 | 0.99328 | -0.12728 | 0.99326 | -0.12775 | 8.7388
65 | 0.10468 | 0.026276 | -0.10464 | -0.02625 | 4.2762e-05 | 2.5869e-05 | 0.15684 | 0.15684 | 0.15684 | 0.99326 | -0.12775 | 0.99281 | -0.13632 | 8.6177
66 | 0.031021 | 0.0077735 | -0.03102 | -0.0077735 | 9.342e-08 | 2.2751e-08 | 0.046562 | 0.046562 | 0.046562 | 0.99134 | -0.16491 | 0.99133 | -0.16498 | 2.5584
67 | 0.033623 | 0.0084229 | -0.033617 | -0.0084214 | 5.224e-06 | 1.5735e-06 | 0.050416 | 0.050416 | 0.050416 | 0.99234 | -0.14543 | 0.99218 | -0.14869 | 2.7701
68 | 0.030182 | 0.0075603 | -0.030179 | -0.0075598 | 2.5557e-06 | 5.6175e-07 | 0.045264 | 0.045264 | 0.045264 | 0.99218 | -0.14869 | 0.99208 | -0.15047 | 2.487
69 | -0.040488 | -0.010148 | 0.040504 | 0.010158 | 1.5429e-05 | 9.7421e-06 | 0.062 | 0.062 | 0.062 | 0.97174 | -0.54452 | 0.97214 | -0.53653 | 17.0329
70 | 0.012917 | 0.0032379 | -0.012915 | -0.0032367 | 2.1155e-06 | 1.1753e-06 | 0.01978 | 0.01978 | 0.01978 | 0.97174 | -0.54452 | 0.97156 | -0.54796 | 5.434
71 | -0.0022468 | -0.00056311 | 0.0022469 | 0.00056298 | 5.2981e-08 | -1.2648e-07 | 0.0033713 | 0.0033712 | 0.0033713 | 0.9917 | -0.1579 | 0.99173 | -0.15741 | 0.92618
72 | -0.0061181 | -0.0015332 | 0.0061188 | 0.0015325 | 7.2269e-07 | -7.1803e-07 | 0.0091798 | 0.0091794 | 0.0091798 | 0.99173 | -0.15741 | 0.99185 | -0.15493 | 1.261
73 | -0.0097872 | -0.0024519 | 0.0097874 | 0.0024512 | 2.0776e-07 | -6.9625e-07 | 0.014683 | 0.014683 | 0.014683 | 0.99185 | -0.15493 | 0.99188 | -0.15448 | 0.80675
74 | -0.013744 | -0.0034427 | 0.013744 | 0.0034422 | 3.5153e-07 | -4.8662e-07 | 0.020618 | 0.020617 | 0.020618 | 0.99188 | -0.15448 | 0.9919 | -0.15395 | 1.1328
75 | 0.0004977 | 0.00012371 | -0.00049769 | -0.00012473 | 4.5373e-09 | -1.0263e-06 | 0.00076241 | 0.00076278 | 0.00076278 | 0.9709 | -0.56155 | 0.97089 | -0.56174 | 0.10478
76 | 0.026198 | 0.0065619 | -0.026195 | -0.0065617 | 2.4725e-06 | 2.0397e-07 | 0.039292 | 0.039293 | 0.039293 | 0.99208 | -0.15047 | 0.99198 | -0.15245 | 2.1589
77 | 0.020716 | 0.0051885 | -0.020716 | -0.0051885 | 3.4939e-07 | -8.7811e-08 | 0.031074 | 0.031074 | 0.031074 | 0.99198 | -0.15245 | 0.99196 | -0.15281 | 1.7073
78 | 0.016673 | 0.0041754 | -0.016672 | -0.004176 | 9.0486e-07 | -6.6583e-07 | 0.025009 | 0.02501 | 0.02501 | 0.99196 | -0.15281 | 0.9919 | -0.15395 | 1.3742
79 | 0.077644 | 0.019482 | -0.077582 | -0.019445 | 6.2817e-05 | 3.6509e-05 | 0.11868 | 0.11868 | 0.11868 | 0.97359 | -0.50804 | 0.97273 | -0.52502 | 6.5209
80 | 0.11159 | 0.028008 | -0.11155 | -0.027983 | 4.0764e-05 | 2.4928e-05 | 0.17056 | 0.17056 | 0.17056 | 0.97359 | -0.50804 | 0.9732 | -0.5157 | 9.3717
81 | 0.063974 | 0.016035 | -0.063965 | -0.016029 | 9.9444e-06 | 5.5053e-06 | 0.097865 | 0.097865 | 0.097865 | 0.97273 | -0.52502 | 0.97256 | -0.52829 | 5.3772
82 | 0.10161 | 0.025493 | -0.10158 | -0.025476 | 2.9322e-05 | 1.776e-05 | 0.15537 | 0.15537 | 0.15537 | 0.9732 | -0.5157 | 0.97289 | -0.52176 | 8.5371
83 | 0.094465 | 0.023692 | -0.09441 | -0.023659 | 5.5152e-05 | 3.3111e-05 | 0.14449 | 0.14449 | 0.14449 | 0.97289 | -0.52176 | 0.97227 | -0.53401 | 7.9389
84 | 0.066449 | 0.016662 | -0.066445 | -0.01666 | 3.6802e-06 | 2.0612e-06 | 0.1017 | 0.1017 | 0.1017 | 0.97227 | -0.53401 | 0.97221 | -0.53518 | 5.5879
85 | 0.027961 | 0.0069962 | -0.027957 | -0.0069956 | 3.2381e-06 | 6.1031e-07 | 0.042788 | 0.042789 | 0.042789 | 0.97227 | -0.53401 | 0.97215 | -0.53645 | 2.351
86 | 0.062895 | 0.015771 | -0.062886 | -0.015766 | 9.1852e-06 | 5.0593e-06 | 0.096267 | 0.096267 | 0.096267 | 0.97221 | -0.53518 | 0.97206 | -0.53824 | 5.2894
87 | 0.018789 | 0.0046978 | -0.018786 | -0.0046989 | 2.9183e-06 | -1.0489e-06 | 0.028756 | 0.028757 | 0.028757 | 0.97215 | -0.53645 | 0.97198 | -0.53971 | 1.58
88 | 0.053249 | 0.01335 | -0.053228 | -0.013339 | 2.1841e-05 | 1.1263e-05 | 0.081516 | 0.081517 | 0.081517 | 0.97206 | -0.53824 | 0.97162 | -0.54685 | 4.4789
89 | 0.017109 | 0.0042784 | -0.017108 | -0.0042789 | 8.5469e-07 | -4.8267e-07 | 0.026188 | 0.026189 | 0.026189 | 0.97198 | -0.53971 | 0.97193 | -0.54077 | 1.4389
90 | 0.021567 | 0.0054031 | -0.021566 | -0.0054033 | 1.2485e-06 | -1.4951e-07 | 0.032997 | 0.032997 | 0.032997 | 0.97256 | -0.52829 | 0.9725 | -0.5295 | 1.813
91 | 0.042397 | 0.010626 | -0.042392 | -0.010624 | 5.4428e-06 | 2.4135e-06 | 0.064868 | 0.064869 | 0.064869 | 0.97256 | -0.52829 | 0.97242 | -0.53098 | 3.5642
92 | 0.044032 | 0.011034 | -0.044029 | -0.011033 | 2.9348e-06 | 1.3454e-06 | 0.067434 | 0.067434 | 0.067434 | 0.97162 | -0.54685 | 0.97155 | -0.54825 | 3.7052
93 | 0.0034486 | 0.00085871 | -0.0034485 | -0.00086186 | 1.0864e-07 | -3.1523e-06 | 0.0052777 | 0.0052789 | 0.0052789 | 0.97193 | -0.54077 | 0.9719 | -0.54143 | 0.29005
94 | 0.013659 | 0.0034202 | -0.013658 | -0.0034213 | 8.6282e-07 | -1.0779e-06 | 0.020911 | 0.020912 | 0.020912 | 0.97193 | -0.54077 | 0.97186 | -0.54209 | 1.149
95 | 0.018768 | 0.0047021 | -0.018768 | -0.0047023 | 5.8084e-07 | -2.1087e-07 | 0.028716 | 0.028717 | 0.028717 | 0.9725 | -0.5295 | 0.97247 | -0.53015 | 1.5778
96 | 0.039595 | 0.0099228 | -0.039592 | -0.0099217 | 2.579e-06 | 1.0695e-06 | 0.060588 | 0.060588 | 0.060588 | 0.97242 | -0.53098 | 0.97235 | -0.53235 | 3.329
97 | 0.029356 | 0.0073545 | -0.02935 | -0.0073531 | 6.3542e-06 | 1.4736e-06 | 0.044966 | 0.044967 | 0.044967 | 0.97142 | -0.55083 | 0.97119 | -0.55537 | 2.4707
98 | -0.044024 | -0.011031 | 0.044029 | 0.011033 | 5.3999e-06 | 2.4757e-06 | 0.067434 | 0.067434 | 0.067434 | 0.97142 | -0.55083 | 0.97155 | -0.54825 | 3.7052
99 | 0.025104 | 0.006289 | -0.025103 | -0.006289 | 5.6769e-07 | 4.676e-08 | 0.038462 | 0.038462 | 0.038462 | 0.97119 | -0.55537 | 0.97117 | -0.55585 | 2.1133
100 | 0.0135 | 0.003381 | -0.013499 | -0.0033831 | 1.6424e-06 | -2.1149e-06 | 0.020684 | 0.020685 | 0.020685 | 0.97117 | -0.55585 | 0.97104 | -0.5584 | 1.1366
101 | -0.017657 | -0.0044253 | 0.017658 | 0.0044247 | 1.1377e-06 | -6.632e-07 | 0.026508 | 0.026508 | 0.026508 | 0.99118 | -0.16803 | 0.99125 | -0.16668 | 1.4565
102 | 0.0043001 | 0.0010777 | -0.0043001 | -0.0010777 | 1.2778e-08 | -2.3603e-09 | 0.0064556 | 0.0064556 | 0.0064556 | 0.99118 | -0.16803 | 0.99117 | -0.16809 | 1.7735
103 | -0.031018 | -0.0077729 | 0.03102 | 0.0077735 | 2.5166e-06 | 6.1301e-07 | 0.046562 | 0.046562 | 0.046562 | 0.99125 | -0.16668 | 0.99133 | -0.16498 | 2.5584
104 | 0.036375 | 0.0091155 | -0.036369 | -0.0091132 | 6.1659e-06 | 2.301e-06 | 0.055665 | 0.055666 | 0.055666 | 0.97235 | -0.53235 | 0.97218 | -0.53591 | 3.0586
105 | 0.033149 | 0.0083063 | -0.033149 | -0.008306 | 8.39e-07 | 2.6756e-07 | 0.050738 | 0.050738 | 0.050738 | 0.97218 | -0.53591 | 0.97215 | -0.53644 | 2.7878
106 | 0.020991 | 0.0052589 | -0.02099 | -0.005259 | 7.0479e-07 | -1.1328e-07 | 0.032128 | 0.032129 | 0.032129 | 0.97215 | -0.53644 | 0.97211 | -0.53714 | 1.7653
107 | 0.015968 | 0.0040007 | -0.015968 | -0.0040012 | 6.5184e-07 | -4.8589e-07 | 0.024433 | 0.024434 | 0.024434 | 0.97247 | -0.53015 | 0.97242 | -0.53101 | 1.3425
108 | 0.017772 | 0.0044525 | -0.01777 | -0.0044532 | 1.612e-06 | -7.6861e-07 | 0.027203 | 0.027203 | 0.027203 | 0.97211 | -0.53714 | 0.97202 | -0.53905 | 1.4947
109 | 0.0059337 | 0.0014865 | -0.0059337 | -0.0014871 | 6.6248e-08 | -6.2217e-07 | 0.0090797 | 0.0090799 | 0.0090799 | 0.97242 | -0.53101 | 0.97241 | -0.53124 | 0.4989
110 | 0.014553 | 0.0036469 | -0.014553 | -0.0036469 | 1.7976e-08 | -1.8424e-08 | 0.022278 | 0.022278 | 0.022278 | 0.97202 | -0.53905 | 0.97201 | -0.53907 | 1.2241
111 | 0.0032174 | 0.00080604 | -0.0032174 | -0.00080636 | 2.7036e-08 | -3.1423e-07 | 0.0049253 | 0.0049254 | 0.0049254 | 0.97201 | -0.53907 | 0.97201 | -0.53925 | 0.45105
112 | 0.0034485 | 0.00086186 | -0.0034484 | -0.00086424 | 8.2245e-08 | -2.3852e-06 | 0.0052789 | 0.0052797 | 0.0052797 | 0.9719 | -0.54143 | 0.97187 | -0.54193 | 0.2901
113 | 0.011815 | 0.0029592 | -0.011814 | -0.0029601 | 4.7013e-07 | -8.8595e-07 | 0.018089 | 0.018089 | 0.018089 | 0.97186 | -0.54209 | 0.97182 | -0.54293 | 0.99392
114 | 0.0029781 | 0.00074554 | -0.0029781 | -0.00074637 | 2.1419e-08 | -8.3723e-07 | 0.0045596 | 0.0045599 | 0.0045599 | 0.97182 | -0.54293 | 0.97181 | -0.54308 | 0.25055
115 | 0.0015309 | 0.00038368 | -0.0015309 | -0.00038368 | 4.2776e-11 | -2.467e-10 | 0.0023441 | 0.0023441 | 0.0023441 | 0.97181 | -0.54308 | 0.97181 | -0.54308 | 0.64398

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59089 | 0.15191

## res_load
| p_mw | q_mvar
0 | 0.002264 | 0.00056741
1 | 0.0021324 | 0.00053444
2 | 0.0025063 | 0.00062813
3 | 0.027783 | 0.0069631
4 | 0.0021392 | 0.00053613
5 | 0.0084304 | 0.0021129
6 | 0.0032119 | 0.00080498
7 | 0.00208 | 0.0005213
8 | 0.0021425 | 0.00053696
9 | 0.00099559 | 0.00024952
10 | 0.00079084 | 0.0001982
11 | 0.0097663 | 0.0024477
12 | 0.014698 | 0.0036836
13 | 0.0064879 | 0.001626
14 | 0.0018174 | 0.00045548
15 | 0.0038321 | 0.00096041
16 | 0.002893 | 0.00072504
17 | 0.0071247 | 0.0017856
18 | 0.00059856 | 0.00015001
19 | 0.0018555 | 0.00046504
20 | 0.0052113 | 0.0013061
21 | 0.017802 | 0.0044616
22 | 0.0052479 | 0.0013152
23 | 0.00050735 | 0.00012715
24 | 0.0072337 | 0.0018129
25 | 0.0021147 | 0.00053
26 | 0.0039684 | 0.00099456
27 | 0.0025292 | 0.00063388
28 | 0.0069208 | 0.0017345
29 | 0.0036013 | 0.00090258
30 | 0.0033671 | 0.00084387
31 | 0.00058011 | 0.00014539
32 | 0.01289 | 0.0032305
33 | 0.012948 | 0.003245
34 | 0.0077983 | 0.0019544
35 | 0.0078234 | 0.0019607
36 | 0.01006 | 0.0025212
37 | 0.00045406 | 0.0001138
38 | 0.00046678 | 0.00011699
39 | 0.0068405 | 0.0017144
40 | 0.0032561 | 0.00081605
41 | 0.0027443 | 0.0006878
42 | 0.003279 | 0.0008218
43 | 0.001471 | 0.00036867
44 | 0.004181 | 0.0010478
45 | 0.0014717 | 0.00036885
46 | 0.001324 | 0.00033184
47 | 0.012702 | 0.0031835
48 | 0.018733 | 0.0046948
49 | 0.0011118 | 0.00027865
50 | 0.0034355 | 0.00086102
51 | 0.027572 | 0.0069101
52 | 0.010096 | 0.0025303
53 | 0.012915 | 0.0032367
54 | 0.0022468 | 0.00056311
55 | 0.0038712 | 0.00097022
56 | 0.0036684 | 0.00091938
57 | 0.0039562 | 0.00099152
58 | 0.0010704 | 0.00026826
59 | 0.00049769 | 0.00012473
60 | 0.0039815 | 0.00099786
61 | 0.0054794 | 0.0013733
62 | 0.0040426 | 0.0010132
63 | 0.002928 | 0.00073383
64 | 0.013607 | 0.0034103
65 | 0.0099352 | 0.00249
66 | 0.0071177 | 0.0017839
67 | 0.00355 | 0.00088971
68 | 0.0091682 | 0.0022978
69 | 0.0096366 | 0.0024152
70 | 0.0016777 | 0.00042047
71 | 0.0091955 | 0.0023046
72 | 0.0027977 | 0.00070118
73 | 0.0027972 | 0.00070105
74 | 0.014668 | 0.0036761
75 | 0.0042455 | 0.001064
76 | 0.011603 | 0.002908
77 | 0.013499 | 0.0033831
78 | 0.013357 | 0.0033476
79 | 0.013359 | 0.0033482
80 | 0.0043001 | 0.0010777
81 | 0.0032171 | 0.00080627
82 | 0.0032196 | 0.0008069
83 | 0.012158 | 0.0030471
84 | 0.0027993 | 0.00070157
85 | 0.0032182 | 0.00080656
86 | 0.010034 | 0.0025147
87 | 0.0059337 | 0.0014871
88 | 0.0032174 | 0.00080636
89 | 0.011335 | 0.0028409
90 | 0.0032174 | 0.00080636
91 | 0.0018436 | 0.00046204
92 | 0.0034484 | 0.00086424
93 | 0.0088362 | 0.0022146
94 | 0.0014472 | 0.00036269
95 | 0.0015309 | 0.00038368

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1