## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-5_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-5_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-5_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-5_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1054-5_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1054-5_0_6_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_1054-5_0_6_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1054-5_0_6_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1054-5_0_6_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_1054-5_0_6_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1054-5_0_6_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1054-5_0_6_node_69 | 0.4 | n |  | TRUE
12 | bus_LV_1054-5_0_6_node_70 | 0.4 | n |  | TRUE
13 | bus_LV_1054-5_0_6_node_68 | 0.4 | n |  | TRUE
14 | bus_LV_1054-5_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1054-5_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1054-5_0_6_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1054-5_0_6_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_1054-5_0_6_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1054-5_0_6_node_71 | 0.4 | n |  | TRUE
20 | bus_LV_1054-5_0_6_node_72 | 0.4 | n |  | TRUE
21 | bus_LV_1054-5_0_6_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_1054-5_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1054-5_0_6_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_1054-5_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1054-5_0_6_node_77 | 0.4 | n |  | TRUE
26 | bus_LV_1054-5_0_6_node_84 | 0.4 | n |  | TRUE
27 | bus_LV_1054-5_0_6_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1054-5_0_6_node_83 | 0.4 | n |  | TRUE
29 | bus_LV_1054-5_0_6_node_5 | 0.4 | n |  | TRUE
30 | bus_LV_1054-5_0_6_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_1054-5_0_6_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1054-5_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1054-5_0_6_node_74 | 0.4 | n |  | TRUE
34 | bus_LV_1054-5_0_6_node_80 | 0.4 | n |  | TRUE
35 | bus_LV_1054-5_0_6_node_82 | 0.4 | n |  | TRUE
36 | bus_LV_1054-5_0_6_node_67 | 0.4 | n |  | TRUE
37 | bus_LV_1054-5_0_6_node_58 | 0.4 | n |  | TRUE
38 | bus_LV_1054-5_0_6_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_1054-5_0_6_node_76 | 0.4 | n |  | TRUE
40 | bus_LV_1054-5_0_6_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_1054-5_0_6_node_78 | 0.4 | n |  | TRUE
42 | bus_LV_1054-5_0_6_node_99 | 0.4 | n |  | TRUE
43 | bus_LV_1054-5_0_6_node_81 | 0.4 | n |  | TRUE
44 | bus_LV_1054-5_0_6_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_1054-5_0_6_node_17 | 0.4 | n |  | TRUE
46 | bus_LV_1054-5_0_6_node_19 | 0.4 | n |  | TRUE
47 | bus_LV_1054-5_0_6_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_1054-5_0_6_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1054-5_0_6_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1054-5_0_6_node_23 | 0.4 | n |  | TRUE
51 | bus_LV_1054-5_0_6_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_1054-5_0_6_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_1054-5_0_6_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_1054-5_0_6_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_1054-5_0_6_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_1054-5_0_6_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_1054-5_0_6_node_114 | 0.4 | n |  | TRUE
58 | bus_LV_1054-5_0_6_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_1054-5_0_6_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_1054-5_0_6_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_1054-5_0_6_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_1054-5_0_6_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1054-5_0_6_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1054-5_0_6_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_1054-5_0_6_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_1054-5_0_6_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_1054-5_0_6_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_1054-5_0_6_node_116 | 0.4 | n |  | TRUE
69 | bus_LV_1054-5_0_6_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1054-5_0_6_node_66 | 0.4 | n |  | TRUE
71 | bus_LV_1054-5_0_6_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_1054-5_0_6_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_1054-5_0_6_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_1054-5_0_6_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_1054-5_0_6_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_1054-5_0_6_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_1054-5_0_6_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_1054-5_0_6_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_1054-5_0_6_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_1054-5_0_6_node_92 | 0.4 | n |  | TRUE
81 | bus_LV_1054-5_0_6_node_91 | 0.4 | n |  | TRUE
82 | bus_LV_1054-5_0_6_node_110 | 0.4 | n |  | TRUE
83 | bus_LV_1054-5_0_6_node_94 | 0.4 | n |  | TRUE
84 | bus_LV_1054-5_0_6_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_1054-5_0_6_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_1054-5_0_6_node_87 | 0.4 | n |  | TRUE
87 | bus_LV_1054-5_0_6_node_88 | 0.4 | n |  | TRUE
88 | bus_LV_1054-5_0_6_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_1054-5_0_6_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_1054-5_0_6_node_107 | 0.4 | n |  | TRUE
91 | bus_LV_1054-5_0_6_node_100 | 0.4 | n |  | TRUE
92 | bus_LV_1054-5_0_6_node_105 | 0.4 | n |  | TRUE
93 | bus_LV_1054-5_0_6_node_101 | 0.4 | n |  | TRUE
94 | bus_LV_1054-5_0_6_node_93 | 0.4 | n |  | TRUE
95 | bus_LV_1054-5_0_6_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_1054-5_0_6_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_1054-5_0_6_node_102 | 0.4 | n |  | TRUE
98 | bus_LV_1054-5_0_6_node_109 | 0.4 | n |  | TRUE
99 | bus_LV_1054-5_0_6_node_111 | 0.4 | n |  | TRUE
100 | bus_LV_1054-5_0_6_node_112 | 0.4 | n |  | TRUE
101 | bus_LV_1054-5_0_6_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_1054-5_0_6_node_113 | 0.4 | n |  | TRUE
103 | bus_LV_1054-5_0_6_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1054-5_0_6_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_1054-5_0_6_node_122 | 0.4 | n |  | TRUE
106 | bus_LV_1054-5_0_6_node_108 | 0.4 | n |  | TRUE
107 | bus_LV_1054-5_0_6_node_119 | 0.4 | n |  | TRUE
108 | bus_LV_1054-5_0_6_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_1054-5_0_6_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_1054-5_0_6_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_1054-5_0_6_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_1054-5_0_6_node_117 | 0.4 | n |  | TRUE
113 | bus_LV_1054-5_0_6_node_118 | 0.4 | n |  | TRUE
114 | bus_MV_211_0_node_172 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-5_0_6_load_0 | 0 | 0.0059508 | 0.0014914 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-5_0_6_load_1 | 1 | 0.0026552 | 0.00066547 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-5_0_6_load_2 | 2 | 0.00097895 | 0.00024535 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-5_0_6_load_31 | 6 | 0.00053305 | 0.00013359 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-5_0_6_load_32 | 8 | 0.0051039 | 0.0012792 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-5_0_6_load_18 | 9 | 0.0020896 | 0.0005237 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-5_0_6_load_69 | 11 | 0.022394 | 0.0056126 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-5_0_6_load_70 | 12 | 0.025965 | 0.0065075 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-5_0_6_load_68 | 13 | 0.008722 | 0.0021859 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-5_0_6_load_33 | 16 | 0.0041211 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-5_0_6_load_71 | 19 | 0.0069216 | 0.0017347 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-5_0_6_load_72 | 20 | 0.006024 | 0.0015098 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-5_0_6_load_43 | 21 | 0.00461 | 0.0011554 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-5_0_6_load_28 | 23 | 0.0058688 | 0.0014709 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-5_0_6_load_84 | 26 | 0.018076 | 0.0045302 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-5_0_6_load_83 | 28 | 0.017271 | 0.0043285 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-5_0_6_load_5 | 29 | 0.0082615 | 0.0020705 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-5_0_6_load_46 | 30 | 0.0021873 | 0.0005482 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-5_0_6_load_22 | 32 | 0.00091275 | 0.00022876 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-5_0_6_load_80 | 34 | 0.04559 | 0.011426 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-5_0_6_load_67 | 36 | 0.0043896 | 0.0011001 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-5_0_6_load_58 | 37 | 0.0031625 | 0.00079259 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-5_0_6_load_42 | 38 | 0.002358 | 0.00059097 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-5_0_6_load_99 | 42 | 0.0065835 | 0.00165 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-5_0_6_load_81 | 43 | 0.016322 | 0.0040908 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-5_0_6_load_27 | 44 | 0.024494 | 0.0061388 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-5_0_6_load_17 | 45 | 0.0023483 | 0.00058855 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-5_0_6_load_19 | 46 | 0.0022864 | 0.00057303 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-5_0_6_load_21 | 47 | 0.0029997 | 0.00075179 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-5_0_6_load_35 | 48 | 0.0017492 | 0.00043838 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-5_0_6_load_36 | 49 | 0.0017714 | 0.00044395 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-5_0_6_load_23 | 50 | 0.001834 | 0.00045965 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-5_0_6_load_25 | 51 | 0.0017392 | 0.00043588 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-5_0_6_load_34 | 52 | 0.0025289 | 0.00063379 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-5_0_6_load_40 | 53 | 0.0011078 | 0.00027764 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-5_0_6_load_29 | 55 | 0.0049399 | 0.0012381 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-5_0_6_load_30 | 56 | 0.0058439 | 0.0014646 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-5_0_6_load_114 | 57 | 0.0058688 | 0.0014708 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-5_0_6_load_51 | 60 | 0.0003821 | 9.5763e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-5_0_6_load_37 | 61 | 0.016381 | 0.0041054 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-5_0_6_load_50 | 62 | 0.00041992 | 0.00010524 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-5_0_6_load_48 | 63 | 0.00065042 | 0.00016301 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-5_0_6_load_49 | 64 | 0.00048845 | 0.00012242 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-5_0_6_load_73 | 65 | 0.0047154 | 0.0011818 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-5_0_6_load_116 | 68 | 0.0097785 | 0.0024507 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-5_0_6_load_65 | 69 | 0.00042875 | 0.00010745 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-5_0_6_load_66 | 70 | 0.021588 | 0.0054105 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-5_0_6_load_61 | 71 | 0.0029356 | 0.00073573 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-5_0_6_load_54 | 72 | 0.0050741 | 0.0012717 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-5_0_6_load_55 | 73 | 0.0024907 | 0.00062424 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-5_0_6_load_56 | 74 | 0.0037789 | 0.00094708 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-5_0_6_load_57 | 75 | 0.003428 | 0.00085914 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-5_0_6_load_59 | 76 | 0.0064928 | 0.0016273 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-5_0_6_load_60 | 77 | 0.0050156 | 0.001257 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-5_0_6_load_62 | 78 | 0.0065277 | 0.001636 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-5_0_6_load_64 | 79 | 0.0083503 | 0.0020928 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-5_0_6_load_92 | 80 | 0.0040554 | 0.0010164 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-5_0_6_load_91 | 81 | 0.0012632 | 0.00031659 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-5_0_6_load_110 | 82 | 0.0013959 | 0.00034985 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-5_0_6_load_85 | 84 | 0.0019412 | 0.0004865 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-5_0_6_load_86 | 85 | 0.001801 | 0.00045136 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-5_0_6_load_87 | 86 | 0.0016511 | 0.00041382 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-5_0_6_load_88 | 87 | 0.0016519 | 0.00041401 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-5_0_6_load_89 | 88 | 0.0021054 | 0.00052765 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-5_0_6_load_90 | 89 | 0.0019464 | 0.00048782 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-5_0_6_load_107 | 90 | 0.0024556 | 0.00061543 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-5_0_6_load_100 | 91 | 0.0014555 | 0.00036477 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-5_0_6_load_105 | 92 | 0.0025787 | 0.00064628 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-5_0_6_load_101 | 93 | 0.0011216 | 0.00028109 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-5_0_6_load_102 | 97 | 0.0019329 | 0.00048444 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-5_0_6_load_109 | 98 | 0.0075569 | 0.0018939 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-5_0_6_load_112 | 100 | 0.0042356 | 0.0010615 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-5_0_6_load_121 | 104 | 0.0030409 | 0.00076212 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-5_0_6_load_122 | 105 | 0.0013461 | 0.00033738 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-5_0_6_load_108 | 106 | 0.0011307 | 0.00028337 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-5_0_6_load_119 | 107 | 0.014358 | 0.0035985 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-5_0_6_load_103 | 108 | 0.0023274 | 0.00058331 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-5_0_6_load_104 | 109 | 0.0019292 | 0.0004835 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-5_0_6_load_106 | 110 | 0.0017624 | 0.0004417 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-5_0_6_load_120 | 111 | 0.010467 | 0.0026233 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-5_0_6_load_117 | 112 | 0.0063307 | 0.0015866 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-5_0_6_load_118 | 113 | 0.012157 | 0.0030468 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-5_0_6_line_0 |  | 0 | 1 | 0.0026767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-5_0_6_line_1 |  | 0 | 2 | 0.028159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-5_0_6_line_2 |  | 1 | 3 | 0.012698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-5_0_6_line_3 |  | 2 | 4 | 0.044753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-5_0_6_line_4 |  | 3 | 5 | 0.012907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-5_0_6_line_5 |  | 4 | 6 | 0.015931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-5_0_6_line_6 |  | 4 | 7 | 0.055492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-5_0_6_line_7 |  | 5 | 8 | 0.019882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-5_0_6_line_8 |  | 5 | 9 | 0.002412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-5_0_6_line_9 |  | 6 | 30 | 0.004172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-5_0_6_line_10 |  | 7 | 31 | 0.071562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-5_0_6_line_11 |  | 7 | 32 | 0.054428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-5_0_6_line_12 |  | 8 | 16 | 0.021609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1054-5_0_6_line_13 |  | 9 | 45 | 0.0006458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-5_0_6_line_14 |  | 10 | 11 | 0.033279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-5_0_6_line_15 |  | 10 | 12 | 0.030341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1054-5_0_6_line_16 |  | 10 | 13 | 0.074519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1054-5_0_6_line_17 |  | 11 | 34 | 0.019681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-5_0_6_line_18 |  | 12 | 35 | 0.03431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1054-5_0_6_line_19 |  | 13 | 18 | 0.017691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1054-5_0_6_line_20 |  | 14 | 15 | 0.045609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-5_0_6_line_21 |  | 14 | 16 | 0.0085457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1054-5_0_6_line_22 |  | 14 | 17 | 0.036879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1054-5_0_6_line_23 |  | 15 | 21 | 0.014258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-5_0_6_line_24 |  | 17 | 29 | 0.021105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-5_0_6_line_25 |  | 17 | 27 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1054-5_0_6_line_26 |  | 18 | 19 | 0.042161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1054-5_0_6_line_27 |  | 18 | 20 | 0.01578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-5_0_6_line_28 |  | 19 | 33 | 0.035157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1054-5_0_6_line_29 |  | 21 | 38 | 0.032708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-5_0_6_line_30 |  | 22 | 23 | 0.039131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-5_0_6_line_31 |  | 22 | 24 | 0.065716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-5_0_6_line_32 |  | 23 | 44 | 0.02649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-5_0_6_line_33 |  | 24 | 25 | 0.10766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1054-5_0_6_line_34 |  | 24 | 26 | 0.050105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1054-5_0_6_line_35 |  | 25 | 43 | 0.034476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1054-5_0_6_line_36 |  | 26 | 35 | 0.0059507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1054-5_0_6_line_37 |  | 27 | 28 | 0.0083384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1054-5_0_6_line_38 |  | 28 | 35 | 0.040892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1054-5_0_6_line_39 |  | 30 | 59 | 0.019602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1054-5_0_6_line_40 |  | 31 | 53 | 0.056026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1054-5_0_6_line_41 |  | 32 | 50 | 0.029644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1054-5_0_6_line_42 |  | 33 | 39 | 0.18421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1054-5_0_6_line_43 |  | 36 | 37 | 0.025823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1054-5_0_6_line_44 |  | 37 | 74 | 0.029128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1054-5_0_6_line_45 |  | 39 | 42 | 0.02488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1054-5_0_6_line_46 |  | 40 | 41 | 0.055656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1054-5_0_6_line_47 |  | 40 | 42 | 0.10278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1054-5_0_6_line_48 |  | 41 | 80 | 0.11673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1054-5_0_6_line_49 |  | 44 | 55 | 0.012227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1054-5_0_6_line_50 |  | 45 | 46 | 0.034995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1054-5_0_6_line_51 |  | 46 | 47 | 0.0026199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1054-5_0_6_line_52 |  | 47 | 48 | 0.01786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1054-5_0_6_line_53 |  | 48 | 49 | 0.010098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1054-5_0_6_line_54 |  | 49 | 61 | 0.016868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1054-5_0_6_line_55 |  | 50 | 51 | 0.023368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1054-5_0_6_line_56 |  | 51 | 52 | 0.024334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1054-5_0_6_line_57 |  | 52 | 54 | 0.25565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1054-5_0_6_line_58 |  | 54 | 60 | 0.27126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1054-5_0_6_line_59 |  | 55 | 56 | 0.013859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1054-5_0_6_line_60 |  | 56 | 57 | 0.038581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1054-5_0_6_line_61 |  | 57 | 58 | 0.085913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1054-5_0_6_line_62 |  | 58 | 67 | 0.14127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1054-5_0_6_line_63 |  | 59 | 63 | 0.020439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1054-5_0_6_line_64 |  | 59 | 64 | 0.024105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1054-5_0_6_line_65 |  | 60 | 62 | 0.025404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1054-5_0_6_line_66 |  | 63 | 69 | 0.021707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1054-5_0_6_line_67 |  | 64 | 66 | 0.052683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1054-5_0_6_line_68 |  | 65 | 66 | 0.046447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1054-5_0_6_line_69 |  | 66 | 71 | 0.014681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1054-5_0_6_line_70 |  | 67 | 68 | 0.087857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1054-5_0_6_line_71 |  | 68 | 112 | 0.057766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1054-5_0_6_line_72 |  | 69 | 70 | 0.014808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1054-5_0_6_line_73 |  | 70 | 75 | 0.0080348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1054-5_0_6_line_74 |  | 71 | 76 | 0.025226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1054-5_0_6_line_75 |  | 72 | 73 | 0.017203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1054-5_0_6_line_76 |  | 72 | 74 | 0.0038021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1054-5_0_6_line_77 |  | 73 | 75 | 0.016967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1054-5_0_6_line_78 |  | 76 | 77 | 0.0095481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1054-5_0_6_line_79 |  | 77 | 78 | 0.033289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1054-5_0_6_line_80 |  | 78 | 79 | 0.012987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1054-5_0_6_line_81 |  | 80 | 81 | 0.0060573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1054-5_0_6_line_82 |  | 81 | 94 | 0.024294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1054-5_0_6_line_83 |  | 82 | 83 | 0.016827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1054-5_0_6_line_84 |  | 83 | 95 | 0.028036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1054-5_0_6_line_85 |  | 83 | 94 | 0.004846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1054-5_0_6_line_86 |  | 84 | 85 | 0.024895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1054-5_0_6_line_87 |  | 84 | 86 | 0.00059367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1054-5_0_6_line_88 |  | 85 | 87 | 0.0002479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1054-5_0_6_line_89 |  | 86 | 88 | 0.024615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1054-5_0_6_line_90 |  | 87 | 89 | 0.031531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1054-5_0_6_line_91 |  | 88 | 90 | 0.001494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1054-5_0_6_line_92 |  | 89 | 91 | 0.00023377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1054-5_0_6_line_93 |  | 90 | 92 | 0.022052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1054-5_0_6_line_94 |  | 91 | 93 | 0.022457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1054-5_0_6_line_95 |  | 92 | 108 | 0.005184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1054-5_0_6_line_96 |  | 93 | 97 | 0.032256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1054-5_0_6_line_97 |  | 95 | 99 | 0.009176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1054-5_0_6_line_98 |  | 95 | 100 | 0.016504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1054-5_0_6_line_99 |  | 95 | 96 | 0.03641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1054-5_0_6_line_100 |  | 96 | 97 | 0.018004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1054-5_0_6_line_101 |  | 96 | 98 | 0.0042632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1054-5_0_6_line_102 |  | 98 | 106 | 0.027892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-5_0_6_line_103 |  | 99 | 105 | 0.033973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1054-5_0_6_line_104 |  | 100 | 101 | 0.14922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_1054-5_0_6_line_105 |  | 101 | 102 | 0.067458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1054-5_0_6_line_106 |  | 101 | 103 | 0.039666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1054-5_0_6_line_107 |  | 102 | 107 | 0.060648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1054-5_0_6_line_108 |  | 103 | 104 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1054-5_0_6_line_109 |  | 107 | 111 | 0.059392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1054-5_0_6_line_110 |  | 108 | 109 | 0.023509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1054-5_0_6_line_111 |  | 109 | 110 | 0.0011942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1054-5_0_6_line_112 |  | 112 | 113 | 0.017326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-5_0_6_trafo_13 | 0.63 MVA 20/0.4 kV | 114 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2667404.8147 | 1213990.3562 | 2667407.3185 | 1213991.3024
1 | 2667404.8147 | 1213990.3562 | 2667378.4732 | 1213980.4024
2 | 2667419.197 | 1213995.791 | 2667407.3185 | 1213991.3024
3 | 2667337.0261 | 1213963.5537 | 2667358.9922 | 1213973.041 | 2667378.4732 | 1213980.4024
4 | 2667431.1108 | 1214000.8399 | 2667419.197 | 1213995.791
5 | 2667337.0261 | 1213963.5537 | 2667324.3441 | 1213955.2276 | 2667323.7359 | 1213954.772
6 | 2667337.0261 | 1213963.5537 | 2667337.0363 | 1213969.3797 | 2667339.4837 | 1213971.253 | 2667352.67 | 1213977.9727 | 2667356.6869 | 1213982.7877 | 2667357.789 | 1213987.4253 | 2667356.4969 | 1213992.2026 | 2667350.3666 | 1214000.9944 | 2667348.7242 | 1214005.8567
7 | 2667431.1108 | 1214000.8399 | 2667432.4224 | 1213997.6972 | 2667430.144 | 1213996.3261 | 2667428.219 | 1213994.6033 | 2667426.6026 | 1213991.1162 | 2667426.1676 | 1213987.9315 | 2667427.2325 | 1213983.8932
8 | 2667431.1108 | 1214000.8399 | 2667433.3314 | 1214001.7813
9 | 2667320.3967 | 1213952.2708 | 2667323.7359 | 1213954.772
10 | 2667286.9369 | 1213969.8591 | 2667312.5031 | 1213986.7692 | 2667339.5556 | 1214002.54 | 2667348.7242 | 1214005.8567
11 | 2667348.7242 | 1214005.8567 | 2667352.0763 | 1214013.0323 | 2667358.2983 | 1214020.3294 | 2667386.5445 | 1214044.1014
12 | 2667427.2325 | 1213983.8932 | 2667427.5882 | 1213982.5442 | 2667433.6 | 1213964.7677 | 2667434.0904 | 1213963.4046
13 | 2667433.926 | 1214002.0334 | 2667433.3314 | 1214001.7813
14 | 2667336.3879 | 1213847.9077 | 2667350.484 | 1213830.6005 | 2667342.0328 | 1213823.6263
15 | 2667336.3879 | 1213847.9077 | 2667360.0283 | 1213866.9257
16 | 2667336.3879 | 1213847.9077 | 2667278.428 | 1213801.0706
17 | 2667326.853 | 1213811.0994 | 2667342.0328 | 1213823.6263
18 | 2667388.2658 | 1213886.3954 | 2667362.8244 | 1213869.175 | 2667360.0283 | 1213866.9257
19 | 2667264.6681 | 1213789.9513 | 2667278.428 | 1213801.0706
20 | 2667432.6714 | 1213957.5527 | 2667435.968 | 1213947.4837 | 2667439.9381 | 1213947.0283 | 2667443.4313 | 1213945.0888 | 2667457.6792 | 1213954.6448 | 2667466.9143 | 1213958.1181
21 | 2667432.6714 | 1213957.5527 | 2667434.7535 | 1213958.1544 | 2667435.8586 | 1213958.4894 | 2667434.0904 | 1213963.4046
22 | 2667416.3369 | 1213930.34 | 2667421.0432 | 1213935.3074 | 2667423.4763 | 1213939.1262 | 2667425.1471 | 1213943.848 | 2667425.057 | 1213947.1157 | 2667424.1587 | 1213949.974 | 2667422.5759 | 1213952.2464 | 2667423.0663 | 1213952.541 | 2667426.5597 | 1213954.6151 | 2667428.5818 | 1213955.8165 | 2667430.3548 | 1213956.8706 | 2667432.6714 | 1213957.5527
23 | 2667466.9143 | 1213958.1181 | 2667477.5061 | 1213967.6631
24 | 2667416.3369 | 1213930.34 | 2667409.0218 | 1213924.3202 | 2667404.0472 | 1213921.5734 | 2667399.4738 | 1213917.7687
25 | 2667416.3369 | 1213930.34 | 2667416.9303 | 1213929.5796 | 2667418.7957 | 1213927.1769 | 2667420.1293 | 1213925.4465 | 2667422.0019 | 1213923.0773 | 2667423.5282 | 1213921.1044 | 2667424.8154 | 1213919.4513 | 2667425.9639 | 1213917.9744
26 | 2667264.6681 | 1213789.9513 | 2667290.3987 | 1213756.5518
27 | 2667264.6681 | 1213789.9513 | 2667252.4464 | 1213779.9689
28 | 2667311.8547 | 1213728.701 | 2667290.3987 | 1213756.5518
29 | 2667501.8035 | 1213989.5592 | 2667477.5061 | 1213967.6631
30 | 2667482.7421 | 1213904.5971 | 2667508.9603 | 1213933.6459
31 | 2667482.7421 | 1213904.5971 | 2667475.0923 | 1213901.9867 | 2667468.9859 | 1213899.9163 | 2667464.5897 | 1213894.3854 | 2667454.4457 | 1213886.6436 | 2667438.2498 | 1213876.7098 | 2667427.5023 | 1213870.6067
32 | 2667527.4621 | 1213952.5766 | 2667517.415 | 1213943.0134 | 2667508.9603 | 1213933.6459
33 | 2667365.3539 | 1213788.5089 | 2667369.513 | 1213789.4898 | 2667372.77 | 1213804.4248 | 2667378.0971 | 1213819.0051 | 2667388.1824 | 1213835.9852 | 2667397.7919 | 1213848.0235 | 2667408.2029 | 1213857.6916 | 2667427.5023 | 1213870.6067
34 | 2667427.5023 | 1213870.6067 | 2667407.3957 | 1213894.8168 | 2667392.4839 | 1213883.6425
35 | 2667365.3539 | 1213788.5089 | 2667362.816 | 1213787.9132 | 2667336.9957 | 1213769.2326
36 | 2667388.2658 | 1213886.3954 | 2667391.5332 | 1213882.9301 | 2667392.4839 | 1213883.6425
37 | 2667425.9639 | 1213917.9744 | 2667423.6654 | 1213916.3586 | 2667419.6274 | 1213912.5821
38 | 2667388.2658 | 1213886.3954 | 2667409.1289 | 1213902.7636 | 2667419.6274 | 1213912.5821
39 | 2667304.708 | 1213940.5191 | 2667320.3967 | 1213952.2708
40 | 2667286.9369 | 1213969.8591 | 2667289.9529 | 1213975.8746 | 2667313.9161 | 1213995.5017 | 2667323.9927 | 1214007.1894 | 2667324.1221 | 1214010.0767
41 | 2667386.5445 | 1214044.1014 | 2667409.2252 | 1214063.1895
42 | 2667311.8547 | 1213728.701 | 2667322.0461 | 1213715.4744 | 2667327.6557 | 1213710.4346 | 2667335.7593 | 1213702.4877 | 2667336.443 | 1213701.8173 | 2667338.1814 | 1213699.2242 | 2667341.7088 | 1213692.2485 | 2667341.8952 | 1213690.5384 | 2667342.3618 | 1213690.2547 | 2667344.0752 | 1213689.2067 | 2667344.8425 | 1213687.8478 | 2667346.2453 | 1213685.3843 | 2667338.4193 | 1213672.1099 | 2667347.1573 | 1213661.8022 | 2667345.7795 | 1213660.7193 | 2667352.871 | 1213652.9389 | 2667351.036 | 1213651.3061 | 2667366.1477 | 1213635.5892 | 2667369.069 | 1213640.5808 | 2667371.2057 | 1213644.4184 | 2667377.9286 | 1213648.4191 | 2667398.9095 | 1213657.8064 | 2667407.9019 | 1213660.6209 | 2667420.071 | 1213661.2811
43 | 2667244.0949 | 1213810.7477 | 2667264.7137 | 1213826.2935
44 | 2667264.7137 | 1213826.2935 | 2667266.5892 | 1213827.7076 | 2667269.613 | 1213831.0215 | 2667273.1694 | 1213837.6213 | 2667278.2608 | 1213848.8747 | 2667279.5873 | 1213850.9283
45 | 2667420.071 | 1213661.2811 | 2667428.8631 | 1213655.6102 | 2667434.6247 | 1213648.571 | 2667436.2393 | 1213643.5002
46 | 2667399.8671 | 1213552.9519 | 2667402.8969 | 1213546.3264 | 2667403.2319 | 1213545.5853 | 2667403.5804 | 1213543.6547 | 2667406.0412 | 1213538.3125 | 2667412.9196 | 1213526.5607 | 2667416.3944 | 1213522.9199 | 2667419.4627 | 1213520.9534 | 2667422.9737 | 1213520.1481 | 2667427.0014 | 1213520.0047 | 2667431.1266 | 1213521.9859 | 2667431.7062 | 1213521.1141 | 2667434.0167 | 1213517.6492
47 | 2667399.8671 | 1213552.9519 | 2667405.3227 | 1213555.504 | 2667415.9394 | 1213574.5692 | 2667423.1341 | 1213595.2968 | 2667439.0187 | 1213622.749 | 2667439.5314 | 1213633.1613 | 2667436.2393 | 1213643.5002
48 | 2667434.0167 | 1213517.6492 | 2667440.6861 | 1213522.3608 | 2667456.643 | 1213532.0251 | 2667480.7173 | 1213545.3056 | 2667537.2567 | 1213571.7462
49 | 2667527.4621 | 1213952.5766 | 2667536.3184 | 1213961.0063
50 | 2667463.4947 | 1214020.4254 | 2667456.4142 | 1214014.7458 | 2667441.9964 | 1214005.4547 | 2667433.926 | 1214002.0334
51 | 2667463.4947 | 1214020.4254 | 2667465.5383 | 1214022.0647
52 | 2667479.4701 | 1214033.2401 | 2667465.5383 | 1214022.0647
53 | 2667479.4701 | 1214033.2401 | 2667487.3473 | 1214039.5589
54 | 2667487.3473 | 1214039.5589 | 2667495.3004 | 1214045.9385 | 2667500.3677 | 1214050.2789
55 | 2667427.1038 | 1214078.2362 | 2667409.2252 | 1214063.1895
56 | 2667427.1038 | 1214078.2362 | 2667445.7219 | 1214093.9052
57 | 2667445.7219 | 1214093.9052 | 2667301.9037 | 1214305.2706
58 | 2667301.9037 | 1214305.2706 | 2667297.6194 | 1214305.9894 | 2667232.852 | 1214269.8142 | 2667220.2061 | 1214266.414 | 2667197.7136 | 1214264.6261 | 2667161.4252 | 1214258.3579 | 2667125.3863 | 1214248.8129 | 2667110.4079 | 1214253.5584 | 2667088.4408 | 1214261.0938 | 2667078.8341 | 1214264.3433 | 2667067.1924 | 1214268.2148 | 2667061.2077 | 1214270.2043 | 2667054.9977 | 1214272.636 | 2667046.5392 | 1214274.4097
59 | 2667546.3567 | 1213970.5611 | 2667536.3184 | 1213961.0063
60 | 2667546.3567 | 1213970.5611 | 2667547.8196 | 1213971.9535 | 2667574.9179 | 1213996.4971
61 | 2667643.272 | 1214047.8938 | 2667641.4633 | 1214047.3062 | 2667622.6334 | 1214036.6194 | 2667588.6302 | 1214008.9167 | 2667574.9179 | 1213996.4971
62 | 2667643.272 | 1214047.8938 | 2667664.432 | 1214054.7158 | 2667684.3984 | 1214054.9425 | 2667710.0396 | 1214052.4208 | 2667709.04 | 1214038.7787 | 2667705.9982 | 1214024.3796 | 2667698.5011 | 1214008.3401 | 2667681.1321 | 1213987.3966
63 | 2667304.708 | 1213940.5191 | 2667306.9848 | 1213927.2365 | 2667307.7002 | 1213924.4206 | 2667309.9106 | 1213921.0181
64 | 2667304.708 | 1213940.5191 | 2667290.0432 | 1213928.8463 | 2667285.8473 | 1213925.5087
65 | 2667022.2397 | 1214269.1795 | 2667035.2752 | 1214274.4265 | 2667043.5244 | 1214275.0419 | 2667046.5392 | 1214274.4097
66 | 2667309.9106 | 1213921.0181 | 2667313.2427 | 1213915.8889 | 2667315.7965 | 1213910.3698 | 2667315.4968 | 1213906.6419 | 2667313.1333 | 1213901.3792
67 | 2667244.6177 | 1213892.7115 | 2667267.4434 | 1213910.8691 | 2667285.8473 | 1213925.5087
68 | 2667244.6177 | 1213892.7115 | 2667237.0237 | 1213886.4887 | 2667220.338 | 1213872.8032 | 2667208.6999 | 1213863.2633
69 | 2667244.6177 | 1213892.7115 | 2667253.4115 | 1213880.9561
70 | 2667681.1321 | 1213987.3966 | 2667644.9976 | 1213955.4 | 2667614.1915 | 1213930.5297
71 | 2667614.1915 | 1213930.5297 | 2667602.4934 | 1213921.0856 | 2667585.0695 | 1213904.9336 | 2667575.2266 | 1213898.1178 | 2667568.6538 | 1213895.7076
72 | 2667306.3169 | 1213888.2742 | 2667309.5247 | 1213893.344 | 2667313.1333 | 1213901.3792
73 | 2667306.3169 | 1213888.2742 | 2667304.6217 | 1213885.5949 | 2667301.5129 | 1213881.8537
74 | 2667248.8416 | 1213860.6055 | 2667255.8615 | 1213866.9556 | 2667257.7267 | 1213871.9686 | 2667257.6899 | 1213875.2369 | 2667253.4115 | 1213880.9561
75 | 2667281.6503 | 1213854.122 | 2667290.9845 | 1213868.5723
76 | 2667281.6503 | 1213854.122 | 2667279.5873 | 1213850.9283
77 | 2667301.5129 | 1213881.8537 | 2667292.7586 | 1213871.3189 | 2667290.9845 | 1213868.5723
78 | 2667248.8416 | 1213860.6055 | 2667241.7608 | 1213854.2002
79 | 2667241.7608 | 1213854.2002 | 2667217.0735 | 1213831.8686
80 | 2667217.0735 | 1213831.8686 | 2667207.442 | 1213823.1561
81 | 2667542.7436 | 1213574.3122 | 2667537.2567 | 1213571.7462
82 | 2667564.7503 | 1213584.6036 | 2667542.7436 | 1213574.3122
83 | 2667566.8055 | 1213580.213 | 2667551.5408 | 1213573.1333
84 | 2667566.8055 | 1213580.213 | 2667591.1491 | 1213591.14 | 2667592.381 | 1213591.6988
85 | 2667566.8055 | 1213580.213 | 2667564.7503 | 1213584.6036
86 | 2667689.8395 | 1213680.0945 | 2667667.7611 | 1213668.5924
87 | 2667690.3661 | 1213680.3688 | 2667689.8395 | 1213680.0945
88 | 2667667.7611 | 1213668.5924 | 2667667.5413 | 1213668.4779
89 | 2667712.1963 | 1213691.7416 | 2667690.3661 | 1213680.3688
90 | 2667639.5772 | 1213653.9096 | 2667667.5413 | 1213668.4779
91 | 2667712.1963 | 1213691.7416 | 2667713.5212 | 1213692.4318
92 | 2667639.5772 | 1213653.9096 | 2667639.3699 | 1213653.8016
93 | 2667713.5212 | 1213692.4318 | 2667733.0782 | 1213702.6203
94 | 2667639.3699 | 1213653.8016 | 2667624.6476 | 1213646.1318 | 2667619.4421 | 1213643.4487
95 | 2667737.6757 | 1213705.0154 | 2667733.0782 | 1213702.6203
96 | 2667619.4421 | 1213643.4487 | 2667591.9171 | 1213629.2614 | 2667590.8029 | 1213628.6111
97 | 2667592.381 | 1213591.6988 | 2667592.7802 | 1213590.6582 | 2667594.889 | 1213582.8773
98 | 2667592.381 | 1213591.6988 | 2667607.4351 | 1213598.4628
99 | 2667578.1532 | 1213616.4975 | 2667577.8952 | 1213613.1147 | 2667578.1 | 1213609.7927 | 2667578.8301 | 1213605.6984 | 2667581.9766 | 1213596.8397 | 2667587.3966 | 1213599.1803 | 2667587.6924 | 1213598.5499 | 2667589.2183 | 1213595.2763 | 2667590.7753 | 1213591.9474 | 2667591.1491 | 1213591.14 | 2667592.381 | 1213591.6988
100 | 2667578.1532 | 1213616.4975 | 2667580.3736 | 1213620.981 | 2667584.8462 | 1213625.1343 | 2667590.8029 | 1213628.6111
101 | 2667578.1532 | 1213616.4975 | 2667577.6841 | 1213620.7349
102 | 2667580.6225 | 1213648.1484 | 2667576.6721 | 1213629.878 | 2667577.6841 | 1213620.7349
103 | 2667621.8005 | 1213573.0095 | 2667609.6647 | 1213568.0577 | 2667594.889 | 1213582.8773
104 | 2667743.1673 | 1213660.4633 | 2667724.6001 | 1213651.9694 | 2667688.6591 | 1213635.5512 | 2667647.2526 | 1213616.7809 | 2667608.2975 | 1213598.8503 | 2667607.4351 | 1213598.4628
105 | 2667770.6897 | 1213598.8597 | 2667768.1947 | 1213603.8345 | 2667755.3961 | 1213633.1518 | 2667743.1673 | 1213660.4633
106 | 2667743.1673 | 1213660.4633 | 2667741.4994 | 1213664.1911 | 2667773.8579 | 1213678.9902
107 | 2667770.6897 | 1213598.8597 | 2667715.3412 | 1213574.0658
108 | 2667769.0207 | 1213697.5579 | 2667769.0499 | 1213694.99 | 2667773.0429 | 1213685.863 | 2667772.2236 | 1213682.4293 | 2667773.8579 | 1213678.9902
109 | 2667661.1393 | 1213549.7855 | 2667715.3412 | 1213574.0658
110 | 2667737.6757 | 1213705.0154 | 2667758.5255 | 1213715.8774
111 | 2667759.5845 | 1213716.4292 | 2667758.5255 | 1213715.8774
112 | 2667551.5888 | 1213893.3805 | 2667565.3399 | 1213894.4925 | 2667568.6538 | 1213895.7076

## bus_geodata
| x | y | coords
0 | 2667404.8147 | 1213990.3562
1 | 2667407.3185 | 1213991.3024
2 | 2667378.4732 | 1213980.4024
3 | 2667419.197 | 1213995.791
4 | 2667337.0261 | 1213963.5537
5 | 2667431.1108 | 1214000.8399
6 | 2667323.7359 | 1213954.772
7 | 2667348.7242 | 1214005.8567
8 | 2667427.2325 | 1213983.8932
9 | 2667433.3314 | 1214001.7813
10 | 2667336.3879 | 1213847.9077
11 | 2667342.0328 | 1213823.6263
12 | 2667360.0283 | 1213866.9257
13 | 2667278.428 | 1213801.0706
14 | 2667432.6714 | 1213957.5527
15 | 2667466.9143 | 1213958.1181
16 | 2667434.0904 | 1213963.4046
17 | 2667416.3369 | 1213930.34
18 | 2667264.6681 | 1213789.9513
19 | 2667290.3987 | 1213756.5518
20 | 2667252.4464 | 1213779.9689
21 | 2667477.5061 | 1213967.6631
22 | 2667482.7421 | 1213904.5971
23 | 2667508.9603 | 1213933.6459
24 | 2667427.5023 | 1213870.6067
25 | 2667365.3539 | 1213788.5089
26 | 2667392.4839 | 1213883.6425
27 | 2667425.9639 | 1213917.9744
28 | 2667419.6274 | 1213912.5821
29 | 2667399.4738 | 1213917.7687
30 | 2667320.3968 | 1213952.2708
31 | 2667286.9369 | 1213969.8591
32 | 2667386.5445 | 1214044.1014
33 | 2667311.8547 | 1213728.701
34 | 2667326.853 | 1213811.0994
35 | 2667388.2658 | 1213886.3954
36 | 2667244.0949 | 1213810.7477
37 | 2667264.7137 | 1213826.2935
38 | 2667501.8035 | 1213989.5592
39 | 2667420.071 | 1213661.2811
40 | 2667399.8671 | 1213552.9519
41 | 2667434.0167 | 1213517.6492
42 | 2667436.2393 | 1213643.5002
43 | 2667336.9957 | 1213769.2326
44 | 2667527.4621 | 1213952.5766
45 | 2667433.926 | 1214002.0334
46 | 2667463.4947 | 1214020.4254
47 | 2667465.5383 | 1214022.0647
48 | 2667479.4701 | 1214033.2401
49 | 2667487.3473 | 1214039.5589
50 | 2667409.2252 | 1214063.1895
51 | 2667427.1038 | 1214078.2362
52 | 2667445.7219 | 1214093.9052
53 | 2667324.1221 | 1214010.0767
54 | 2667301.9037 | 1214305.2706
55 | 2667536.3184 | 1213961.0063
56 | 2667546.3567 | 1213970.5611
57 | 2667574.9179 | 1213996.4971
58 | 2667643.272 | 1214047.8938
59 | 2667304.708 | 1213940.5191
60 | 2667046.5392 | 1214274.4097
61 | 2667500.3677 | 1214050.2789
62 | 2667022.2397 | 1214269.1795
63 | 2667309.9106 | 1213921.0181
64 | 2667285.8473 | 1213925.5087
65 | 2667208.6999 | 1213863.2633
66 | 2667244.6177 | 1213892.7115
67 | 2667681.1321 | 1213987.3966
68 | 2667614.1915 | 1213930.5297
69 | 2667313.1333 | 1213901.3792
70 | 2667306.3169 | 1213888.2742
71 | 2667253.4115 | 1213880.9561
72 | 2667281.6503 | 1213854.122
73 | 2667290.9845 | 1213868.5723
74 | 2667279.5873 | 1213850.9283
75 | 2667301.5129 | 1213881.8537
76 | 2667248.8416 | 1213860.6055
77 | 2667241.7608 | 1213854.2002
78 | 2667217.0735 | 1213831.8686
79 | 2667207.442 | 1213823.1561
80 | 2667537.2567 | 1213571.7462
81 | 2667542.7436 | 1213574.3122
82 | 2667551.5408 | 1213573.1333
83 | 2667566.8055 | 1213580.213
84 | 2667689.8395 | 1213680.0945
85 | 2667667.7611 | 1213668.5924
86 | 2667690.3661 | 1213680.3688
87 | 2667667.5413 | 1213668.4779
88 | 2667712.1963 | 1213691.7416
89 | 2667639.5772 | 1213653.9096
90 | 2667713.5212 | 1213692.4318
91 | 2667639.3699 | 1213653.8016
92 | 2667733.0782 | 1213702.6203
93 | 2667619.4421 | 1213643.4487
94 | 2667564.7503 | 1213584.6036
95 | 2667592.381 | 1213591.6988
96 | 2667578.1532 | 1213616.4975
97 | 2667590.8029 | 1213628.6111
98 | 2667577.6841 | 1213620.7349
99 | 2667594.889 | 1213582.8773
100 | 2667607.4351 | 1213598.4628
101 | 2667743.1673 | 1213660.4633
102 | 2667770.6897 | 1213598.8597
103 | 2667773.8579 | 1213678.9902
104 | 2667769.0207 | 1213697.5579
105 | 2667621.8005 | 1213573.0095
106 | 2667580.6225 | 1213648.1484
107 | 2667715.3412 | 1213574.0658
108 | 2667737.6757 | 1213705.0154
109 | 2667758.5255 | 1213715.8774
110 | 2667759.5846 | 1213716.4292
111 | 2667661.1393 | 1213549.7855
112 | 2667568.6538 | 1213895.7076
113 | 2667551.5888 | 1213893.3805
114 | 2667468.9859 | 1213899.9163

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98457 | -0.29478 | 0.0059508 | 0.0014914
1 | 0.98481 | -0.29006 | 0.0026552 | 0.00066547
2 | 0.98215 | -0.34157 | 0.00097895 | 0.00024535
3 | 0.986 | -0.26709 | 0 | 0
4 | 0.97834 | -0.41561 | 0 | 0
5 | 0.98721 | -0.2438 | 0 | 0
6 | 0.97712 | -0.4395 | 0.00053305 | 0.00013359
7 | 0.97788 | -0.42466 | 0 | 0
8 | 0.98962 | -0.19754 | 0.0051039 | 0.0012792
9 | 0.98715 | -0.24507 | 0.0020896 | 0.0005237
10 | 0.99224 | -0.14778 | 0 | 0
11 | 0.99017 | -0.18791 | 0.022394 | 0.0056126
12 | 0.99344 | -0.12472 | 0.025965 | 0.0065075
13 | 0.99045 | -0.1821 | 0.008722 | 0.0021859
14 | 0.99126 | -0.16622 | 0 | 0
15 | 0.99097 | -0.17186 | 0 | 0
16 | 0.99098 | -0.17151 | 0.0041211 | 0.0010328
17 | 0.99251 | -0.14227 | 0 | 0
18 | 0.99006 | -0.18958 | 0 | 0
19 | 0.98919 | -0.2063 | 0.0069216 | 0.0017347
20 | 0.98997 | -0.19127 | 0.006024 | 0.0015098
21 | 0.99088 | -0.17362 | 0.00461 | 0.0011554
22 | 0.99545 | -0.086642 | 0 | 0
23 | 0.99274 | -0.13861 | 0.0058688 | 0.0014709
24 | 1 | 0 | -0.48813 | -0.12455
25 | 0.9984 | -0.030684 | 0 | 0
26 | 0.99551 | -0.085113 | 0.018076 | 0.0045302
27 | 0.99308 | -0.13154 | 0 | 0
28 | 0.99338 | -0.12584 | 0.017271 | 0.0043285
29 | 0.99235 | -0.14536 | 0.0082615 | 0.0020705
30 | 0.9768 | -0.44573 | 0.0021873 | 0.0005482
31 | 0.97781 | -0.42611 | 0 | 0
32 | 0.97749 | -0.43244 | 0.00091275 | 0.00022876
33 | 0.98852 | -0.21918 | 0 | 0
34 | 0.98935 | -0.20388 | 0.04559 | 0.011426
35 | 0.99501 | -0.094799 | 0 | 0
36 | 0.97191 | -0.54212 | 0.0043896 | 0.0011001
37 | 0.97201 | -0.54003 | 0.0031625 | 0.00079259
38 | 0.99081 | -0.17499 | 0.002358 | 0.00059097
39 | 0.98501 | -0.28694 | 0 | 0
40 | 0.98273 | -0.33111 | 0 | 0
41 | 0.98175 | -0.35011 | 0 | 0
42 | 0.98453 | -0.29612 | 0.0065835 | 0.00165
43 | 0.99789 | -0.040529 | 0.016322 | 0.0040908
44 | 0.99105 | -0.17119 | 0.024494 | 0.0061388
45 | 0.98713 | -0.24539 | 0.0023483 | 0.00058855
46 | 0.98632 | -0.26117 | 0.0022864 | 0.00057303
47 | 0.98627 | -0.26225 | 0.0029997 | 0.00075179
48 | 0.98594 | -0.26862 | 0.0017492 | 0.00043838
49 | 0.98577 | -0.27191 | 0.0017714 | 0.00044395
50 | 0.9773 | -0.43618 | 0.001834 | 0.00045965
51 | 0.97719 | -0.43835 | 0.0017392 | 0.00043588
52 | 0.97711 | -0.43984 | 0.0025289 | 0.00063379
53 | 0.97775 | -0.42724 | 0.0011078 | 0.00027764
54 | 0.97692 | -0.44365 | 0 | 0
55 | 0.99054 | -0.18094 | 0.0049399 | 0.0012381
56 | 0.99003 | -0.19079 | 0.0058439 | 0.0014646
57 | 0.98881 | -0.21425 | 0.0058688 | 0.0014708
58 | 0.98656 | -0.25766 | 0 | 0
59 | 0.97535 | -0.47425 | 0 | 0
60 | 0.97672 | -0.44765 | 0.0003821 | 9.5763e-05
61 | 0.98552 | -0.27686 | 0.016381 | 0.0041054
62 | 0.97671 | -0.44784 | 0.00041992 | 0.00010524
63 | 0.97449 | -0.49111 | 0.00065042 | 0.00016301
64 | 0.97457 | -0.48951 | 0.00048845 | 0.00012242
65 | 0.97269 | -0.52651 | 0.0047154 | 0.0011818
66 | 0.9729 | -0.52248 | 0 | 0
67 | 0.98287 | -0.32945 | 0 | 0
68 | 0.98057 | -0.37437 | 0.0097785 | 0.0024507
69 | 0.97359 | -0.5088 | 0.00042875 | 0.00010745
70 | 0.97299 | -0.52076 | 0.021588 | 0.0054105
71 | 0.97249 | -0.53041 | 0.0029356 | 0.00073573
72 | 0.97226 | -0.53517 | 0.0050741 | 0.0012717
73 | 0.97252 | -0.52997 | 0.0024907 | 0.00062424
74 | 0.97222 | -0.53597 | 0.0037789 | 0.00094708
75 | 0.97282 | -0.52406 | 0.003428 | 0.00085914
76 | 0.97187 | -0.54268 | 0.0064928 | 0.0016273
77 | 0.9717 | -0.54619 | 0.0050156 | 0.001257
78 | 0.97123 | -0.55534 | 0.0065277 | 0.001636
79 | 0.97113 | -0.55734 | 0.0083503 | 0.0020928
80 | 0.97971 | -0.39007 | 0.0040554 | 0.0010164
81 | 0.9796 | -0.39203 | 0.0012632 | 0.00031659
82 | 0.97911 | -0.40176 | 0.0013959 | 0.00034985
83 | 0.97913 | -0.40133 | 0 | 0
84 | 0.97481 | -0.4861 | 0.0019412 | 0.0004865
85 | 0.9752 | -0.47845 | 0.001801 | 0.00045136
86 | 0.97481 | -0.48626 | 0.0016511 | 0.00041382
87 | 0.97521 | -0.47837 | 0.0016519 | 0.00041401
88 | 0.9745 | -0.4922 | 0.0021054 | 0.00052765
89 | 0.9758 | -0.4667 | 0.0019464 | 0.00048782
90 | 0.97449 | -0.49251 | 0.0024556 | 0.00061543
91 | 0.9758 | -0.4666 | 0.0014555 | 0.00036477
92 | 0.97431 | -0.49599 | 0.0025787 | 0.00064628
93 | 0.9763 | -0.4569 | 0.0011216 | 0.00028109
94 | 0.97921 | -0.39979 | 0 | 0
95 | 0.97868 | -0.41011 | 0 | 0
96 | 0.97749 | -0.43356 | 0 | 0
97 | 0.97704 | -0.44232 | 0.0019329 | 0.00048444
98 | 0.97745 | -0.43424 | 0.0075569 | 0.0018939
99 | 0.97867 | -0.41033 | 0 | 0
100 | 0.97856 | -0.41252 | 0.0042356 | 0.0010615
101 | 0.97727 | -0.4378 | 0 | 0
102 | 0.97675 | -0.448 | 0 | 0
103 | 0.97716 | -0.44 | 0 | 0
104 | 0.9771 | -0.44111 | 0.0030409 | 0.00076212
105 | 0.97863 | -0.41117 | 0.0013461 | 0.00033738
106 | 0.97742 | -0.43481 | 0.0011307 | 0.00028337
107 | 0.97535 | -0.47554 | 0.014358 | 0.0035985
108 | 0.97428 | -0.49656 | 0.0023274 | 0.00058331
109 | 0.9742 | -0.49815 | 0.0019292 | 0.0004835
110 | 0.9742 | -0.49819 | 0.0017624 | 0.0004417
111 | 0.97477 | -0.48694 | 0.010467 | 0.0026233
112 | 0.97958 | -0.39375 | 0.0063307 | 0.0015866
113 | 0.97939 | -0.39758 | 0.012157 | 0.0030468
114 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.099096 | -0.02521 | 0.099119 | 0.025224 | 2.2555e-05 | 1.4401e-05 | 0.1499 | 0.1499 | 0.1499 | 0.98457 | -0.29478 | 0.98481 | -0.29006 | 41.182
1 | 0.093145 | 0.023718 | -0.092936 | -0.023585 | 0.00020967 | 0.00013383 | 0.14091 | 0.14091 | 0.14091 | 0.98457 | -0.29478 | 0.98215 | -0.34157 | 38.7112
2 | -0.10177 | -0.02589 | 0.10189 | 0.025962 | 0.00011281 | 7.2034e-05 | 0.15391 | 0.15391 | 0.15391 | 0.98481 | -0.29006 | 0.986 | -0.26709 | 42.2841
3 | 0.091957 | 0.023339 | -0.09163 | -0.023131 | 0.00032624 | 0.00020823 | 0.13943 | 0.13943 | 0.13943 | 0.98215 | -0.34157 | 0.97834 | -0.41561 | 38.3038
4 | -0.10189 | -0.025962 | 0.102 | 0.026035 | 0.00011466 | 7.3218e-05 | 0.15391 | 0.15391 | 0.15391 | 0.986 | -0.26709 | 0.98721 | -0.2438 | 42.2841
5 | 0.082697 | 0.020899 | -0.082602 | -0.020839 | 9.4605e-05 | 6.0347e-05 | 0.12584 | 0.12584 | 0.12584 | 0.97834 | -0.41561 | 0.97712 | -0.4395 | 34.5716
6 | 0.0089338 | 0.0022317 | -0.0089299 | -0.00223 | 3.8407e-06 | 1.7615e-06 | 0.013585 | 0.013586 | 0.013586 | 0.97834 | -0.41561 | 0.97788 | -0.42466 | 3.7323
7 | -0.13166 | -0.033481 | 0.13196 | 0.033669 | 0.00029414 | 0.000188 | 0.19863 | 0.19863 | 0.19863 | 0.98721 | -0.2438 | 0.98962 | -0.19754 | 54.5674
8 | 0.02966 | 0.0074462 | -0.029659 | -0.0074451 | 1.8082e-06 | 1.1264e-06 | 0.044711 | 0.044711 | 0.044711 | 0.98721 | -0.2438 | 0.98715 | -0.24507 | 12.2834
9 | 0.082069 | 0.020705 | -0.082044 | -0.02069 | 2.4457e-05 | 1.56e-05 | 0.12503 | 0.12503 | 0.12503 | 0.97712 | -0.4395 | 0.9768 | -0.44573 | 34.3486
10 | 0.0011079 | 0.00027612 | -0.0011078 | -0.00027697 | 7.6238e-08 | -8.4891e-07 | 0.0016853 | 0.0016857 | 0.0016857 | 0.97788 | -0.42466 | 0.97781 | -0.42611 | 0.46309
11 | 0.007822 | 0.0019538 | -0.0078191 | -0.0019527 | 2.8905e-06 | 1.1674e-06 | 0.0119 | 0.0119 | 0.0119 | 0.97788 | -0.42466 | 0.97749 | -0.43244 | 3.2693
12 | -0.13706 | -0.034948 | 0.13723 | 0.035058 | 0.00017244 | 0.00010981 | 0.2063 | 0.2063 | 0.2063 | 0.98962 | -0.19754 | 0.99098 | -0.17151 | 28.3378
13 | 0.027569 | 0.0069214 | -0.027569 | -0.0069211 | 4.1833e-07 | 2.5947e-07 | 0.041562 | 0.041562 | 0.041562 | 0.98715 | -0.24507 | 0.98713 | -0.24539 | 11.418
14 | 0.068149 | 0.017143 | -0.068019 | -0.01706 | 0.0001304 | 8.303e-05 | 0.10222 | 0.10222 | 0.10222 | 0.99224 | -0.14778 | 0.99017 | -0.18791 | 28.0833
15 | -0.17315 | -0.043889 | 0.17334 | 0.044011 | 0.00019205 | 0.00012134 | 0.25984 | 0.25984 | 0.25984 | 0.99224 | -0.14778 | 0.99344 | -0.12472 | 17.8461
16 | 0.105 | 0.026746 | -0.10483 | -0.026639 | 0.00017356 | 0.00010724 | 0.15762 | 0.15762 | 0.15762 | 0.99224 | -0.14778 | 0.99045 | -0.1821 | 10.8255
17 | 0.045625 | 0.011448 | -0.04559 | -0.011426 | 3.4701e-05 | 2.1955e-05 | 0.068569 | 0.068569 | 0.068569 | 0.99017 | -0.18791 | 0.98935 | -0.20388 | 18.8376
18 | -0.19931 | -0.050518 | 0.19959 | 0.0507 | 0.00028705 | 0.00018193 | 0.29873 | 0.29873 | 0.29873 | 0.99344 | -0.12472 | 0.99501 | -0.094799 | 20.5173
19 | 0.096105 | 0.024453 | -0.09607 | -0.024431 | 3.4638e-05 | 2.1258e-05 | 0.14452 | 0.14452 | 0.14452 | 0.99045 | -0.1821 | 0.99006 | -0.18958 | 9.9255
20 | 0.0069706 | 0.0017468 | -0.0069687 | -0.0017462 | 1.8727e-06 | 6.1075e-07 | 0.010464 | 0.010464 | 0.010464 | 0.99126 | -0.16622 | 0.99097 | -0.17186 | 2.8747
21 | 0.14139 | 0.036114 | -0.14135 | -0.036091 | 3.6173e-05 | 2.271e-05 | 0.21249 | 0.21249 | 0.21249 | 0.99126 | -0.16622 | 0.99098 | -0.17151 | 14.5939
22 | -0.14836 | -0.03786 | 0.14853 | 0.037969 | 0.00017185 | 0.00010808 | 0.22295 | 0.22295 | 0.22295 | 0.99126 | -0.16622 | 0.99251 | -0.14227 | 15.3125
23 | 0.0069687 | 0.0017462 | -0.0069682 | -0.001746 | 5.8545e-07 | 1.9101e-07 | 0.010464 | 0.010464 | 0.010464 | 0.99097 | -0.17186 | 0.99088 | -0.17362 | 2.8747
24 | 0.0082627 | 0.002071 | -0.0082615 | -0.0020705 | 1.2146e-06 | 5.046e-07 | 0.012388 | 0.012388 | 0.012388 | 0.99251 | -0.14227 | 0.99235 | -0.14536 | 3.4033
25 | -0.15679 | -0.04004 | 0.15688 | 0.040091 | 8.1369e-05 | 5.1266e-05 | 0.23534 | 0.23534 | 0.23534 | 0.99251 | -0.14227 | 0.99308 | -0.13154 | 16.1633
26 | 0.090046 | 0.022922 | -0.089973 | -0.022877 | 7.253e-05 | 4.4252e-05 | 0.13546 | 0.13546 | 0.13546 | 0.99006 | -0.18958 | 0.98919 | -0.2063 | 9.3037
27 | 0.0060245 | 0.0015099 | -0.006024 | -0.0015098 | 4.8516e-07 | 1.0759e-07 | 0.0090546 | 0.0090547 | 0.0090547 | 0.99006 | -0.18958 | 0.98997 | -0.19127 | 2.4875
28 | 0.083051 | 0.021143 | -0.083 | -0.021111 | 5.1541e-05 | 3.1182e-05 | 0.12505 | 0.12505 | 0.12505 | 0.98919 | -0.2063 | 0.98852 | -0.21918 | 8.5886
29 | 0.0023582 | 0.00059065 | -0.002358 | -0.00059097 | 1.5381e-07 | -3.2284e-07 | 0.0035412 | 0.0035413 | 0.0035413 | 0.99088 | -0.17362 | 0.99081 | -0.17499 | 0.97289
30 | 0.075895 | 0.019254 | -0.075706 | -0.019133 | 0.00018914 | 0.00012054 | 0.11353 | 0.11353 | 0.11353 | 0.99545 | -0.086642 | 0.99274 | -0.13861 | 31.1903
31 | -0.075895 | -0.019254 | 0.076213 | 0.019456 | 0.00031764 | 0.00020243 | 0.11353 | 0.11353 | 0.11353 | 0.99545 | -0.086642 | 1 | 0 | 31.1902
32 | 0.069838 | 0.017662 | -0.069729 | -0.017593 | 0.00010897 | 6.9397e-05 | 0.10474 | 0.10474 | 0.10474 | 0.99274 | -0.13861 | 0.99105 | -0.17119 | 28.7736
33 | 0.016354 | 0.0041091 | -0.01633 | -0.0040952 | 2.3917e-05 | 1.3897e-05 | 0.024339 | 0.024339 | 0.024339 | 1 | 0 | 0.9984 | -0.030684 | 6.6866
34 | 0.39391 | 0.10099 | -0.3923 | -0.099954 | 0.0016183 | 0.0010331 | 0.58695 | 0.58696 | 0.58696 | 1 | 0 | 0.99551 | -0.085113 | 40.3129
35 | 0.01633 | 0.0040952 | -0.016322 | -0.0040908 | 7.6589e-06 | 4.4511e-06 | 0.024339 | 0.024339 | 0.024339 | 0.9984 | -0.030684 | 0.99789 | -0.040529 | 6.6866
36 | 0.37422 | 0.095424 | -0.37405 | -0.095312 | 0.00017491 | 0.00011163 | 0.55994 | 0.55994 | 0.55994 | 0.99551 | -0.085113 | 0.99501 | -0.094799 | 38.4572
37 | -0.15688 | -0.040091 | 0.15692 | 0.040118 | 4.3295e-05 | 2.7277e-05 | 0.23534 | 0.23534 | 0.23534 | 0.99308 | -0.13154 | 0.99338 | -0.12584 | 16.1633
38 | -0.17419 | -0.044447 | 0.17445 | 0.044612 | 0.00026157 | 0.00016528 | 0.26121 | 0.26121 | 0.26121 | 0.99338 | -0.12584 | 0.99501 | -0.094799 | 17.9401
39 | 0.079857 | 0.020142 | -0.079748 | -0.020072 | 0.00010887 | 6.9429e-05 | 0.1217 | 0.1217 | 0.1217 | 0.9768 | -0.44573 | 0.97535 | -0.47425 | 33.4332
40 | 0.0011078 | 0.00027697 | -0.0011078 | -0.00027764 | 5.9708e-08 | -6.6451e-07 | 0.0016857 | 0.0016859 | 0.0016859 | 0.97781 | -0.42611 | 0.97775 | -0.42724 | 0.46316
41 | 0.0069064 | 0.0017239 | -0.0069051 | -0.0017235 | 1.2282e-06 | 4.1451e-07 | 0.010511 | 0.010511 | 0.010511 | 0.97749 | -0.43244 | 0.9773 | -0.43618 | 2.8877
42 | 0.083 | 0.021111 | -0.08273 | -0.020948 | 0.00027007 | 0.00016343 | 0.12505 | 0.12505 | 0.12505 | 0.98852 | -0.21918 | 0.98501 | -0.28694 | 8.5889
43 | -0.0043896 | -0.0011001 | 0.00439 | 0.0011001 | 4.3736e-07 | -4.013e-08 | 0.0067206 | 0.0067205 | 0.0067206 | 0.97191 | -0.54212 | 0.97201 | -0.54003 | 1.8463
44 | -0.0075525 | -0.0018927 | 0.007554 | 0.0018933 | 1.4601e-06 | 5.7336e-07 | 0.011562 | 0.011562 | 0.011562 | 0.97201 | -0.54003 | 0.97222 | -0.53597 | 3.1763
45 | 0.08273 | 0.020948 | -0.082693 | -0.020926 | 3.6477e-05 | 2.2079e-05 | 0.12505 | 0.12505 | 0.12505 | 0.98501 | -0.28694 | 0.98453 | -0.29612 | 8.5889
46 | 0.075982 | 0.0192 | -0.075913 | -0.019158 | 6.9133e-05 | 4.1427e-05 | 0.11511 | 0.11511 | 0.11511 | 0.98273 | -0.33111 | 0.98175 | -0.35011 | 7.9057
47 | -0.075982 | -0.0192 | 0.07611 | 0.019276 | 0.00012766 | 7.6485e-05 | 0.11511 | 0.1151 | 0.11511 | 0.98273 | -0.33111 | 0.98453 | -0.29612 | 7.9056
48 | 0.075913 | 0.019158 | -0.075768 | -0.019071 | 0.000145 | 8.6909e-05 | 0.11511 | 0.11511 | 0.11511 | 0.98175 | -0.35011 | 0.97971 | -0.39007 | 7.9058
49 | 0.045235 | 0.011454 | -0.045213 | -0.011441 | 2.1176e-05 | 1.3395e-05 | 0.067959 | 0.067959 | 0.067959 | 0.99105 | -0.17119 | 0.99054 | -0.18094 | 18.6702
50 | 0.02522 | 0.0063326 | -0.025201 | -0.0063209 | 1.8971e-05 | 1.1695e-05 | 0.038022 | 0.038022 | 0.038022 | 0.98713 | -0.24539 | 0.98632 | -0.26117 | 10.4456
51 | 0.022915 | 0.0057478 | -0.022914 | -0.0057471 | 1.1743e-06 | 7.181e-07 | 0.034572 | 0.034572 | 0.034572 | 0.98632 | -0.26117 | 0.98627 | -0.26225 | 9.4979
52 | 0.019914 | 0.0049953 | -0.019908 | -0.0049917 | 6.0466e-06 | 3.642e-06 | 0.030047 | 0.030047 | 0.030047 | 0.98627 | -0.26225 | 0.98594 | -0.26862 | 8.2546
53 | 0.018159 | 0.0045533 | -0.018156 | -0.0045516 | 2.8445e-06 | 1.6917e-06 | 0.027407 | 0.027407 | 0.027407 | 0.98594 | -0.26862 | 0.98577 | -0.27191 | 7.5294
54 | 0.016385 | 0.0041077 | -0.016381 | -0.0041054 | 3.8694e-06 | 2.2614e-06 | 0.024733 | 0.024733 | 0.024733 | 0.98577 | -0.27191 | 0.98552 | -0.27686 | 6.7948
55 | 0.0050711 | 0.0012638 | -0.0050706 | -0.0012638 | 5.2208e-07 | 4.1358e-08 | 0.0077187 | 0.0077188 | 0.0077188 | 0.9773 | -0.43618 | 0.97719 | -0.43835 | 2.1205
56 | 0.0033314 | 0.00082792 | -0.0033312 | -0.00082807 | 2.3461e-07 | -1.5467e-07 | 0.0050704 | 0.0050705 | 0.0050705 | 0.97719 | -0.43835 | 0.97711 | -0.43984 | 1.393
57 | 0.00080232 | 0.00019428 | -0.00080218 | -0.00019739 | 1.4269e-07 | -3.1103e-06 | 0.0012194 | 0.0012206 | 0.0012206 | 0.97711 | -0.43984 | 0.97692 | -0.44365 | 0.33532
58 | 0.00080218 | 0.00019739 | -0.00080203 | -0.00020069 | 1.5169e-07 | -3.2986e-06 | 0.0012206 | 0.0012218 | 0.0012218 | 0.97692 | -0.44365 | 0.97672 | -0.44765 | 0.33565
59 | 0.040273 | 0.010203 | -0.040254 | -0.010191 | 1.9047e-05 | 1.2011e-05 | 0.060539 | 0.060539 | 0.060539 | 0.99054 | -0.18094 | 0.99003 | -0.19079 | 16.6315
60 | 0.034411 | 0.008726 | -0.034372 | -0.0087017 | 3.8754e-05 | 2.4307e-05 | 0.051755 | 0.051755 | 0.051755 | 0.99003 | -0.19079 | 0.98881 | -0.21425 | 14.2185
61 | 0.028503 | 0.0072308 | -0.028444 | -0.007194 | 5.936e-05 | 3.6891e-05 | 0.042924 | 0.042924 | 0.042924 | 0.98881 | -0.21425 | 0.98656 | -0.25766 | 11.7924
62 | 0.028444 | 0.007194 | -0.028346 | -0.0071333 | 9.7613e-05 | 6.0675e-05 | 0.042924 | 0.042925 | 0.042925 | 0.98656 | -0.25766 | 0.98287 | -0.32945 | 11.7926
63 | 0.045105 | 0.011347 | -0.045069 | -0.011324 | 3.6311e-05 | 2.2984e-05 | 0.068829 | 0.068829 | 0.068829 | 0.97535 | -0.47425 | 0.97449 | -0.49111 | 18.9092
64 | 0.034643 | 0.0087252 | -0.034618 | -0.0087093 | 2.5265e-05 | 1.5869e-05 | 0.052868 | 0.052868 | 0.052868 | 0.97535 | -0.47425 | 0.97457 | -0.48951 | 14.5241
65 | 0.00041993 | 0.00010493 | -0.00041992 | -0.00010524 | 3.8984e-09 | -3.1545e-07 | 0.00063964 | 0.00063975 | 0.00063975 | 0.97672 | -0.44765 | 0.97671 | -0.44784 | 0.17576
66 | 0.044419 | 0.011161 | -0.044381 | -0.011137 | 3.7459e-05 | 2.3703e-05 | 0.067836 | 0.067836 | 0.067836 | 0.97449 | -0.49111 | 0.97359 | -0.5088 | 18.6364
67 | 0.034129 | 0.0085869 | -0.034076 | -0.0085532 | 5.3672e-05 | 3.3695e-05 | 0.052122 | 0.052122 | 0.052122 | 0.97457 | -0.48951 | 0.9729 | -0.52248 | 14.3193
68 | -0.0047154 | -0.0011818 | 0.0047163 | 0.0011818 | 9.0632e-07 | 3.4e-09 | 0.0072136 | 0.0072134 | 0.0072136 | 0.97269 | -0.52651 | 0.9729 | -0.52248 | 1.9818
69 | 0.029359 | 0.0073714 | -0.029348 | -0.0073645 | 1.1103e-05 | 6.9237e-06 | 0.044909 | 0.044909 | 0.044909 | 0.9729 | -0.52248 | 0.97249 | -0.53041 | 12.3376
70 | 0.028346 | 0.0071333 | -0.028285 | -0.0070955 | 6.0706e-05 | 3.7741e-05 | 0.042925 | 0.042925 | 0.042925 | 0.98287 | -0.32945 | 0.98057 | -0.37437 | 11.7927
71 | 0.018507 | 0.0046448 | -0.01849 | -0.0046346 | 1.7089e-05 | 1.0209e-05 | 0.028087 | 0.028087 | 0.028087 | 0.98057 | -0.37437 | 0.97958 | -0.39375 | 7.7162
72 | 0.043952 | 0.01103 | -0.043927 | -0.011014 | 2.5062e-05 | 1.5856e-05 | 0.067181 | 0.067181 | 0.067181 | 0.97359 | -0.5088 | 0.97299 | -0.52076 | 18.4563
73 | 0.022339 | 0.0056034 | -0.022336 | -0.0056012 | 3.5171e-06 | 2.1512e-06 | 0.034165 | 0.034166 | 0.034166 | 0.97299 | -0.52076 | 0.97282 | -0.52406 | 9.3861
74 | 0.026412 | 0.0066287 | -0.026397 | -0.0066192 | 1.5453e-05 | 9.5769e-06 | 0.040417 | 0.040417 | 0.040417 | 0.97249 | -0.53041 | 0.97187 | -0.54268 | 11.1036
75 | -0.016407 | -0.0041123 | 0.016411 | 0.0041147 | 4.0679e-06 | 2.39e-06 | 0.025111 | 0.025111 | 0.025111 | 0.97226 | -0.53517 | 0.97252 | -0.52997 | 6.8987
76 | 0.011333 | 0.0028406 | -0.011333 | -0.0028403 | 4.2897e-07 | 2.2739e-07 | 0.017345 | 0.017345 | 0.017345 | 0.97226 | -0.53517 | 0.97222 | -0.53597 | 4.7652
77 | -0.018902 | -0.0047389 | 0.018908 | 0.0047421 | 5.3223e-06 | 3.1957e-06 | 0.028922 | 0.028922 | 0.028922 | 0.97252 | -0.52997 | 0.97282 | -0.52406 | 7.9456
78 | 0.019904 | 0.0049919 | -0.019901 | -0.0049899 | 3.3256e-06 | 2.0101e-06 | 0.030476 | 0.030476 | 0.030476 | 0.97187 | -0.54268 | 0.9717 | -0.54619 | 8.3726
79 | 0.014885 | 0.0037329 | -0.014879 | -0.0037291 | 6.4869e-06 | 3.7394e-06 | 0.022796 | 0.022796 | 0.022796 | 0.9717 | -0.54619 | 0.97123 | -0.55534 | 6.2625
80 | 0.0083511 | 0.0020931 | -0.0083503 | -0.0020928 | 7.9728e-07 | 3.4955e-07 | 0.012795 | 0.012795 | 0.012795 | 0.97123 | -0.55534 | 0.97113 | -0.55734 | 3.515
81 | 0.071713 | 0.018055 | -0.071706 | -0.018051 | 6.7406e-06 | 4.0089e-06 | 0.10895 | 0.10895 | 0.10895 | 0.97971 | -0.39007 | 0.9796 | -0.39203 | 7.4828
82 | 0.070443 | 0.017734 | -0.070417 | -0.017719 | 2.6091e-05 | 1.5475e-05 | 0.10703 | 0.10703 | 0.10703 | 0.9796 | -0.39203 | 0.97921 | -0.39979 | 7.3511
83 | -0.0013959 | -0.00034985 | 0.0013959 | 0.00034966 | 2.8398e-08 | -1.9345e-07 | 0.0021215 | 0.0021214 | 0.0021215 | 0.97911 | -0.40176 | 0.97913 | -0.40133 | 0.58282
84 | 0.069016 | 0.017366 | -0.068987 | -0.017349 | 2.8929e-05 | 1.7104e-05 | 0.10491 | 0.10491 | 0.10491 | 0.97913 | -0.40133 | 0.97868 | -0.41011 | 7.2054
85 | -0.070411 | -0.017716 | 0.070417 | 0.017719 | 5.2045e-06 | 3.087e-06 | 0.10703 | 0.10703 | 0.10703 | 0.97913 | -0.40133 | 0.97921 | -0.39979 | 7.3511
86 | -0.016757 | -0.004201 | 0.016763 | 0.0042046 | 6.1082e-06 | 3.5988e-06 | 0.025579 | 0.025579 | 0.025579 | 0.97481 | -0.4861 | 0.9752 | -0.47845 | 7.0272
87 | 0.014816 | 0.0037145 | -0.014816 | -0.0037144 | 1.1387e-07 | 6.5476e-08 | 0.022616 | 0.022616 | 0.022616 | 0.97481 | -0.4861 | 0.97481 | -0.48626 | 6.2132
88 | -0.018564 | -0.0046559 | 0.018564 | 0.004656 | 7.4597e-08 | 4.4648e-08 | 0.028327 | 0.028327 | 0.028327 | 0.9752 | -0.47845 | 0.97521 | -0.47837 | 7.7822
89 | 0.013164 | 0.0033006 | -0.013161 | -0.0032985 | 3.7277e-06 | 2.0789e-06 | 0.020096 | 0.020096 | 0.020096 | 0.97481 | -0.48626 | 0.9745 | -0.4922 | 5.5208
90 | -0.020216 | -0.00507 | 0.020227 | 0.0050768 | 1.1252e-05 | 6.8074e-06 | 0.030848 | 0.030847 | 0.030848 | 0.97521 | -0.47837 | 0.9758 | -0.4667 | 8.4746
91 | 0.011055 | 0.0027709 | -0.011055 | -0.0027708 | 1.5965e-07 | 8.3562e-08 | 0.016881 | 0.016881 | 0.016881 | 0.9745 | -0.4922 | 0.97449 | -0.49251 | 4.6376
92 | -0.022174 | -0.0055646 | 0.022174 | 0.0055647 | 1.0024e-07 | 6.1235e-08 | 0.033816 | 0.033816 | 0.033816 | 0.9758 | -0.4667 | 0.9758 | -0.4666 | 9.29
93 | 0.0085996 | 0.0021553 | -0.0085982 | -0.0021547 | 1.4259e-06 | 6.3791e-07 | 0.013131 | 0.013131 | 0.013131 | 0.97449 | -0.49251 | 0.97431 | -0.49599 | 3.6075
94 | -0.023629 | -0.0059294 | 0.02364 | 0.0059362 | 1.0935e-05 | 6.7179e-06 | 0.036035 | 0.036035 | 0.036035 | 0.9758 | -0.4666 | 0.9763 | -0.4569 | 9.8997
95 | 0.0060195 | 0.0015084 | -0.0060193 | -0.0015084 | 1.643e-07 | 4.0591e-08 | 0.0091932 | 0.0091932 | 0.0091932 | 0.97431 | -0.49599 | 0.97428 | -0.49656 | 2.5256
96 | -0.024762 | -0.0062173 | 0.024779 | 0.0062279 | 1.7233e-05 | 1.0625e-05 | 0.037744 | 0.037744 | 0.037744 | 0.9763 | -0.4569 | 0.97704 | -0.44232 | 10.3693
97 | 0.0013462 | 0.00033688 | -0.0013462 | -0.00033698 | 1.4414e-08 | -1.0608e-07 | 0.0020466 | 0.0020467 | 0.0020467 | 0.97868 | -0.41011 | 0.97867 | -0.41033 | 0.56227
98 | 0.03219 | 0.0080907 | -0.032186 | -0.0080892 | 3.7075e-06 | 1.5433e-06 | 0.048951 | 0.048951 | 0.048951 | 0.97868 | -0.41011 | 0.97856 | -0.41252 | 3.362
99 | 0.035451 | 0.0089213 | -0.035411 | -0.0088964 | 3.9687e-05 | 2.4942e-05 | 0.053913 | 0.053913 | 0.053913 | 0.97868 | -0.41011 | 0.97749 | -0.43356 | 14.8114
100 | 0.026723 | 0.0067193 | -0.026712 | -0.0067123 | 1.1177e-05 | 6.9278e-06 | 0.040688 | 0.040688 | 0.040688 | 0.97749 | -0.43356 | 0.97704 | -0.44232 | 11.178
101 | 0.0086879 | 0.0021771 | -0.0086876 | -0.002177 | 2.7963e-07 | 1.2552e-07 | 0.013225 | 0.013225 | 0.013225 | 0.97749 | -0.43356 | 0.97745 | -0.43424 | 3.6333
102 | 0.0011307 | 0.00028304 | -0.0011307 | -0.00028337 | 3.0988e-08 | -3.2976e-07 | 0.0017212 | 0.0017213 | 0.0017213 | 0.97745 | -0.43424 | 0.97742 | -0.43481 | 0.47289
103 | 0.0013462 | 0.00033698 | -0.0013461 | -0.00033738 | 5.337e-08 | -3.9272e-07 | 0.0020467 | 0.0020468 | 0.0020468 | 0.97867 | -0.41033 | 0.97863 | -0.41117 | 0.56232
104 | 0.027951 | 0.0070276 | -0.027917 | -0.0070117 | 3.371e-05 | 1.5958e-05 | 0.04251 | 0.042512 | 0.042512 | 0.97856 | -0.41252 | 0.97727 | -0.4378 | 3.8931
105 | 0.024875 | 0.00625 | -0.024863 | -0.0062448 | 1.2101e-05 | 5.2101e-06 | 0.037882 | 0.037882 | 0.037882 | 0.97727 | -0.4378 | 0.97675 | -0.448 | 3.4691
106 | 0.0030414 | 0.00076168 | -0.0030411 | -0.00076198 | 3.1898e-07 | -2.928e-07 | 0.0046307 | 0.0046309 | 0.0046309 | 0.97727 | -0.4378 | 0.97716 | -0.44 | 1.2722
107 | 0.024863 | 0.0062448 | -0.024831 | -0.0062246 | 3.2638e-05 | 2.0131e-05 | 0.037882 | 0.037883 | 0.037883 | 0.97675 | -0.448 | 0.97535 | -0.47554 | 10.4073
108 | 0.0030411 | 0.00076198 | -0.0030409 | -0.00076212 | 1.5975e-07 | -1.4658e-07 | 0.0046309 | 0.004631 | 0.004631 | 0.97716 | -0.44 | 0.9771 | -0.44111 | 1.2722
109 | 0.010473 | 0.0026262 | -0.010467 | -0.0026233 | 5.6859e-06 | 2.8982e-06 | 0.015978 | 0.015978 | 0.015978 | 0.97535 | -0.47554 | 0.97477 | -0.48694 | 4.3896
110 | 0.0036919 | 0.00092508 | -0.0036916 | -0.00092519 | 2.8029e-07 | -1.1336e-07 | 0.0056385 | 0.0056386 | 0.0056386 | 0.97428 | -0.49656 | 0.9742 | -0.49815 | 1.5491
111 | 0.0017624 | 0.00044169 | -0.0017624 | -0.0004417 | 3.2451e-09 | -1.2792e-08 | 0.002692 | 0.002692 | 0.002692 | 0.9742 | -0.49815 | 0.9742 | -0.49819 | 0.73955
112 | 0.012159 | 0.003048 | -0.012157 | -0.0030468 | 2.2165e-06 | 1.2005e-06 | 0.01847 | 0.01847 | 0.01847 | 0.97958 | -0.39375 | 0.97939 | -0.39758 | 5.0743

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48813 | 0.12455

## res_load
| p_mw | q_mvar
0 | 0.0059508 | 0.0014914
1 | 0.0026552 | 0.00066547
2 | 0.00097895 | 0.00024535
3 | 0.00053305 | 0.00013359
4 | 0.0051039 | 0.0012792
5 | 0.0020896 | 0.0005237
6 | 0.022394 | 0.0056126
7 | 0.025965 | 0.0065075
8 | 0.008722 | 0.0021859
9 | 0.0041211 | 0.0010328
10 | 0.0069216 | 0.0017347
11 | 0.006024 | 0.0015098
12 | 0.00461 | 0.0011554
13 | 0.0058688 | 0.0014709
14 | 0.018076 | 0.0045302
15 | 0.017271 | 0.0043285
16 | 0.0082615 | 0.0020705
17 | 0.0021873 | 0.0005482
18 | 0.00091275 | 0.00022876
19 | 0.04559 | 0.011426
20 | 0.0043896 | 0.0011001
21 | 0.0031625 | 0.00079259
22 | 0.002358 | 0.00059097
23 | 0.0065835 | 0.00165
24 | 0.016322 | 0.0040908
25 | 0.024494 | 0.0061388
26 | 0.0023483 | 0.00058855
27 | 0.0022864 | 0.00057303
28 | 0.0029997 | 0.00075179
29 | 0.0017492 | 0.00043838
30 | 0.0017714 | 0.00044395
31 | 0.001834 | 0.00045965
32 | 0.0017392 | 0.00043588
33 | 0.0025289 | 0.00063379
34 | 0.0011078 | 0.00027764
35 | 0.0049399 | 0.0012381
36 | 0.0058439 | 0.0014646
37 | 0.0058688 | 0.0014708
38 | 0.0003821 | 9.5763e-05
39 | 0.016381 | 0.0041054
40 | 0.00041992 | 0.00010524
41 | 0.00065042 | 0.00016301
42 | 0.00048845 | 0.00012242
43 | 0.0047154 | 0.0011818
44 | 0.0097785 | 0.0024507
45 | 0.00042875 | 0.00010745
46 | 0.021588 | 0.0054105
47 | 0.0029356 | 0.00073573
48 | 0.0050741 | 0.0012717
49 | 0.0024907 | 0.00062424
50 | 0.0037789 | 0.00094708
51 | 0.003428 | 0.00085914
52 | 0.0064928 | 0.0016273
53 | 0.0050156 | 0.001257
54 | 0.0065277 | 0.001636
55 | 0.0083503 | 0.0020928
56 | 0.0040554 | 0.0010164
57 | 0.0012632 | 0.00031659
58 | 0.0013959 | 0.00034985
59 | 0.0019412 | 0.0004865
60 | 0.001801 | 0.00045136
61 | 0.0016511 | 0.00041382
62 | 0.0016519 | 0.00041401
63 | 0.0021054 | 0.00052765
64 | 0.0019464 | 0.00048782
65 | 0.0024556 | 0.00061543
66 | 0.0014555 | 0.00036477
67 | 0.0025787 | 0.00064628
68 | 0.0011216 | 0.00028109
69 | 0.0019329 | 0.00048444
70 | 0.0075569 | 0.0018939
71 | 0.0042356 | 0.0010615
72 | 0.0030409 | 0.00076212
73 | 0.0013461 | 0.00033738
74 | 0.0011307 | 0.00028337
75 | 0.014358 | 0.0035985
76 | 0.0023274 | 0.00058331
77 | 0.0019292 | 0.0004835
78 | 0.0017624 | 0.0004417
79 | 0.010467 | 0.0026233
80 | 0.0063307 | 0.0015866
81 | 0.012157 | 0.0030468

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1