## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-7_1_4_node_3 | 0.4 | n |  | TRUE
1 | bus_LV_1054-7_1_4_node_9 | 0.4 | n |  | TRUE
2 | bus_LV_1054-7_1_4_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_1054-7_1_4_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1054-7_1_4_node_62 | 0.4 | n |  | TRUE
5 | bus_LV_1054-7_1_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1054-7_1_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1054-7_1_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1054-7_1_4_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_1054-7_1_4_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_1054-7_1_4_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1054-7_1_4_node_35 | 0.4 | n |  | TRUE
12 | bus_LV_1054-7_1_4_node_41 | 0.4 | n |  | TRUE
13 | bus_LV_1054-7_1_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1054-7_1_4_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_1054-7_1_4_node_48 | 0.4 | n |  | TRUE
16 | bus_LV_1054-7_1_4_node_50 | 0.4 | n |  | TRUE
17 | bus_LV_1054-7_1_4_node_53 | 0.4 | n |  | TRUE
18 | bus_LV_1054-7_1_4_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_1054-7_1_4_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_1054-7_1_4_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_1054-7_1_4_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_1054-7_1_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1054-7_1_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1054-7_1_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1054-7_1_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1054-7_1_4_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_1054-7_1_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1054-7_1_4_node_60 | 0.4 | n |  | TRUE
29 | bus_LV_1054-7_1_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1054-7_1_4_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_1054-7_1_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1054-7_1_4_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_1054-7_1_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1054-7_1_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1054-7_1_4_node_40 | 0.4 | n |  | TRUE
36 | bus_MV_213_0_node_154 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-7_1_4_load_23 | 2 | 0.0048604 | 0.0012181 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-7_1_4_load_62 | 4 | 0.0069133 | 0.0017326 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-7_1_4_load_37 | 8 | 0.016346 | 0.0040966 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-7_1_4_load_27 | 9 | 0.0030121 | 0.00075491 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-7_1_4_load_35 | 11 | 0.0015931 | 0.00039926 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-7_1_4_load_41 | 12 | 0.0023028 | 0.00057713 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-7_1_4_load_13 | 13 | 0.0046596 | 0.0011678 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-7_1_4_load_24 | 14 | 0.01796 | 0.0045011 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-7_1_4_load_53 | 17 | 0.020211 | 0.0050652 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-7_1_4_load_43 | 18 | 0.036605 | 0.0091741 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-7_1_4_load_58 | 19 | 0.0048738 | 0.0012215 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-7_1_4_load_39 | 20 | 0.018293 | 0.0045846 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-7_1_4_load_38 | 21 | 0.032568 | 0.0081622 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-7_1_4_load_33 | 22 | 0.016717 | 0.0041897 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-7_1_4_load_11 | 23 | 0.0031905 | 0.00079963 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-7_1_4_load_12 | 24 | 0.0058053 | 0.001455 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-7_1_4_load_30 | 26 | 0.030763 | 0.00771 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-7_1_4_load_60 | 28 | 0.0023263 | 0.00058303 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-7_1_4_load_59 | 30 | 0.001633 | 0.00040927 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-7_1_4_load_25 | 31 | 0.015474 | 0.0038781 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-7_1_4_load_42 | 32 | 0.0018512 | 0.00046396 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-7_1_4_load_34 | 33 | 0.023193 | 0.0058128 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-7_1_4_load_36 | 34 | 0.025926 | 0.0064978 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-7_1_4_load_40 | 35 | 0.021312 | 0.0053414 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-7_1_4_line_0 |  | 0 | 1 | 0.055645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1054-7_1_4_line_1 |  | 0 | 2 | 0.015637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-7_1_4_line_2 |  | 1 | 9 | 0.01049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-7_1_4_line_3 |  | 1 | 3 | 0.018673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-7_1_4_line_4 |  | 1 | 5 | 0.097908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1054-7_1_4_line_5 |  | 2 | 14 | 0.002456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-7_1_4_line_6 |  | 3 | 4 | 0.003563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-7_1_4_line_7 |  | 5 | 6 | 0.031475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1054-7_1_4_line_8 |  | 5 | 7 | 0.26211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1054-7_1_4_line_9 |  | 5 | 8 | 0.057293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-7_1_4_line_10 |  | 6 | 10 | 0.045779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1054-7_1_4_line_11 |  | 6 | 11 | 0.041762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-7_1_4_line_12 |  | 7 | 13 | 0.0097927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-7_1_4_line_13 |  | 8 | 21 | 0.023296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-7_1_4_line_14 |  | 10 | 12 | 0.040417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1054-7_1_4_line_15 |  | 11 | 22 | 0.028345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-7_1_4_line_16 |  | 12 | 32 | 0.01908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1054-7_1_4_line_17 |  | 13 | 23 | 0.031238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-7_1_4_line_18 |  | 14 | 31 | 0.004965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-7_1_4_line_19 |  | 15 | 16 | 0.0090953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-7_1_4_line_20 |  | 15 | 17 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-7_1_4_line_21 |  | 15 | 18 | 0.018193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1054-7_1_4_line_22 |  | 16 | 19 | 0.027727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-7_1_4_line_23 |  | 18 | 32 | 0.094538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-7_1_4_line_24 |  | 20 | 21 | 0.064066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-7_1_4_line_25 |  | 22 | 33 | 0.024618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-7_1_4_line_26 |  | 23 | 24 | 0.026553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-7_1_4_line_27 |  | 24 | 25 | 0.028698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-7_1_4_line_28 |  | 25 | 26 | 0.039119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-7_1_4_line_29 |  | 25 | 27 | 0.0077411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-7_1_4_line_30 |  | 27 | 28 | 0.015688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-7_1_4_line_31 |  | 27 | 29 | 0.027148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-7_1_4_line_32 |  | 29 | 30 | 0.007229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-7_1_4_line_33 |  | 33 | 34 | 0.0051898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1054-7_1_4_line_34 |  | 34 | 35 | 0.017157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-7_1_4_trafo_3 | 0.63 MVA 20/0.4 kV | 36 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2666815.402 | 1213466.2117 | 2666857.1347 | 1213493.4629 | 2666854.2147 | 1213498.4777
1 | 2666815.402 | 1213466.2117 | 2666811.919 | 1213471.9762 | 2666811.756 | 1213476.3549 | 2666809.3864 | 1213480.2047
2 | 2666854.2147 | 1213498.4777 | 2666848.9232 | 1213507.5358
3 | 2666870.9931 | 1213506.7709 | 2666858.0062 | 1213500.4214 | 2666854.2147 | 1213498.4777
4 | 2666854.2147 | 1213498.4777 | 2666857.1347 | 1213493.4629 | 2666860.1165 | 1213488.3598 | 2666928.0992 | 1213532.7609 | 2666930.707 | 1213528.4986
5 | 2666808.0991 | 1213482.2962 | 2666809.3864 | 1213480.2047
6 | 2666870.9931 | 1213506.7709 | 2666869.1057 | 1213509.7961
7 | 2666930.707 | 1213528.4986 | 2666947.1432 | 1213501.633
8 | 2666788.2431 | 1213556.5526 | 2666813.7005 | 1213571.9361 | 2666831.6514 | 1213582.6884 | 2666899.7841 | 1213625.1452 | 2666915.309 | 1213600.2594 | 2666938.1566 | 1213565.9166 | 2666938.4036 | 1213561.5055 | 2666942.5703 | 1213555.0705 | 2666943.0597 | 1213555.454 | 2666946.1321 | 1213557.8455 | 2666946.9529 | 1213558.4884 | 2666949.0076 | 1213555.4541 | 2666941.0584 | 1213548.3271 | 2666938.3509 | 1213546.5845 | 2666938.9148 | 1213545.7459 | 2666940.5445 | 1213543.3515 | 2666933.4939 | 1213538.7251 | 2666928.0992 | 1213532.7609 | 2666930.707 | 1213528.4986
9 | 2666930.707 | 1213528.4986 | 2666902.1266 | 1213510.5001 | 2666882.518 | 1213497.5173
10 | 2666947.1432 | 1213501.633 | 2666950.9647 | 1213498.8741 | 2666955.8125 | 1213495.3819 | 2666975.5094 | 1213466.3405
11 | 2666947.1432 | 1213501.633 | 2666911.7028 | 1213479.5408
12 | 2666788.2431 | 1213556.5526 | 2666789.6352 | 1213554.3446 | 2666783.6179 | 1213550.4229
13 | 2666882.518 | 1213497.5173 | 2666863.0941 | 1213484.6567
14 | 2666975.5094 | 1213466.3405 | 2666955.2808 | 1213454.7952 | 2666940.9474 | 1213447.9411 | 2666939.8154 | 1213447.4395
15 | 2666887.649 | 1213464.5466 | 2666911.7028 | 1213479.5408
16 | 2666939.8154 | 1213447.4395 | 2666922.3715 | 1213439.7089
17 | 2666757.8735 | 1213532.7647 | 2666761.2308 | 1213535.526 | 2666775.0203 | 1213544.8195 | 2666783.6179 | 1213550.4229
18 | 2666805.4966 | 1213486.5245 | 2666808.0991 | 1213482.2962
19 | 2666821.9379 | 1213388.6811 | 2666822.3792 | 1213387.9411 | 2666824.6703 | 1213384.1422 | 2666826.1024 | 1213381.7568 | 2666826.6211 | 1213380.8843
20 | 2666821.9379 | 1213388.6811 | 2666812.1555 | 1213383.1953
21 | 2666821.9379 | 1213388.6811 | 2666837.8526 | 1213397.4955
22 | 2666826.6211 | 1213380.8843 | 2666813.6712 | 1213373.9238 | 2666802.3901 | 1213367.4134
23 | 2666922.3715 | 1213439.7089 | 2666895.723 | 1213427.8991 | 2666869.2058 | 1213414.8604 | 2666837.8526 | 1213397.4955
24 | 2666863.0941 | 1213484.6567 | 2666809.6753 | 1213449.2881
25 | 2666887.649 | 1213464.5466 | 2666866.7577 | 1213451.5238
26 | 2666757.8735 | 1213532.7647 | 2666749.692 | 1213526.0355 | 2666740.0787 | 1213516.8889 | 2666738.202 | 1213514.9612
27 | 2666718.6244 | 1213494.0235 | 2666719.4976 | 1213495.412 | 2666725.9074 | 1213502.3324 | 2666738.202 | 1213514.9612
28 | 2666718.6244 | 1213494.0235 | 2666739.8273 | 1213470.1348 | 2666734.5038 | 1213465.2499
29 | 2666718.6244 | 1213494.0235 | 2666717.0164 | 1213495.84 | 2666718.5464 | 1213497.5916 | 2666720.5805 | 1213499.7823
30 | 2666720.5805 | 1213499.7823 | 2666715.6738 | 1213503.8077 | 2666707.5467 | 1213508.4753
31 | 2666739.1593 | 1213519.6247 | 2666738.1906 | 1213518.6244 | 2666720.5805 | 1213499.7823
32 | 2666739.1593 | 1213519.6247 | 2666733.8401 | 1213524.5349
33 | 2666866.7577 | 1213451.5238 | 2666862.3535 | 1213448.7784
34 | 2666847.7939 | 1213439.7025 | 2666862.3535 | 1213448.7784

## bus_geodata
| x | y | coords
0 | 2666815.402 | 1213466.2117
1 | 2666854.2147 | 1213498.4777
2 | 2666809.3864 | 1213480.2047
3 | 2666870.9931 | 1213506.7709
4 | 2666869.1057 | 1213509.7961
5 | 2666930.707 | 1213528.4986
6 | 2666947.1432 | 1213501.633
7 | 2666788.2431 | 1213556.5526
8 | 2666882.518 | 1213497.5173
9 | 2666848.9232 | 1213507.5358
10 | 2666975.5094 | 1213466.3405
11 | 2666911.7028 | 1213479.5408
12 | 2666939.8154 | 1213447.4395
13 | 2666783.6179 | 1213550.4229
14 | 2666808.0991 | 1213482.2962
15 | 2666821.9379 | 1213388.6811
16 | 2666826.6211 | 1213380.8843
17 | 2666812.1555 | 1213383.1953
18 | 2666837.8526 | 1213397.4955
19 | 2666802.3901 | 1213367.4134
20 | 2666809.6753 | 1213449.2881
21 | 2666863.0941 | 1213484.6567
22 | 2666887.649 | 1213464.5466
23 | 2666757.8735 | 1213532.7647
24 | 2666738.202 | 1213514.9612
25 | 2666718.6244 | 1213494.0235
26 | 2666734.5038 | 1213465.2499
27 | 2666720.5805 | 1213499.7823
28 | 2666707.5467 | 1213508.4753
29 | 2666739.1593 | 1213519.6247
30 | 2666733.8401 | 1213524.5349
31 | 2666805.4966 | 1213486.5245
32 | 2666922.3715 | 1213439.7089
33 | 2666866.7577 | 1213451.5238
34 | 2666862.3535 | 1213448.7784
35 | 2666847.7939 | 1213439.7025
36 | 2666818.4591 | 1213461.165

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.32546 | -0.08324
1 | 0.99518 | -0.09101 | 0 | 0
2 | 0.99946 | -0.010443 | 0.0048604 | 0.0012181
3 | 0.99506 | -0.093282 | 0 | 0
4 | 0.99504 | -0.093716 | 0.0069133 | 0.0017326
5 | 0.987 | -0.2475 | 0 | 0
6 | 0.9855 | -0.27656 | 0 | 0
7 | 0.98112 | -0.36165 | 0 | 0
8 | 0.98345 | -0.31664 | 0.016346 | 0.0040966
9 | 0.99515 | -0.091566 | 0.0030121 | 0.00075491
10 | 0.98457 | -0.29461 | 0 | 0
11 | 0.98206 | -0.34331 | 0.0015931 | 0.00039926
12 | 0.98333 | -0.31857 | 0.0023028 | 0.00057713
13 | 0.98068 | -0.37023 | 0.0046596 | 0.0011678
14 | 0.99938 | -0.011876 | 0.01796 | 0.0045011
15 | 0.97636 | -0.45475 | 0 | 0
16 | 0.97632 | -0.45556 | 0 | 0
17 | 0.97615 | -0.45889 | 0.020211 | 0.0050652
18 | 0.97679 | -0.44641 | 0.036605 | 0.0091741
19 | 0.9762 | -0.45803 | 0.0048738 | 0.0012215
20 | 0.98127 | -0.35921 | 0.018293 | 0.0045846
21 | 0.98236 | -0.33802 | 0.032568 | 0.0081622
22 | 0.97977 | -0.38805 | 0.016717 | 0.0041897
23 | 0.97941 | -0.39502 | 0.0031905 | 0.00079963
24 | 0.97841 | -0.41459 | 0.0058053 | 0.001455
25 | 0.97749 | -0.43275 | 0 | 0
26 | 0.97637 | -0.45473 | 0.030763 | 0.00771
27 | 0.97746 | -0.43331 | 0 | 0
28 | 0.97742 | -0.43398 | 0.0023263 | 0.00058303
29 | 0.97742 | -0.43412 | 0 | 0
30 | 0.97741 | -0.43434 | 0.001633 | 0.00040927
31 | 0.99931 | -0.013216 | 0.015474 | 0.0038781
32 | 0.9822 | -0.34045 | 0.0018512 | 0.00046396
33 | 0.97816 | -0.41959 | 0.023193 | 0.0058128
34 | 0.97794 | -0.42405 | 0.025926 | 0.0064978
35 | 0.9776 | -0.43072 | 0.021312 | 0.0053414
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.28549 | 0.073629 | -0.28423 | -0.072825 | 0.0012597 | 0.00080401 | 0.42556 | 0.42556 | 0.42556 | 1 | 0 | 0.99518 | -0.09101 | 38.9706
1 | 0.038316 | 0.0096113 | -0.038297 | -0.0095993 | 1.9064e-05 | 1.1996e-05 | 0.057018 | 0.057018 | 0.057018 | 1 | 0 | 0.99946 | -0.010443 | 15.6643
2 | 0.0030122 | 0.00075482 | -0.0030121 | -0.00075491 | 7.9799e-08 | -8.5228e-08 | 0.0045038 | 0.0045039 | 0.0045039 | 0.99518 | -0.09101 | 0.99515 | -0.091566 | 1.2373
3 | 0.0069142 | 0.0017329 | -0.0069135 | -0.0017327 | 7.4843e-07 | 2.364e-07 | 0.010338 | 0.010338 | 0.010338 | 0.99518 | -0.09101 | 0.99506 | -0.093282 | 2.8402
4 | 0.27431 | 0.070337 | -0.27224 | -0.069019 | 0.0020645 | 0.0013175 | 0.41072 | 0.41072 | 0.41072 | 0.99518 | -0.09101 | 0.987 | -0.2475 | 37.6116
5 | 0.033437 | 0.0083812 | -0.033434 | -0.0083797 | 2.2824e-06 | 1.4286e-06 | 0.049782 | 0.049782 | 0.049782 | 0.99946 | -0.010443 | 0.99938 | -0.011876 | 13.6763
6 | 0.0069135 | 0.0017327 | -0.0069133 | -0.0017326 | 1.4281e-07 | 4.5115e-08 | 0.010338 | 0.010338 | 0.010338 | 0.99506 | -0.093282 | 0.99504 | -0.093716 | 2.8402
7 | 0.15593 | 0.039594 | -0.15571 | -0.039455 | 0.00021776 | 0.00013816 | 0.23526 | 0.23526 | 0.23526 | 0.987 | -0.2475 | 0.9855 | -0.27656 | 21.5441
8 | 0.048817 | 0.012397 | -0.048551 | -0.012233 | 0.00026663 | 0.00016398 | 0.073655 | 0.073658 | 0.073658 | 0.987 | -0.2475 | 0.98112 | -0.36165 | 10.1178
9 | 0.067499 | 0.017029 | -0.067276 | -0.016887 | 0.00022266 | 0.00014177 | 0.1018 | 0.1018 | 0.1018 | 0.987 | -0.2475 | 0.98345 | -0.31664 | 27.9677
10 | 0.066372 | 0.016835 | -0.066315 | -0.0168 | 5.7554e-05 | 3.5086e-05 | 0.10029 | 0.10029 | 0.10029 | 0.9855 | -0.27656 | 0.98457 | -0.29461 | 9.184
11 | 0.089337 | 0.02262 | -0.089052 | -0.022438 | 0.00028531 | 0.00018207 | 0.13497 | 0.13497 | 0.13497 | 0.9855 | -0.27656 | 0.98206 | -0.34331 | 37.0806
12 | 0.048551 | 0.012233 | -0.048531 | -0.01222 | 1.9924e-05 | 1.2628e-05 | 0.073658 | 0.073658 | 0.073658 | 0.98112 | -0.36165 | 0.98068 | -0.37023 | 20.2357
13 | 0.050931 | 0.012791 | -0.050879 | -0.012758 | 5.189e-05 | 3.2914e-05 | 0.07707 | 0.077071 | 0.077071 | 0.98345 | -0.31664 | 0.98236 | -0.33802 | 21.1732
14 | 0.066315 | 0.0168 | -0.066238 | -0.016752 | 7.6222e-05 | 4.7755e-05 | 0.10029 | 0.10029 | 0.10029 | 0.98457 | -0.29461 | 0.98333 | -0.31857 | 13.776
15 | 0.087458 | 0.022039 | -0.087272 | -0.02192 | 0.00018678 | 0.00011918 | 0.13256 | 0.13256 | 0.13256 | 0.98206 | -0.34331 | 0.97977 | -0.38805 | 36.4175
16 | 0.063936 | 0.016175 | -0.063869 | -0.016133 | 6.7051e-05 | 4.2671e-05 | 0.096805 | 0.096805 | 0.096805 | 0.98333 | -0.31857 | 0.9822 | -0.34045 | 26.5947
17 | 0.043871 | 0.011052 | -0.043819 | -0.011019 | 5.1941e-05 | 3.2848e-05 | 0.066588 | 0.066588 | 0.066588 | 0.98068 | -0.37023 | 0.97941 | -0.39502 | 18.2934
18 | 0.015475 | 0.0038786 | -0.015474 | -0.0038781 | 9.8843e-07 | 5.6754e-07 | 0.023041 | 0.023041 | 0.023041 | 0.99938 | -0.011876 | 0.99931 | -0.013216 | 6.3299
19 | 0.0048745 | 0.0012215 | -0.0048743 | -0.0012215 | 1.8823e-07 | 6.7248e-09 | 0.0074289 | 0.0074289 | 0.0074289 | 0.97636 | -0.45475 | 0.97632 | -0.45556 | 2.0409
20 | 0.020215 | 0.0050677 | -0.020211 | -0.0050652 | 3.9919e-06 | 2.4146e-06 | 0.030808 | 0.030808 | 0.030808 | 0.97636 | -0.45475 | 0.97615 | -0.45889 | 8.4638
21 | -0.025089 | -0.0062892 | 0.025099 | 0.0062953 | 9.9746e-06 | 6.1561e-06 | 0.038237 | 0.038237 | 0.038237 | 0.97636 | -0.45475 | 0.97679 | -0.44641 | 10.5047
22 | 0.0048743 | 0.0012215 | -0.0048738 | -0.0012215 | 5.7384e-07 | 2.0568e-08 | 0.0074289 | 0.0074291 | 0.0074291 | 0.97632 | -0.45556 | 0.9762 | -0.45803 | 2.0409
23 | -0.061704 | -0.015469 | 0.062017 | 0.015669 | 0.00031325 | 0.00019929 | 0.094001 | 0.094 | 0.094001 | 0.97679 | -0.44641 | 0.9822 | -0.34045 | 25.8243
24 | -0.018293 | -0.0045846 | 0.018311 | 0.0045956 | 1.8486e-05 | 1.1021e-05 | 0.027739 | 0.027739 | 0.027739 | 0.98127 | -0.35921 | 0.98236 | -0.33802 | 7.6207
25 | 0.070555 | 0.01773 | -0.070449 | -0.017662 | 0.00010603 | 6.7551e-05 | 0.10717 | 0.10717 | 0.10717 | 0.97977 | -0.38805 | 0.97816 | -0.41959 | 29.4426
26 | 0.040629 | 0.01022 | -0.040591 | -0.010196 | 3.7956e-05 | 2.3958e-05 | 0.06174 | 0.061741 | 0.061741 | 0.97941 | -0.39502 | 0.97841 | -0.41459 | 16.9617
27 | 0.034785 | 0.0087409 | -0.034755 | -0.0087219 | 3.0129e-05 | 1.8923e-05 | 0.052912 | 0.052912 | 0.052912 | 0.97841 | -0.41459 | 0.97749 | -0.43275 | 14.5362
28 | 0.030796 | 0.0077302 | -0.030763 | -0.00771 | 3.2246e-05 | 2.0148e-05 | 0.046884 | 0.046884 | 0.046884 | 0.97749 | -0.43275 | 0.97637 | -0.45473 | 12.8803
29 | 0.0039596 | 0.00099174 | -0.0039595 | -0.00099177 | 1.0546e-07 | -2.9538e-08 | 0.0060274 | 0.0060274 | 0.0060274 | 0.97749 | -0.43275 | 0.97746 | -0.43331 | 1.6559
30 | 0.0023264 | 0.00058289 | -0.0023263 | -0.00058303 | 7.3788e-08 | -1.4941e-07 | 0.0035415 | 0.0035416 | 0.0035416 | 0.97746 | -0.43331 | 0.97742 | -0.43398 | 0.97296
31 | 0.0016331 | 0.00040889 | -0.001633 | -0.00040919 | 6.2917e-08 | -3.0001e-07 | 0.0024859 | 0.0024861 | 0.0024861 | 0.97746 | -0.43331 | 0.97742 | -0.43412 | 0.68298
32 | 0.001633 | 0.00040919 | -0.001633 | -0.00040927 | 1.6755e-08 | -7.988e-08 | 0.0024861 | 0.0024861 | 0.0024861 | 0.97742 | -0.43412 | 0.97741 | -0.43434 | 0.68299
33 | 0.047255 | 0.01185 | -0.047245 | -0.011843 | 1.0058e-05 | 6.3719e-06 | 0.071889 | 0.071889 | 0.071889 | 0.97816 | -0.41959 | 0.97794 | -0.42405 | 19.7497
34 | 0.021319 | 0.0053455 | -0.021312 | -0.0053414 | 6.7705e-06 | 4.1179e-06 | 0.03244 | 0.03244 | 0.03244 | 0.97794 | -0.42405 | 0.9776 | -0.43072 | 8.912

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32546 | 0.08324

## res_load
| p_mw | q_mvar
0 | 0.0048604 | 0.0012181
1 | 0.0069133 | 0.0017326
2 | 0.016346 | 0.0040966
3 | 0.0030121 | 0.00075491
4 | 0.0015931 | 0.00039926
5 | 0.0023028 | 0.00057713
6 | 0.0046596 | 0.0011678
7 | 0.01796 | 0.0045011
8 | 0.020211 | 0.0050652
9 | 0.036605 | 0.0091741
10 | 0.0048738 | 0.0012215
11 | 0.018293 | 0.0045846
12 | 0.032568 | 0.0081622
13 | 0.016717 | 0.0041897
14 | 0.0031905 | 0.00079963
15 | 0.0058053 | 0.001455
16 | 0.030763 | 0.00771
17 | 0.0023263 | 0.00058303
18 | 0.001633 | 0.00040927
19 | 0.015474 | 0.0038781
20 | 0.0018512 | 0.00046396
21 | 0.023193 | 0.0058128
22 | 0.025926 | 0.0064978
23 | 0.021312 | 0.0053414

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1