## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1058-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1058-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1058-10_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1058-10_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1058-10_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1058-10_0_4_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1058-10_0_4_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_1058-10_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1058-10_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1058-10_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1058-10_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1058-10_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1058-10_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1058-10_0_4_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_1058-10_0_4_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1058-10_0_4_node_46 | 0.4 | n |  | TRUE
16 | bus_LV_1058-10_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1058-10_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1058-10_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1058-10_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1058-10_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1058-10_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1058-10_0_4_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_1058-10_0_4_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_1058-10_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1058-10_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1058-10_0_4_node_50 | 0.4 | n |  | TRUE
27 | bus_LV_1058-10_0_4_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_1058-10_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1058-10_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1058-10_0_4_node_62 | 0.4 | n |  | TRUE
31 | bus_LV_1058-10_0_4_node_101 | 0.4 | n |  | TRUE
32 | bus_LV_1058-10_0_4_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_1058-10_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1058-10_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1058-10_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1058-10_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1058-10_0_4_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_1058-10_0_4_node_128 | 0.4 | n |  | TRUE
39 | bus_LV_1058-10_0_4_node_63 | 0.4 | n |  | TRUE
40 | bus_LV_1058-10_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1058-10_0_4_node_108 | 0.4 | n |  | TRUE
42 | bus_LV_1058-10_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1058-10_0_4_node_48 | 0.4 | n |  | TRUE
44 | bus_LV_1058-10_0_4_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_1058-10_0_4_node_68 | 0.4 | n |  | TRUE
46 | bus_LV_1058-10_0_4_node_99 | 0.4 | n |  | TRUE
47 | bus_LV_1058-10_0_4_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_1058-10_0_4_node_61 | 0.4 | n |  | TRUE
49 | bus_LV_1058-10_0_4_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_1058-10_0_4_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_1058-10_0_4_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_1058-10_0_4_node_104 | 0.4 | n |  | TRUE
53 | bus_LV_1058-10_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_1058-10_0_4_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_1058-10_0_4_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_1058-10_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_1058-10_0_4_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_1058-10_0_4_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_1058-10_0_4_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_1058-10_0_4_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_1058-10_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1058-10_0_4_node_103 | 0.4 | n |  | TRUE
63 | bus_LV_1058-10_0_4_node_91 | 0.4 | n |  | TRUE
64 | bus_LV_1058-10_0_4_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_1058-10_0_4_node_80 | 0.4 | n |  | TRUE
66 | bus_LV_1058-10_0_4_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_1058-10_0_4_node_109 | 0.4 | n |  | TRUE
68 | bus_LV_1058-10_0_4_node_127 | 0.4 | n |  | TRUE
69 | bus_LV_1058-10_0_4_node_102 | 0.4 | n |  | TRUE
70 | bus_LV_1058-10_0_4_node_73 | 0.4 | n |  | TRUE
71 | bus_LV_1058-10_0_4_node_78 | 0.4 | n |  | TRUE
72 | bus_LV_1058-10_0_4_node_110 | 0.4 | n |  | TRUE
73 | bus_LV_1058-10_0_4_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1058-10_0_4_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_1058-10_0_4_node_111 | 0.4 | n |  | TRUE
76 | bus_LV_1058-10_0_4_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_1058-10_0_4_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_1058-10_0_4_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_1058-10_0_4_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_1058-10_0_4_node_95 | 0.4 | n |  | TRUE
81 | bus_LV_1058-10_0_4_node_94 | 0.4 | n |  | TRUE
82 | bus_LV_1058-10_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_1058-10_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_1058-10_0_4_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_1058-10_0_4_node_67 | 0.4 | n |  | TRUE
86 | bus_LV_1058-10_0_4_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_1058-10_0_4_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_1058-10_0_4_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_1058-10_0_4_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_1058-10_0_4_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_1058-10_0_4_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_1058-10_0_4_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_1058-10_0_4_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1058-10_0_4_node_123 | 0.4 | n |  | TRUE
95 | bus_LV_1058-10_0_4_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_1058-10_0_4_node_113 | 0.4 | n |  | TRUE
97 | bus_LV_1058-10_0_4_node_121 | 0.4 | n |  | TRUE
98 | bus_LV_1058-10_0_4_node_126 | 0.4 | n |  | TRUE
99 | bus_LV_1058-10_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_1058-10_0_4_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_1058-10_0_4_node_124 | 0.4 | n |  | TRUE
102 | bus_LV_1058-10_0_4_node_114 | 0.4 | n |  | TRUE
103 | bus_LV_1058-10_0_4_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_1058-10_0_4_node_119 | 0.4 | n |  | TRUE
105 | bus_LV_1058-10_0_4_node_118 | 0.4 | n |  | TRUE
106 | bus_LV_1058-10_0_4_node_117 | 0.4 | n |  | TRUE
107 | bus_LV_1058-10_0_4_node_120 | 0.4 | n |  | TRUE
108 | bus_LV_1058-10_0_4_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_1058-10_0_4_node_81 | 0.4 | n |  | TRUE
110 | bus_LV_1058-10_0_4_node_86 | 0.4 | n |  | TRUE
111 | bus_LV_1058-10_0_4_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_1058-10_0_4_node_88 | 0.4 | n |  | TRUE
113 | bus_LV_1058-10_0_4_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_1058-10_0_4_node_90 | 0.4 | n |  | TRUE
115 | bus_LV_1058-10_0_4_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_1058-10_0_4_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_1058-10_0_4_node_100 | 0.4 | n |  | TRUE
118 | bus_LV_1058-10_0_4_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_1058-10_0_4_node_107 | 0.4 | n |  | TRUE
120 | bus_LV_1058-10_0_4_node_122 | 0.4 | n |  | TRUE
121 | bus_LV_1058-10_0_4_node_125 | 0.4 | n |  | TRUE
122 | bus_MV_23_0_node_192 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1058-10_0_4_load_0 | 0 | 0.012632 | 0.0031659 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1058-10_0_4_load_1 | 1 | 0.0045985 | 0.0011525 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1058-10_0_4_load_30 | 5 | 0.0082104 | 0.0020577 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1058-10_0_4_load_29 | 6 | 0.0019318 | 0.00048414 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1058-10_0_4_load_6 | 8 | 0.031127 | 0.0078011 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1058-10_0_4_load_24 | 12 | 0.0021779 | 0.00054584 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1058-10_0_4_load_47 | 13 | 0.0098117 | 0.0024591 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1058-10_0_4_load_27 | 14 | 0.0073856 | 0.001851 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1058-10_0_4_load_10 | 17 | 0.0040369 | 0.0010117 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1058-10_0_4_load_11 | 18 | 0.0078885 | 0.001977 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1058-10_0_4_load_44 | 22 | 0.0049106 | 0.0012307 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1058-10_0_4_load_45 | 23 | 0.0047426 | 0.0011886 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1058-10_0_4_load_56 | 27 | 0.0044408 | 0.001113 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1058-10_0_4_load_62 | 30 | 0.012108 | 0.0030346 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1058-10_0_4_load_101 | 31 | 0.0036628 | 0.00091797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1058-10_0_4_load_98 | 32 | 0.0031669 | 0.00079371 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1058-10_0_4_load_28 | 34 | 0.0016225 | 0.00040663 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1058-10_0_4_load_53 | 37 | 0.0066487 | 0.0016663 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1058-10_0_4_load_128 | 38 | 0.0072407 | 0.0018147 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1058-10_0_4_load_63 | 39 | 0.017853 | 0.0044745 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1058-10_0_4_load_31 | 40 | 0.010147 | 0.0025432 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1058-10_0_4_load_108 | 41 | 0.0039284 | 0.00098454 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1058-10_0_4_load_43 | 42 | 0.0048626 | 0.0012187 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1058-10_0_4_load_48 | 43 | 0.0044787 | 0.0011225 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1058-10_0_4_load_57 | 44 | 0.0041562 | 0.0010416 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1058-10_0_4_load_68 | 45 | 0.0032969 | 0.00082628 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1058-10_0_4_load_99 | 46 | 0.0029858 | 0.00074831 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1058-10_0_4_load_54 | 47 | 0.0070579 | 0.0017689 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1058-10_0_4_load_25 | 49 | 0.025094 | 0.0062891 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1058-10_0_4_load_26 | 50 | 0.014926 | 0.0037409 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1058-10_0_4_load_52 | 51 | 0.016754 | 0.004199 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1058-10_0_4_load_104 | 52 | 0.015729 | 0.0039421 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1058-10_0_4_load_32 | 53 | 0.0031912 | 0.00079978 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1058-10_0_4_load_35 | 56 | 0.0031939 | 0.00080048 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1058-10_0_4_load_36 | 57 | 0.0055176 | 0.0013828 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1058-10_0_4_load_37 | 58 | 0.0028267 | 0.00070845 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1058-10_0_4_load_38 | 59 | 0.0038006 | 0.00095253 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1058-10_0_4_load_49 | 61 | 0.015107 | 0.0037861 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1058-10_0_4_load_103 | 62 | 0.0032475 | 0.00081391 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1058-10_0_4_load_91 | 63 | 0.0020207 | 0.00050643 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1058-10_0_4_load_109 | 67 | 0.012771 | 0.0032006 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1058-10_0_4_load_127 | 68 | 0.012809 | 0.0032103 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1058-10_0_4_load_102 | 69 | 0.0070542 | 0.0017679 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1058-10_0_4_load_78 | 71 | 0.0033891 | 0.00084939 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1058-10_0_4_load_110 | 72 | 0.013058 | 0.0032727 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1058-10_0_4_load_59 | 74 | 0.015168 | 0.0038015 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1058-10_0_4_load_111 | 75 | 0.015907 | 0.0039867 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1058-10_0_4_load_60 | 76 | 0.014765 | 0.0037005 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1058-10_0_4_load_55 | 78 | 0.0069554 | 0.0017432 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1058-10_0_4_load_58 | 79 | 0.0039377 | 0.00098689 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1058-10_0_4_load_95 | 80 | 0.0020109 | 0.00050399 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1058-10_0_4_load_94 | 81 | 0.0011259 | 0.00028217 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1058-10_0_4_load_64 | 82 | 0.0028199 | 0.00070675 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1058-10_0_4_load_65 | 83 | 0.0018042 | 0.00045218 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1058-10_0_4_load_66 | 84 | 0.0033544 | 0.00084069 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1058-10_0_4_load_67 | 85 | 0.0018021 | 0.00045164 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1058-10_0_4_load_82 | 86 | 0.0028148 | 0.00070545 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1058-10_0_4_load_69 | 87 | 0.00096953 | 0.00024299 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1058-10_0_4_load_70 | 88 | 0.0032277 | 0.00080893 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1058-10_0_4_load_85 | 92 | 0.0027798 | 0.00069668 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1058-10_0_4_load_123 | 94 | 0.0020592 | 0.00051608 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1058-10_0_4_load_113 | 96 | 0.0031521 | 0.00078999 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1058-10_0_4_load_121 | 97 | 0.0034101 | 0.00085466 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1058-10_0_4_load_126 | 98 | 0.0032128 | 0.00080521 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1058-10_0_4_load_83 | 99 | 0.0049869 | 0.0012498 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1058-10_0_4_load_84 | 100 | 0.0028041 | 0.00070278 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1058-10_0_4_load_124 | 101 | 0.0025036 | 0.00062745 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1058-10_0_4_load_114 | 102 | 0.0010869 | 0.00027241 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1058-10_0_4_load_119 | 104 | 0.0028117 | 0.00070468 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1058-10_0_4_load_117 | 106 | 0.0027001 | 0.00067672 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1058-10_0_4_load_120 | 107 | 0.0012368 | 0.00030997 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1058-10_0_4_load_79 | 108 | 0.01222 | 0.0030625 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1058-10_0_4_load_81 | 109 | 0.0068566 | 0.0017184 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1058-10_0_4_load_86 | 110 | 0.0067954 | 0.0017031 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1058-10_0_4_load_87 | 111 | 0.0030016 | 0.00075228 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1058-10_0_4_load_88 | 112 | 0.0030016 | 0.00075228 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1058-10_0_4_load_89 | 113 | 0.0032476 | 0.00081391 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1058-10_0_4_load_90 | 114 | 0.0063525 | 0.0015921 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1058-10_0_4_load_92 | 115 | 0.0053567 | 0.0013425 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1058-10_0_4_load_93 | 116 | 0.0018297 | 0.00045856 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1058-10_0_4_load_100 | 117 | 0.0061268 | 0.0015355 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1058-10_0_4_load_106 | 118 | 0.002943 | 0.00073759 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1058-10_0_4_load_107 | 119 | 0.0030099 | 0.00075436 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1058-10_0_4_load_122 | 120 | 0.0012369 | 0.00030999 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1058-10_0_4_load_125 | 121 | 0.0021537 | 0.00053977 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1058-10_0_4_line_0 |  | 0 | 1 | 0.025599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1058-10_0_4_line_1 |  | 0 | 2 | 0.019038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1058-10_0_4_line_2 |  | 2 | 3 | 0.055348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1058-10_0_4_line_3 |  | 3 | 6 | 0.04626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1058-10_0_4_line_4 |  | 3 | 4 | 0.003159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1058-10_0_4_line_5 |  | 4 | 5 | 0.0062104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1058-10_0_4_line_6 |  | 6 | 7 | 0.029227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1058-10_0_4_line_7 |  | 7 | 33 | 0.11036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1058-10_0_4_line_8 |  | 7 | 34 | 0.050299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1058-10_0_4_line_9 |  | 8 | 9 | 0.22096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1058-10_0_4_line_10 |  | 9 | 10 | 0.1714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1058-10_0_4_line_11 |  | 10 | 11 | 0.004614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1058-10_0_4_line_12 |  | 10 | 12 | 0.038342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1058-10_0_4_line_13 |  | 11 | 13 | 0.032079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1058-10_0_4_line_14 |  | 13 | 16 | 0.01982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1058-10_0_4_line_15 |  | 14 | 15 | 0.01586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1058-10_0_4_line_16 |  | 15 | 41 | 0.0091994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1058-10_0_4_line_17 |  | 15 | 16 | 0.004627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1058-10_0_4_line_18 |  | 16 | 18 | 0.0087157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1058-10_0_4_line_19 |  | 17 | 18 | 0.024567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1058-10_0_4_line_20 |  | 17 | 19 | 0.045638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1058-10_0_4_line_21 |  | 19 | 20 | 0.006941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1058-10_0_4_line_22 |  | 19 | 21 | 0.020181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1058-10_0_4_line_23 |  | 20 | 22 | 0.014368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1058-10_0_4_line_24 |  | 20 | 23 | 0.022323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1058-10_0_4_line_25 |  | 21 | 35 | 0.005481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1058-10_0_4_line_26 |  | 22 | 42 | 0.030803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1058-10_0_4_line_27 |  | 24 | 25 | 0.034962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_1058-10_0_4_line_28 |  | 24 | 26 | 0.038879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1058-10_0_4_line_29 |  | 24 | 27 | 0.048579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1058-10_0_4_line_30 |  | 25 | 31 | 0.037799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1058-10_0_4_line_31 |  | 25 | 32 | 0.050008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1058-10_0_4_line_32 |  | 25 | 28 | 0.023418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1058-10_0_4_line_33 |  | 26 | 43 | 0.035085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1058-10_0_4_line_34 |  | 27 | 44 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1058-10_0_4_line_35 |  | 28 | 29 | 0.012305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1058-10_0_4_line_36 |  | 28 | 30 | 0.023955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1058-10_0_4_line_37 |  | 29 | 36 | 0.031684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1058-10_0_4_line_38 |  | 29 | 37 | 0.029399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1058-10_0_4_line_39 |  | 30 | 35 | 0.060524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1058-10_0_4_line_40 |  | 31 | 45 | 0.031242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1058-10_0_4_line_41 |  | 32 | 46 | 0.027255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1058-10_0_4_line_42 |  | 33 | 38 | 0.009388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1058-10_0_4_line_43 |  | 33 | 36 | 0.034716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1058-10_0_4_line_44 |  | 35 | 39 | 0.02412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1058-10_0_4_line_45 |  | 36 | 40 | 0.018458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1058-10_0_4_line_46 |  | 37 | 47 | 0.03246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1058-10_0_4_line_47 |  | 39 | 48 | 0.019384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1058-10_0_4_line_48 |  | 43 | 61 | 0.012042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1058-10_0_4_line_49 |  | 44 | 79 | 0.02764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1058-10_0_4_line_50 |  | 45 | 84 | 0.034468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1058-10_0_4_line_51 |  | 46 | 117 | 0.028109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1058-10_0_4_line_52 |  | 47 | 78 | 0.031808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1058-10_0_4_line_53 |  | 48 | 75 | 0.017591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1058-10_0_4_line_54 |  | 48 | 73 | 0.01602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1058-10_0_4_line_55 |  | 49 | 50 | 0.016015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1058-10_0_4_line_56 |  | 50 | 51 | 0.01613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1058-10_0_4_line_57 |  | 51 | 52 | 0.019447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1058-10_0_4_line_58 |  | 52 | 77 | 0.017184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1058-10_0_4_line_59 |  | 53 | 54 | 0.011329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1058-10_0_4_line_60 |  | 53 | 55 | 0.025017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_1058-10_0_4_line_61 |  | 54 | 56 | 0.011339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1058-10_0_4_line_62 |  | 54 | 57 | 0.009074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1058-10_0_4_line_63 |  | 55 | 58 | 0.018741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1058-10_0_4_line_64 |  | 55 | 59 | 0.13204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1058-10_0_4_line_65 |  | 55 | 60 | 0.049268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1058-10_0_4_line_66 |  | 56 | 61 | 0.036169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1058-10_0_4_line_67 |  | 57 | 62 | 0.024558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1058-10_0_4_line_68 |  | 58 | 63 | 0.0032723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1058-10_0_4_line_69 |  | 60 | 68 | 0.023602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1058-10_0_4_line_70 |  | 60 | 66 | 0.036938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1058-10_0_4_line_71 |  | 62 | 69 | 0.0015474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1058-10_0_4_line_72 |  | 63 | 64 | 0.01383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_1058-10_0_4_line_73 |  | 64 | 65 | 0.007836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1058-10_0_4_line_74 |  | 65 | 70 | 0.086107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1058-10_0_4_line_75 |  | 65 | 71 | 0.043617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1058-10_0_4_line_76 |  | 66 | 67 | 0.023487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1058-10_0_4_line_77 |  | 67 | 72 | 0.0016809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1058-10_0_4_line_78 |  | 69 | 113 | 0.0070901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1058-10_0_4_line_79 |  | 70 | 92 | 0.024658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1058-10_0_4_line_80 |  | 70 | 89 | 0.0249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1058-10_0_4_line_81 |  | 73 | 74 | 0.024173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1058-10_0_4_line_82 |  | 74 | 76 | 0.0043324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1058-10_0_4_line_83 |  | 75 | 77 | 0.024675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1058-10_0_4_line_84 |  | 77 | 109 | 0.0066798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1058-10_0_4_line_85 |  | 79 | 80 | 0.025514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1058-10_0_4_line_86 |  | 80 | 81 | 0.024313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1058-10_0_4_line_87 |  | 82 | 83 | 0.029705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1058-10_0_4_line_88 |  | 82 | 84 | 0.030322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1058-10_0_4_line_89 |  | 83 | 85 | 0.0082188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1058-10_0_4_line_90 |  | 85 | 86 | 0.025136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1058-10_0_4_line_91 |  | 87 | 88 | 0.0086791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1058-10_0_4_line_92 |  | 87 | 89 | 0.019228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1058-10_0_4_line_93 |  | 89 | 90 | 0.080138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1058-10_0_4_line_94 |  | 89 | 91 | 0.015066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1058-10_0_4_line_95 |  | 90 | 93 | 0.066094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1058-10_0_4_line_96 |  | 90 | 94 | 0.010929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1058-10_0_4_line_97 |  | 91 | 98 | 0.036495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1058-10_0_4_line_98 |  | 92 | 100 | 0.0092772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1058-10_0_4_line_99 |  | 93 | 97 | 0.023275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1058-10_0_4_line_100 |  | 93 | 95 | 0.038389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1058-10_0_4_line_101 |  | 94 | 101 | 0.0066758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1058-10_0_4_line_102 |  | 95 | 96 | 0.035232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1058-10_0_4_line_103 |  | 96 | 102 | 0.026633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1058-10_0_4_line_104 |  | 97 | 107 | 0.022454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1058-10_0_4_line_105 |  | 99 | 100 | 0.02631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1058-10_0_4_line_106 |  | 101 | 121 | 0.02015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1058-10_0_4_line_107 |  | 102 | 103 | 0.066145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1058-10_0_4_line_108 |  | 103 | 104 | 0.030858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1058-10_0_4_line_109 |  | 104 | 105 | 0.031723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1058-10_0_4_line_110 |  | 105 | 106 | 0.0081592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1058-10_0_4_line_111 |  | 107 | 120 | 0.0086155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1058-10_0_4_line_112 |  | 108 | 109 | 0.012693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1058-10_0_4_line_113 |  | 110 | 111 | 0.0016347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1058-10_0_4_line_114 |  | 110 | 112 | 0.0071086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1058-10_0_4_line_115 |  | 111 | 113 | 0.018587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1058-10_0_4_line_116 |  | 112 | 114 | 0.020036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1058-10_0_4_line_117 |  | 114 | 115 | 0.0023305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1058-10_0_4_line_118 |  | 115 | 116 | 0.031604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1058-10_0_4_line_119 |  | 117 | 118 | 0.030784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1058-10_0_4_line_120 |  | 118 | 119 | 0.024095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1058-10_0_4_trafo_60 | 0.63 MVA 20/0.4 kV | 122 | 76 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2666924.4468 | 1208121.8468 | 2666899.0939 | 1208125.3892
1 | 2666943.3018 | 1208119.2123 | 2666924.4468 | 1208121.8468
2 | 2666943.3018 | 1208119.2123 | 2666998.7 | 1208115.7093
3 | 2666998.7 | 1208115.7093 | 2667010.1662 | 1208114.982 | 2667025.2522 | 1208115.5516 | 2667037.2652 | 1208116.9096 | 2667044.1561 | 1208120.0778
4 | 2666998.7406 | 1208118.8672 | 2666998.7 | 1208115.7093
5 | 2666998.7406 | 1208118.8672 | 2667004.4607 | 1208118.6424 | 2667004.9463 | 1208118.6258
6 | 2667066.7367 | 1208138.4204 | 2667062.951 | 1208134.9758 | 2667058.0656 | 1208129.94 | 2667049.678 | 1208123.2862 | 2667044.1561 | 1208120.0778
7 | 2667066.7367 | 1208138.4204 | 2667041.9295 | 1208175.4645 | 2667034.1623 | 1208188.7187 | 2667029.6258 | 1208200.6751 | 2667027.2788 | 1208209.9322 | 2667025.3872 | 1208224.0085 | 2667024.8898 | 1208232.4192 | 2667024.9599 | 1208233.6207 | 2667029.2041 | 1208233.4682
8 | 2667066.7367 | 1208138.4204 | 2667095.8897 | 1208097.4318
9 | 2666712.0929 | 1208470.3949 | 2666713.4141 | 1208472.5888 | 2666716.0391 | 1208474.4415 | 2666764.9565 | 1208485.8731 | 2666801.4828 | 1208493.0861 | 2666815.7479 | 1208493.5571 | 2666828.7233 | 1208491.0564 | 2666852.4654 | 1208483.6955 | 2666865.6484 | 1208480.997 | 2666879.6368 | 1208479.0191 | 2666889.0322 | 1208477.8014 | 2666905.4434 | 1208478.0855 | 2666910.0419 | 1208476.8251 | 2666919.4693 | 1208472.7617 | 2666925.0546 | 1208468.7675
10 | 2666856.6901 | 1208378.067 | 2666749.8728 | 1208449.8379 | 2666741.9485 | 1208454.7968 | 2666719.7572 | 1208466.934 | 2666712.0929 | 1208470.3949
11 | 2666853.3733 | 1208374.8501 | 2666856.6901 | 1208378.067
12 | 2666856.6901 | 1208378.067 | 2666867.4481 | 1208392.9966 | 2666878.4877 | 1208409.6021
13 | 2666853.3733 | 1208374.8501 | 2666879.9522 | 1208356.889
14 | 2666896.374 | 1208345.7917 | 2666879.9522 | 1208356.889
15 | 2666898.839 | 1208349.7106 | 2666885.6796 | 1208358.5638
16 | 2666898.839 | 1208349.7106 | 2666906.4776 | 1208344.5842
17 | 2666896.374 | 1208345.7917 | 2666898.2265 | 1208348.7365 | 2666898.839 | 1208349.7106
18 | 2666896.374 | 1208345.7917 | 2666894.4094 | 1208342.6678 | 2666893.8343 | 1208341.7497 | 2666897.1388 | 1208339.6003
19 | 2666897.1388 | 1208339.6003 | 2666901.1101 | 1208337.0172 | 2666917.7191 | 1208326.1839
20 | 2666955.7016 | 1208300.8848 | 2666930.8039 | 1208317.6492 | 2666917.7191 | 1208326.1839
21 | 2666951.9505 | 1208295.0391 | 2666955.7016 | 1208300.8848
22 | 2666970.075 | 1208301.9022 | 2666969.4762 | 1208301.0616 | 2666967.4029 | 1208298.1477 | 2666957.9956 | 1208304.4571 | 2666955.7016 | 1208300.8848
23 | 2666951.9505 | 1208295.0391 | 2666964.0231 | 1208287.2493
24 | 2666951.9505 | 1208295.0391 | 2666944.6871 | 1208297.3035 | 2666930.1862 | 1208299.8032
25 | 2666970.075 | 1208301.9022 | 2666974.6331 | 1208298.8403
26 | 2666989.9055 | 1208270.5487 | 2666964.0231 | 1208287.2493
27 | 2667075.0226 | 1208263.6902 | 2667067.8762 | 1208264.9996 | 2667072.3561 | 1208281.082 | 2667076.3235 | 1208291.344
28 | 2667076.3235 | 1208291.344 | 2667065.4504 | 1208298.8598 | 2667065.3821 | 1208311.7002 | 2667055.873 | 1208320.2987
29 | 2667076.3235 | 1208291.344 | 2667082.6667 | 1208296.5518 | 2667094.3099 | 1208299.6623 | 2667109.5804 | 1208302.0354 | 2667122.4364 | 1208302.5487
30 | 2667075.0226 | 1208263.6902 | 2667073.5139 | 1208267.3644 | 2667073.4734 | 1208270.9662 | 2667076.7588 | 1208285.7677 | 2667078.5288 | 1208289.2786 | 2667081.9455 | 1208292.3967 | 2667085.7497 | 1208294.185 | 2667087.988 | 1208294.723
31 | 2667075.0226 | 1208263.6902 | 2667079.8147 | 1208262.8102 | 2667124.8651 | 1208260.0415
32 | 2667051.9838 | 1208267.8896 | 2667061.5681 | 1208266.1406 | 2667067.8762 | 1208264.9996 | 2667075.0226 | 1208263.6902
33 | 2667055.873 | 1208320.2987 | 2667064.6455 | 1208320.4195 | 2667070.6473 | 1208318.7859 | 2667079.1509 | 1208321.8611 | 2667080.8062 | 1208326.7827 | 2667085.6812 | 1208330.0284
34 | 2667122.4364 | 1208302.5487 | 2667143.3072 | 1208303.3821 | 2667146.538 | 1208303.3086
35 | 2667049.9838 | 1208255.7485 | 2667050.1548 | 1208256.7733 | 2667050.8381 | 1208260.9169 | 2667050.9949 | 1208261.8525 | 2667051.1302 | 1208262.6657 | 2667051.7987 | 1208266.7757 | 2667051.9838 | 1208267.8896
36 | 2667051.9838 | 1208267.8896 | 2667028.45 | 1208272.3609
37 | 2667019.5771 | 1208257.297 | 2667021.896 | 1208256.6226 | 2667027.0374 | 1208255.1127 | 2667028.2427 | 1208254.7594 | 2667029.5777 | 1208254.363 | 2667034.1545 | 1208253.0247 | 2667035.9395 | 1208252.5 | 2667041.0243 | 1208254.6806 | 2667044.549 | 1208255.6319 | 2667047.4277 | 1208255.8866 | 2667049.9838 | 1208255.7485
38 | 2667049.9838 | 1208255.7485 | 2667055.1569 | 1208255.4843 | 2667065.0067 | 1208254.4609 | 2667079.2833 | 1208253.3955
39 | 2666974.6331 | 1208298.8403 | 2666986.7372 | 1208290.7045 | 2666998.4491 | 1208283.6315 | 2667008.4037 | 1208278.6958 | 2667019 | 1208274.1564 | 2667028.45 | 1208272.3609
40 | 2667118.9694 | 1208298.5221 | 2667103.4537 | 1208297.1858 | 2667090.3598 | 1208295.293 | 2667087.988 | 1208294.723
41 | 2667124.8651 | 1208260.0415 | 2667152.0686 | 1208258.3697
42 | 2667038.6131 | 1208233.1181 | 2667029.2041 | 1208233.4682
43 | 2667019.5771 | 1208257.297 | 2667021.896 | 1208256.6226 | 2667027.0374 | 1208255.1127 | 2667028.2427 | 1208254.7594 | 2667025.3819 | 1208240.7298 | 2667024.9599 | 1208233.6207 | 2667029.2041 | 1208233.4682
44 | 2666974.6331 | 1208298.8403 | 2666987.1912 | 1208319.4338
45 | 2667019.5771 | 1208257.297 | 2667020.8263 | 1208253.0306 | 2667020.8893 | 1208247.4279 | 2667020.4524 | 1208239.0302
46 | 2667079.2833 | 1208253.3955 | 2667082.7442 | 1208253.1372 | 2667096.9477 | 1208252.3741 | 2667104.2487 | 1208250.833 | 2667111.2983 | 1208248.9231
47 | 2666997.2835 | 1208335.9839 | 2666987.1912 | 1208319.4338
48 | 2667085.6812 | 1208330.0284 | 2667081.0907 | 1208339.3492 | 2667081.6186 | 1208340.9147
49 | 2667146.538 | 1208303.3086 | 2667174.1712 | 1208302.6804
50 | 2667153.4016 | 1208299.7922 | 2667140.1247 | 1208299.7218 | 2667121.8655 | 1208298.7715 | 2667118.9694 | 1208298.5221
51 | 2667180.1251 | 1208256.6454 | 2667152.0686 | 1208258.3697
52 | 2667142.8644 | 1208248.7248 | 2667132.8378 | 1208247.3078 | 2667127.0773 | 1208247.0762 | 2667121.365 | 1208247.2899 | 2667116.08 | 1208248.042 | 2667111.3411 | 1208248.9115 | 2667111.2983 | 1208248.9231
53 | 2666997.2835 | 1208335.9839 | 2666982.4283 | 1208345.4051
54 | 2666997.2835 | 1208335.9839 | 2667005.6222 | 1208349.6747
55 | 2666920.3836 | 1208405.8538 | 2666927.2104 | 1208400.7821 | 2666933.3349 | 1208396.4346
56 | 2666946.4883 | 1208387.0975 | 2666933.3349 | 1208396.4346
57 | 2666946.4883 | 1208387.0975 | 2666961.0695 | 1208376.747 | 2666962.402 | 1208375.9249
58 | 2666976.8076 | 1208366.5729 | 2666972.2547 | 1208369.846 | 2666962.402 | 1208375.9249
59 | 2667096.7991 | 1208385.932 | 2667089.0629 | 1208394.2078
60 | 2667090.7314 | 1208415.7377 | 2667083.84 | 1208399.7949 | 2667089.0629 | 1208394.2078
61 | 2667096.7991 | 1208385.932 | 2667093.176 | 1208375.1879
62 | 2667096.7991 | 1208385.932 | 2667105.4349 | 1208383.1464
63 | 2667090.7314 | 1208415.7377 | 2667077.8017 | 1208420.9067 | 2667073.4217 | 1208422.91
64 | 2667090.7314 | 1208415.7377 | 2667103.1003 | 1208411.085 | 2667128.6946 | 1208402.6898 | 2667148.7837 | 1208397.0789 | 2667179.4756 | 1208390.3978 | 2667218.7155 | 1208384.9039
65 | 2667090.7314 | 1208415.7377 | 2667091.9689 | 1208418.5978 | 2667127.1524 | 1208406.6415 | 2667128.2532 | 1208410.1672 | 2667123.1874 | 1208411.7223
66 | 2667081.6186 | 1208340.9147 | 2667093.176 | 1208375.1879
67 | 2667105.4349 | 1208383.1464 | 2667126.1081 | 1208376.4779 | 2667128.841 | 1208375.7187
68 | 2667070.4459 | 1208424.2712 | 2667073.4217 | 1208422.91
69 | 2667130.2708 | 1208434.2379 | 2667127.5794 | 1208425.4578 | 2667123.1874 | 1208411.7223
70 | 2667123.1874 | 1208411.7223 | 2667128.2532 | 1208410.1672 | 2667137.6218 | 1208407.293 | 2667156.4022 | 1208402.4456 | 2667158.795 | 1208401.95
71 | 2667130.332 | 1208375.3046 | 2667128.841 | 1208375.7187
72 | 2667069.0114 | 1208432.5373 | 2667064.3975 | 1208427.0376 | 2667070.4459 | 1208424.2712
73 | 2667074.0989 | 1208438.5092 | 2667069.0114 | 1208432.5373
74 | 2667133.7648 | 1208500.0731 | 2667132.5279 | 1208498.5138 | 2667128.8425 | 1208494.292 | 2667115.767 | 1208477.9683 | 2667103.2055 | 1208465.2749 | 2667089.3948 | 1208451.4446 | 2667077.8492 | 1208440.3525 | 2667074.1515 | 1208438.5654 | 2667074.0989 | 1208438.5092
75 | 2667074.0989 | 1208438.5092 | 2667068.717 | 1208441.1392 | 2667065.3354 | 1208442.3464 | 2667063.5068 | 1208442.0146 | 2667061.9064 | 1208441.0071 | 2667059.2054 | 1208439.8316 | 2667057.901 | 1208439.539 | 2667052.6634 | 1208440.8254 | 2667050.9527 | 1208440.1613 | 2667048.9054 | 1208438.9932 | 2667046.391 | 1208437.4529 | 2667037.9485 | 1208431.6657 | 2667035.3431 | 1208429.7499
76 | 2667158.795 | 1208401.95 | 2667162.0261 | 1208416.8177 | 2667163.6988 | 1208424.9193
77 | 2667162.0673 | 1208425.3234 | 2667163.6988 | 1208424.9193
78 | 2667130.332 | 1208375.3046 | 2667137.1634 | 1208373.4068
79 | 2667133.7648 | 1208500.0731 | 2667138.8357 | 1208496.7059 | 2667155.0884 | 1208487.7216
80 | 2667133.7648 | 1208500.0731 | 2667139.3439 | 1208505.5948 | 2667145.2787 | 1208512.6103 | 2667148.8449 | 1208517.9648 | 2667149.6217 | 1208519.1965
81 | 2667005.6222 | 1208349.6747 | 2667018.2078 | 1208370.3129
82 | 2667020.4634 | 1208374.0118 | 2667018.2078 | 1208370.3129
83 | 2666976.8076 | 1208366.5729 | 2666975.5168 | 1208363.7122 | 2666974.5576 | 1208354.3401 | 2666979.3344 | 1208347.3672 | 2666982.4283 | 1208345.4051
84 | 2666976.8076 | 1208366.5729 | 2666980.2997 | 1208372.2672
85 | 2667174.1712 | 1208302.6804 | 2667178.959 | 1208302.5715 | 2667199.6477 | 1208301.3487
86 | 2667223.9183 | 1208299.9141 | 2667199.6477 | 1208301.3487
87 | 2667183.6942 | 1208298.6173 | 2667190.6932 | 1208298.2787 | 2667213.3475 | 1208296.8668
88 | 2667183.6942 | 1208298.6173 | 2667158.8117 | 1208299.8209 | 2667153.4016 | 1208299.7922
89 | 2667213.3475 | 1208296.8668 | 2667221.5504 | 1208296.3556
90 | 2667246.6402 | 1208294.8317 | 2667231.0325 | 1208295.7646 | 2667221.5504 | 1208296.3556
91 | 2667166.4348 | 1208509.8776 | 2667171.3785 | 1208507.2339 | 2667174.1484 | 1208505.9034
92 | 2667149.6217 | 1208519.1965 | 2667154.926 | 1208516.032 | 2667166.4348 | 1208509.8776
93 | 2667119.9691 | 1208583.5915 | 2667119.3941 | 1208582.6622 | 2667118.2632 | 1208579.7922 | 2667116.6628 | 1208574.7266 | 2667115.5604 | 1208569.3221 | 2667115.5631 | 1208560.9725 | 2667116.3024 | 1208555.3996 | 2667117.1828 | 1208551.4849 | 2667119.7882 | 1208544.9324 | 2667123.2651 | 1208539.3014 | 2667129.1142 | 1208532.3073 | 2667133.791 | 1208528.8244 | 2667139.7787 | 1208525.0561 | 2667144.1644 | 1208522.4483 | 2667149.6217 | 1208519.1965
94 | 2667149.6217 | 1208519.1965 | 2667151.0634 | 1208522.8261 | 2667152.7681 | 1208525.3802 | 2667154.2036 | 1208527.531 | 2667157.2539 | 1208532.1125
95 | 2667155.506 | 1208637.4241 | 2667155.5153 | 1208635.2451 | 2667154.7693 | 1208629.9224 | 2667152.1177 | 1208623.0216 | 2667148.9178 | 1208616.8708 | 2667141.8801 | 1208609.2425 | 2667127.9813 | 1208595.1664 | 2667124.4485 | 1208590.8908 | 2667119.9691 | 1208583.5915
96 | 2667119.9691 | 1208583.5915 | 2667109.0406 | 1208583.6579
97 | 2667150.2973 | 1208567.934 | 2667157.2539 | 1208532.1125
98 | 2667155.0884 | 1208487.7216 | 2667163.1791 | 1208483.2492 | 2667163.209 | 1208483.2361
99 | 2667155.506 | 1208637.4241 | 2667132.231 | 1208637.3146
100 | 2667146.7689 | 1208667.9779 | 2667151.5068 | 1208663.1171 | 2667156.3839 | 1208653.9886 | 2667159.3099 | 1208644.6158 | 2667159.748 | 1208637.4385 | 2667155.506 | 1208637.4241
101 | 2667109.0406 | 1208583.6579 | 2667102.3649 | 1208583.6985
102 | 2667146.7689 | 1208667.9779 | 2667141.3685 | 1208670.919 | 2667135.964 | 1208673.5376 | 2667131.7843 | 1208675.414 | 2667125.8684 | 1208676.8706 | 2667113.484 | 1208677.5429
103 | 2667113.484 | 1208677.5429 | 2667113.484 | 1208677.5429 | 2667087.2844 | 1208672.7585
104 | 2667109.7769 | 1208637.2089 | 2667132.231 | 1208637.3146
105 | 2667187.3148 | 1208472.7012 | 2667186.7578 | 1208472.8859 | 2667163.209 | 1208483.2361
106 | 2667082.2153 | 1208583.821 | 2667102.3649 | 1208583.6985
107 | 2667040.793 | 1208706.9553 | 2667042.0121 | 1208697.919 | 2667046.498 | 1208688.408 | 2667052.3423 | 1208681.147 | 2667061.9849 | 1208674.818 | 2667073.1299 | 1208672.1416 | 2667085.0027 | 1208672.3418 | 2667087.2844 | 1208672.7585
108 | 2667040.793 | 1208706.9553 | 2667043.4092 | 1208717.6913 | 2667048.2663 | 1208725.2171 | 2667053.2522 | 1208730.065 | 2667056.5351 | 1208732.1632
109 | 2667086.3327 | 1208742.6999 | 2667059.8569 | 1208734.2862 | 2667056.5351 | 1208732.1632
110 | 2667086.3327 | 1208742.6999 | 2667087.048 | 1208739.9396 | 2667092.0761 | 1208741.6394
111 | 2667109.7769 | 1208637.2089 | 2667101.1615 | 1208637.1684
112 | 2666986.9357 | 1208383.0879 | 2666980.2997 | 1208372.2672
113 | 2667156.6776 | 1208368.1114 | 2667155.087 | 1208368.4882
114 | 2667156.6776 | 1208368.1114 | 2667163.5948 | 1208366.4728
115 | 2667155.087 | 1208368.4882 | 2667153.61 | 1208368.8381 | 2667137.1634 | 1208373.4068
116 | 2667183.3504 | 1208363.1642 | 2667165.6623 | 1208365.983 | 2667163.5948 | 1208366.4728
117 | 2667185.6518 | 1208362.7975 | 2667183.3504 | 1208363.1642
118 | 2667185.6518 | 1208362.7975 | 2667191.5967 | 1208361.8501 | 2667193.2234 | 1208361.2013 | 2667194.9879 | 1208357.7746 | 2667196.7706 | 1208356.1048 | 2667201.3635 | 1208355.356 | 2667212.5824 | 1208354.9487 | 2667214.2299 | 1208354.7767
119 | 2667180.1251 | 1208256.6454 | 2667185.783 | 1208256.2977 | 2667210.7864 | 1208253.9241
120 | 2667210.7864 | 1208253.9241 | 2667214.4695 | 1208253.5745 | 2667227.8508 | 1208250.879 | 2667234.3903 | 1208249.2276

## bus_geodata
| x | y | coords
0 | 2666924.4468 | 1208121.8468
1 | 2666899.0939 | 1208125.3892
2 | 2666943.3018 | 1208119.2123
3 | 2666998.7 | 1208115.7093
4 | 2666998.7406 | 1208118.8672
5 | 2667004.9463 | 1208118.6258
6 | 2667044.1561 | 1208120.0778
7 | 2667066.7367 | 1208138.4204
8 | 2666925.0545 | 1208468.7675
9 | 2666712.0929 | 1208470.3949
10 | 2666856.6901 | 1208378.067
11 | 2666853.3733 | 1208374.8501
12 | 2666878.4877 | 1208409.6021
13 | 2666879.9522 | 1208356.889
14 | 2666885.6796 | 1208358.5638
15 | 2666898.839 | 1208349.7106
16 | 2666896.374 | 1208345.7917
17 | 2666917.7191 | 1208326.1839
18 | 2666897.1388 | 1208339.6003
19 | 2666955.7016 | 1208300.8848
20 | 2666951.9505 | 1208295.0391
21 | 2666970.075 | 1208301.9022
22 | 2666964.0231 | 1208287.2493
23 | 2666930.1862 | 1208299.8032
24 | 2667076.3235 | 1208291.344
25 | 2667075.0226 | 1208263.6902
26 | 2667055.873 | 1208320.2987
27 | 2667122.4364 | 1208302.5487
28 | 2667051.9838 | 1208267.8896
29 | 2667049.9838 | 1208255.7485
30 | 2667028.45 | 1208272.3609
31 | 2667087.988 | 1208294.723
32 | 2667124.8651 | 1208260.0415
33 | 2667029.2041 | 1208233.4682
34 | 2667095.8897 | 1208097.4318
35 | 2666974.6331 | 1208298.8403
36 | 2667019.5771 | 1208257.297
37 | 2667079.2833 | 1208253.3955
38 | 2667038.6131 | 1208233.1181
39 | 2666987.1912 | 1208319.4338
40 | 2667020.4524 | 1208239.0302
41 | 2666906.4776 | 1208344.5842
42 | 2666989.9055 | 1208270.5487
43 | 2667085.6812 | 1208330.0284
44 | 2667146.538 | 1208303.3086
45 | 2667118.9694 | 1208298.5221
46 | 2667152.0686 | 1208258.3697
47 | 2667111.2983 | 1208248.9231
48 | 2666997.2835 | 1208335.9839
49 | 2666920.3836 | 1208405.8538
50 | 2666933.3349 | 1208396.4346
51 | 2666946.4883 | 1208387.0975
52 | 2666962.402 | 1208375.9249
53 | 2667089.0629 | 1208394.2078
54 | 2667096.7991 | 1208385.932
55 | 2667090.7314 | 1208415.7377
56 | 2667093.176 | 1208375.1879
57 | 2667105.4349 | 1208383.1464
58 | 2667073.4217 | 1208422.91
59 | 2667218.7155 | 1208384.9039
60 | 2667123.1874 | 1208411.7223
61 | 2667081.6186 | 1208340.9147
62 | 2667128.841 | 1208375.7187
63 | 2667070.4459 | 1208424.2712
64 | 2667069.0114 | 1208432.5373
65 | 2667074.0989 | 1208438.5092
66 | 2667158.795 | 1208401.95
67 | 2667163.6988 | 1208424.9193
68 | 2667130.2708 | 1208434.2379
69 | 2667130.332 | 1208375.3046
70 | 2667133.7648 | 1208500.0731
71 | 2667035.3431 | 1208429.7499
72 | 2667162.0673 | 1208425.3234
73 | 2667005.6222 | 1208349.6747
74 | 2667018.2078 | 1208370.3129
75 | 2666982.4283 | 1208345.4051
76 | 2667020.4634 | 1208374.0118
77 | 2666976.8076 | 1208366.5729
78 | 2667142.8644 | 1208248.7248
79 | 2667174.1712 | 1208302.6804
80 | 2667199.6477 | 1208301.3487
81 | 2667223.9183 | 1208299.9141
82 | 2667183.6942 | 1208298.6173
83 | 2667213.3475 | 1208296.8668
84 | 2667153.4016 | 1208299.7922
85 | 2667221.5504 | 1208296.3556
86 | 2667246.6402 | 1208294.8317
87 | 2667166.4348 | 1208509.8776
88 | 2667174.1484 | 1208505.9034
89 | 2667149.6217 | 1208519.1965
90 | 2667119.9691 | 1208583.5915
91 | 2667157.2539 | 1208532.1125
92 | 2667155.0884 | 1208487.7216
93 | 2667155.506 | 1208637.4241
94 | 2667109.0406 | 1208583.6579
95 | 2667146.7689 | 1208667.9779
96 | 2667113.484 | 1208677.5429
97 | 2667132.231 | 1208637.3146
98 | 2667150.2973 | 1208567.934
99 | 2667187.3148 | 1208472.7012
100 | 2667163.209 | 1208483.2361
101 | 2667102.3649 | 1208583.6985
102 | 2667087.2844 | 1208672.7585
103 | 2667040.793 | 1208706.9553
104 | 2667056.5351 | 1208732.1632
105 | 2667086.3327 | 1208742.6999
106 | 2667092.0761 | 1208741.6394
107 | 2667109.7769 | 1208637.2089
108 | 2666986.9357 | 1208383.0879
109 | 2666980.2997 | 1208372.2672
110 | 2667156.6776 | 1208368.1114
111 | 2667155.087 | 1208368.4882
112 | 2667163.5948 | 1208366.4728
113 | 2667137.1634 | 1208373.4068
114 | 2667183.3504 | 1208363.1642
115 | 2667185.6518 | 1208362.7975
116 | 2667214.2299 | 1208354.7767
117 | 2667180.1251 | 1208256.6454
118 | 2667210.7864 | 1208253.9241
119 | 2667234.3903 | 1208249.2276
120 | 2667101.1615 | 1208637.1684
121 | 2667082.2153 | 1208583.821
122 | 2667005.6222 | 1208349.6747

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97595 | -0.46339 | 0.012632 | 0.0031659
1 | 0.97584 | -0.46554 | 0.0045985 | 0.0011525
2 | 0.97625 | -0.45739 | 0 | 0
3 | 0.97714 | -0.43996 | 0 | 0
4 | 0.97711 | -0.44043 | 0 | 0
5 | 0.97707 | -0.44136 | 0.0082104 | 0.0020577
6 | 0.97823 | -0.4185 | 0.0019318 | 0.00048414
7 | 0.97897 | -0.40393 | 0 | 0
8 | 0.97101 | -0.55959 | 0.031127 | 0.0078011
9 | 0.97743 | -0.43327 | 0 | 0
10 | 0.98242 | -0.3364 | 0 | 0
11 | 0.98256 | -0.33363 | 0 | 0
12 | 0.98234 | -0.33791 | 0.0021779 | 0.00054584
13 | 0.98356 | -0.31435 | 0.0098117 | 0.0024591
14 | 0.9842 | -0.30201 | 0.0073856 | 0.001851
15 | 0.98431 | -0.2999 | 0 | 0
16 | 0.98436 | -0.29896 | 0 | 0
17 | 0.98622 | -0.26295 | 0.0040369 | 0.0010117
18 | 0.9848 | -0.29043 | 0.0078885 | 0.001977
19 | 0.98903 | -0.20882 | 0 | 0
20 | 0.98894 | -0.21061 | 0 | 0
21 | 0.99054 | -0.17977 | 0 | 0
22 | 0.98881 | -0.21312 | 0.0049106 | 0.0012307
23 | 0.98884 | -0.2125 | 0.0047426 | 0.0011886
24 | 0.98262 | -0.33266 | 0 | 0
25 | 0.98407 | -0.3046 | 0 | 0
26 | 0.98115 | -0.36121 | 0 | 0
27 | 0.98192 | -0.34642 | 0.0044408 | 0.001113
28 | 0.98524 | -0.28187 | 0 | 0
29 | 0.98448 | -0.2967 | 0 | 0
30 | 0.98681 | -0.25149 | 0.012108 | 0.0030346
31 | 0.98338 | -0.31792 | 0.0036628 | 0.00091797
32 | 0.98322 | -0.32103 | 0.0031669 | 0.00079371
33 | 0.98195 | -0.3459 | 0 | 0
34 | 0.9789 | -0.40542 | 0.0016225 | 0.00040663
35 | 0.99095 | -0.1719 | 0 | 0
36 | 0.98311 | -0.32318 | 0 | 0
37 | 0.98392 | -0.30763 | 0.0066487 | 0.0016663
38 | 0.98188 | -0.34712 | 0.0072407 | 0.0018147
39 | 0.99305 | -0.13174 | 0.017853 | 0.0044745
40 | 0.98294 | -0.32655 | 0.010147 | 0.0025432
41 | 0.98428 | -0.30055 | 0.0039284 | 0.00098454
42 | 0.98867 | -0.21579 | 0.0048626 | 0.0012187
43 | 0.97983 | -0.38704 | 0.0044787 | 0.0011225
44 | 0.98167 | -0.35132 | 0.0041562 | 0.0010416
45 | 0.98293 | -0.32687 | 0.0032969 | 0.00082628
46 | 0.98285 | -0.32844 | 0.0029858 | 0.00074831
47 | 0.9835 | -0.31583 | 0.0070579 | 0.0017689
48 | 0.99482 | -0.098066 | 0 | 0
49 | 0.9879 | -0.23193 | 0.025094 | 0.0062891
50 | 0.98827 | -0.22476 | 0.014926 | 0.0037409
51 | 0.98886 | -0.21324 | 0.016754 | 0.004199
52 | 0.98988 | -0.19358 | 0.015729 | 0.0039421
53 | 0.97757 | -0.43126 | 0.0031912 | 0.00079978
54 | 0.97782 | -0.4264 | 0 | 0
55 | 0.97704 | -0.44165 | 0 | 0
56 | 0.97818 | -0.41918 | 0.0031939 | 0.00080048
57 | 0.97743 | -0.43391 | 0.0055176 | 0.0013828
58 | 0.97683 | -0.44581 | 0.0028267 | 0.00070845
59 | 0.97657 | -0.45083 | 0.0038006 | 0.00095253
60 | 0.97527 | -0.47648 | 0 | 0
61 | 0.97938 | -0.39568 | 0.015107 | 0.0037861
62 | 0.97652 | -0.4518 | 0.0032475 | 0.00081391
63 | 0.97679 | -0.4465 | 0.0020207 | 0.00050643
64 | 0.97665 | -0.44926 | 0 | 0
65 | 0.97657 | -0.45083 | 0 | 0
66 | 0.97438 | -0.49398 | 0 | 0
67 | 0.97381 | -0.50512 | 0.012771 | 0.0032006
68 | 0.97498 | -0.48202 | 0.012809 | 0.0032103
69 | 0.97647 | -0.45283 | 0.0070542 | 0.0017679
70 | 0.97576 | -0.46672 | 0 | 0
71 | 0.97643 | -0.45353 | 0.0033891 | 0.00084939
72 | 0.97379 | -0.50553 | 0.013058 | 0.0032727
73 | 0.99668 | -0.062769 | 0 | 0
74 | 0.99948 | -0.0097561 | 0.015168 | 0.0038015
75 | 0.99309 | -0.13142 | 0.015907 | 0.0039867
76 | 1 | 0 | -0.52668 | -0.13489
77 | 0.99102 | -0.17145 | 0 | 0
78 | 0.98329 | -0.31981 | 0.0069554 | 0.0017432
79 | 0.98148 | -0.35486 | 0.0039377 | 0.00098689
80 | 0.98141 | -0.35631 | 0.0020109 | 0.00050399
81 | 0.98139 | -0.3568 | 0.0011259 | 0.00028217
82 | 0.98227 | -0.33977 | 0.0028199 | 0.00070675
83 | 0.98209 | -0.34322 | 0.0018042 | 0.00045218
84 | 0.98252 | -0.33471 | 0.0033544 | 0.00084069
85 | 0.98205 | -0.3439 | 0.0018021 | 0.00045164
86 | 0.98199 | -0.34518 | 0.0028148 | 0.00070545
87 | 0.975 | -0.48178 | 0.00096953 | 0.00024299
88 | 0.97497 | -0.4823 | 0.0032277 | 0.00080893
89 | 0.97507 | -0.4803 | 0 | 0
90 | 0.9734 | -0.51321 | 0 | 0
91 | 0.97503 | -0.48119 | 0 | 0
92 | 0.97552 | -0.47149 | 0.0027798 | 0.00069668
93 | 0.97244 | -0.53225 | 0 | 0
94 | 0.97333 | -0.51457 | 0.0020592 | 0.00051608
95 | 0.97209 | -0.53916 | 0 | 0
96 | 0.97177 | -0.5455 | 0.0031521 | 0.00078999
97 | 0.97231 | -0.53478 | 0.0034101 | 0.00085466
98 | 0.97492 | -0.48334 | 0.0032128 | 0.00080521
99 | 0.97533 | -0.47522 | 0.0049869 | 0.0012498
100 | 0.97545 | -0.47282 | 0.0028041 | 0.00070278
101 | 0.9733 | -0.51514 | 0.0025036 | 0.00062745
102 | 0.9716 | -0.54875 | 0.0010869 | 0.00027241
103 | 0.97126 | -0.55549 | 0 | 0
104 | 0.9711 | -0.55863 | 0.0028117 | 0.00070468
105 | 0.97102 | -0.56022 | 0 | 0
106 | 0.971 | -0.56062 | 0.0027001 | 0.00067672
107 | 0.97226 | -0.5358 | 0.0012368 | 0.00030997
108 | 0.99076 | -0.17646 | 0.01222 | 0.0030625
109 | 0.9909 | -0.17371 | 0.0068566 | 0.0017184
110 | 0.97579 | -0.46633 | 0.0067954 | 0.0017031
111 | 0.97582 | -0.46563 | 0.0030016 | 0.00075228
112 | 0.97568 | -0.46848 | 0.0030016 | 0.00075228
113 | 0.97628 | -0.45667 | 0.0032476 | 0.00081391
114 | 0.97542 | -0.47345 | 0.0063525 | 0.0015921
115 | 0.97541 | -0.47375 | 0.0053567 | 0.0013425
116 | 0.97535 | -0.47481 | 0.0018297 | 0.00045856
117 | 0.98253 | -0.33457 | 0.0061268 | 0.0015355
118 | 0.98236 | -0.33788 | 0.002943 | 0.00073759
119 | 0.9823 | -0.33919 | 0.0030099 | 0.00075436
120 | 0.97225 | -0.536 | 0.0012369 | 0.00030999
121 | 0.97326 | -0.51594 | 0.0021537 | 0.00053977
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0045989 | 0.0011525 | -0.0045985 | -0.0011525 | 4.72e-07 | -1.777e-08 | 0.0070119 | 0.007012 | 0.007012 | 0.97595 | -0.46339 | 0.97584 | -0.46554 | 1.9264
1 | -0.017231 | -0.0043184 | 0.017236 | 0.0043213 | 4.9277e-06 | 2.9158e-06 | 0.026272 | 0.026272 | 0.026272 | 0.97595 | -0.46339 | 0.97625 | -0.45739 | 7.2176
2 | -0.017236 | -0.0043213 | 0.01725 | 0.0043298 | 1.4326e-05 | 8.4758e-06 | 0.026272 | 0.026272 | 0.026272 | 0.97625 | -0.45739 | 0.97714 | -0.43996 | 7.2176
3 | -0.025461 | -0.0063877 | 0.025487 | 0.0064039 | 2.6083e-05 | 1.6113e-05 | 0.038776 | 0.038775 | 0.038776 | 0.97714 | -0.43996 | 0.97823 | -0.4185 | 10.6527
4 | 0.0082109 | 0.0020579 | -0.0082107 | -0.0020579 | 1.8521e-07 | 7.8966e-08 | 0.012504 | 0.012504 | 0.012504 | 0.97714 | -0.43996 | 0.97711 | -0.44043 | 3.4351
5 | 0.0082107 | 0.0020579 | -0.0082104 | -0.0020577 | 3.6412e-07 | 1.5525e-07 | 0.012504 | 0.012504 | 0.012504 | 0.97711 | -0.44043 | 0.97707 | -0.44136 | 3.4351
6 | -0.027419 | -0.006888 | 0.027438 | 0.0068998 | 1.9071e-05 | 1.1838e-05 | 0.041714 | 0.041714 | 0.041714 | 0.97823 | -0.4185 | 0.97897 | -0.40393 | 11.4599
7 | -0.029061 | -0.0073059 | 0.029142 | 0.0073562 | 8.0778e-05 | 5.0306e-05 | 0.04418 | 0.044179 | 0.04418 | 0.97897 | -0.40393 | 0.98195 | -0.3459 | 12.1373
8 | 0.0016226 | 0.00040607 | -0.0016225 | -0.00040663 | 1.1472e-07 | -5.5896e-07 | 0.0024661 | 0.0024663 | 0.0024663 | 0.97897 | -0.40393 | 0.9789 | -0.40542 | 0.67755
9 | -0.031127 | -0.0078011 | 0.031315 | 0.007919 | 0.00018852 | 0.0001179 | 0.0477 | 0.047699 | 0.0477 | 0.97101 | -0.55959 | 0.97743 | -0.43327 | 13.1043
10 | -0.031315 | -0.007919 | 0.031461 | 0.0080104 | 0.00014623 | 9.1431e-05 | 0.047699 | 0.047698 | 0.047699 | 0.97743 | -0.43327 | 0.98242 | -0.3364 | 13.104
11 | -0.033639 | -0.0085559 | 0.033644 | 0.0085587 | 4.4998e-06 | 2.8214e-06 | 0.050997 | 0.050997 | 0.050997 | 0.98242 | -0.3364 | 0.98256 | -0.33363 | 14.0101
12 | 0.0021781 | 0.00054546 | -0.0021779 | -0.00054584 | 1.5648e-07 | -3.853e-07 | 0.0032989 | 0.0032991 | 0.0032991 | 0.98242 | -0.3364 | 0.98234 | -0.33791 | 0.90634
13 | -0.033644 | -0.0085587 | 0.033675 | 0.0085783 | 3.1285e-05 | 1.9615e-05 | 0.050997 | 0.050997 | 0.050997 | 0.98256 | -0.33363 | 0.98356 | -0.31435 | 14.0101
14 | -0.043487 | -0.011037 | 0.043519 | 0.011058 | 3.2219e-05 | 2.0369e-05 | 0.065841 | 0.06584 | 0.065841 | 0.98356 | -0.31435 | 0.98436 | -0.29896 | 18.0881
15 | -0.0073856 | -0.001851 | 0.0073864 | 0.0018513 | 7.4158e-07 | 2.7304e-07 | 0.011166 | 0.011166 | 0.011166 | 0.9842 | -0.30201 | 0.98431 | -0.2999 | 3.0677
16 | 0.0039285 | 0.0009845 | -0.0039284 | -0.00098454 | 1.2167e-07 | -3.9057e-08 | 0.0059388 | 0.0059389 | 0.0059389 | 0.98431 | -0.2999 | 0.98428 | -0.30055 | 1.6316
17 | -0.011315 | -0.0028358 | 0.011315 | 0.0028361 | 5.0767e-07 | 2.6609e-07 | 0.017105 | 0.017105 | 0.017105 | 0.98431 | -0.2999 | 0.98436 | -0.29896 | 4.6992
18 | -0.054835 | -0.013894 | 0.054857 | 0.013908 | 2.2486e-05 | 1.428e-05 | 0.082945 | 0.082945 | 0.082945 | 0.98436 | -0.29896 | 0.9848 | -0.29043 | 22.7872
19 | 0.062828 | 0.015938 | -0.062746 | -0.015885 | 8.2908e-05 | 5.2748e-05 | 0.094865 | 0.094865 | 0.094865 | 0.98622 | -0.26295 | 0.9848 | -0.29043 | 26.0618
20 | -0.066865 | -0.01695 | 0.06704 | 0.017061 | 0.00017443 | 0.00011105 | 0.10096 | 0.10096 | 0.10096 | 0.98622 | -0.26295 | 0.98903 | -0.20882 | 27.735
21 | 0.014519 | 0.0036392 | -0.014518 | -0.0036385 | 1.2421e-06 | 7.0585e-07 | 0.021845 | 0.021845 | 0.021845 | 0.98903 | -0.20882 | 0.98894 | -0.21061 | 6.0013
22 | -0.081559 | -0.0207 | 0.081673 | 0.020773 | 0.00011412 | 7.2779e-05 | 0.1228 | 0.1228 | 0.1228 | 0.98903 | -0.20882 | 0.99054 | -0.17977 | 33.7362
23 | 0.009775 | 0.00245 | -0.0097738 | -0.0024494 | 1.1655e-06 | 5.6163e-07 | 0.014708 | 0.014708 | 0.014708 | 0.98894 | -0.21061 | 0.98881 | -0.21312 | 4.0407
24 | 0.004743 | 0.0011886 | -0.0047426 | -0.0011886 | 4.2635e-07 | -1.3526e-08 | 0.0071365 | 0.0071366 | 0.0071366 | 0.98894 | -0.21061 | 0.98884 | -0.2125 | 1.9606
25 | -0.081673 | -0.020773 | 0.081704 | 0.020792 | 3.0995e-05 | 1.9766e-05 | 0.1228 | 0.1228 | 0.1228 | 0.99054 | -0.17977 | 0.99095 | -0.1719 | 33.7362
26 | 0.0048632 | 0.0012187 | -0.0048626 | -0.0012187 | 6.1867e-07 | 8.9054e-10 | 0.0073184 | 0.0073185 | 0.0073185 | 0.98881 | -0.21312 | 0.98867 | -0.21579 | 2.0106
27 | -0.17915 | -0.045296 | 0.17939 | 0.045449 | 0.00024149 | 0.00015278 | 0.27144 | 0.27144 | 0.27144 | 0.98262 | -0.33266 | 0.98407 | -0.3046 | 18.6426
28 | 0.16346 | 0.041361 | -0.16324 | -0.04122 | 0.0002236 | 0.00014114 | 0.24768 | 0.24768 | 0.24768 | 0.98262 | -0.33266 | 0.98115 | -0.36121 | 17.0112
29 | 0.015686 | 0.0039349 | -0.015676 | -0.003929 | 1.028e-05 | 5.9642e-06 | 0.023755 | 0.023755 | 0.023755 | 0.98262 | -0.33266 | 0.98192 | -0.34642 | 6.5262
30 | 0.019583 | 0.0049161 | -0.01957 | -0.0049086 | 1.2431e-05 | 7.4759e-06 | 0.029614 | 0.029614 | 0.029614 | 0.98407 | -0.3046 | 0.98338 | -0.31792 | 8.1357
31 | 0.018257 | 0.004583 | -0.018242 | -0.0045745 | 1.4295e-05 | 8.5137e-06 | 0.027609 | 0.027609 | 0.027609 | 0.98407 | -0.3046 | 0.98322 | -0.32103 | 7.5849
32 | -0.21723 | -0.054948 | 0.21747 | 0.055099 | 0.00023715 | 0.00015058 | 0.32866 | 0.32866 | 0.32866 | 0.98407 | -0.3046 | 0.98524 | -0.28187 | 22.5727
33 | 0.16324 | 0.04122 | -0.16304 | -0.041093 | 0.00020178 | 0.00012737 | 0.24768 | 0.24768 | 0.24768 | 0.98115 | -0.36121 | 0.97983 | -0.38704 | 17.0112
34 | 0.011235 | 0.002816 | -0.011232 | -0.0028146 | 2.6218e-06 | 1.3729e-06 | 0.017026 | 0.017026 | 0.017026 | 0.98192 | -0.34642 | 0.98167 | -0.35132 | 4.6774
35 | 0.067358 | 0.016996 | -0.06731 | -0.016966 | 4.7792e-05 | 3.0431e-05 | 0.10177 | 0.10177 | 0.10177 | 0.98524 | -0.28187 | 0.98448 | -0.2967 | 27.9594
36 | -0.28483 | -0.072095 | 0.28524 | 0.07236 | 0.00041607 | 0.00026507 | 0.43043 | 0.43043 | 0.43043 | 0.98524 | -0.28187 | 0.98681 | -0.25149 | 29.5625
37 | 0.04663 | 0.011777 | -0.046571 | -0.01174 | 5.9077e-05 | 3.7407e-05 | 0.070513 | 0.070514 | 0.070514 | 0.98448 | -0.2967 | 0.98311 | -0.32318 | 19.3719
38 | 0.02068 | 0.0051884 | -0.020669 | -0.0051819 | 1.0772e-05 | 6.5207e-06 | 0.031259 | 0.031259 | 0.031259 | 0.98448 | -0.2967 | 0.98392 | -0.30763 | 8.5876
39 | -0.29735 | -0.075395 | 0.29849 | 0.076123 | 0.0011423 | 0.00072798 | 0.44869 | 0.44869 | 0.44869 | 0.98681 | -0.25149 | 0.99095 | -0.1719 | 30.8165
40 | 0.015907 | 0.0039906 | -0.015901 | -0.0039867 | 6.7888e-06 | 3.9487e-06 | 0.024072 | 0.024072 | 0.024072 | 0.98338 | -0.31792 | 0.98293 | -0.32687 | 6.6131
41 | 0.015076 | 0.0037808 | -0.01507 | -0.0037777 | 5.3207e-06 | 3.0597e-06 | 0.022816 | 0.022816 | 0.022816 | 0.98322 | -0.32103 | 0.98285 | -0.32844 | 6.2682
42 | 0.0072411 | 0.0018148 | -0.0072407 | -0.0018147 | 4.2389e-07 | 1.5254e-07 | 0.010973 | 0.010973 | 0.010973 | 0.98195 | -0.3459 | 0.98188 | -0.34712 | 3.0146
43 | -0.036383 | -0.009171 | 0.036422 | 0.009196 | 3.96e-05 | 2.4904e-05 | 0.055152 | 0.055152 | 0.055152 | 0.98195 | -0.3459 | 0.98311 | -0.32318 | 15.1517
44 | -0.3802 | -0.096915 | 0.38094 | 0.097387 | 0.00073853 | 0.00047141 | 0.57149 | 0.57149 | 0.57149 | 0.99095 | -0.1719 | 0.99305 | -0.13174 | 39.2505
45 | 0.010149 | 0.002544 | -0.010147 | -0.0025432 | 1.6333e-06 | 8.1133e-07 | 0.015361 | 0.015362 | 0.015362 | 0.98311 | -0.32318 | 0.98294 | -0.32655 | 4.2202
46 | 0.01402 | 0.0035156 | -0.014015 | -0.0035125 | 5.4729e-06 | 3.0905e-06 | 0.021204 | 0.021204 | 0.021204 | 0.98392 | -0.30763 | 0.9835 | -0.31583 | 5.8253
47 | -0.39879 | -0.10186 | 0.39944 | 0.10228 | 0.00065039 | 0.00041524 | 0.59824 | 0.59824 | 0.59824 | 0.99305 | -0.13174 | 0.99482 | -0.098066 | 41.0878
48 | 0.15856 | 0.03997 | -0.1585 | -0.039929 | 6.5506e-05 | 4.1317e-05 | 0.24088 | 0.24088 | 0.24088 | 0.97983 | -0.38704 | 0.97938 | -0.39568 | 16.5441
49 | 0.007076 | 0.001773 | -0.0070748 | -0.0017726 | 1.1924e-06 | 4.1377e-07 | 0.010726 | 0.010726 | 0.010726 | 0.98167 | -0.35132 | 0.98148 | -0.35486 | 2.9466
50 | 0.012604 | 0.0031604 | -0.012599 | -0.0031578 | 4.7059e-06 | 2.5751e-06 | 0.019081 | 0.019081 | 0.019081 | 0.98293 | -0.32687 | 0.98252 | -0.33471 | 5.242
51 | 0.012084 | 0.0030294 | -0.012081 | -0.0030275 | 3.5285e-06 | 1.9021e-06 | 0.018296 | 0.018296 | 0.018296 | 0.98285 | -0.32844 | 0.98253 | -0.33457 | 5.0264
52 | 0.0069568 | 0.0017436 | -0.0069554 | -0.0017432 | 1.3215e-06 | 4.422e-07 | 0.010526 | 0.010526 | 0.010526 | 0.9835 | -0.31583 | 0.98329 | -0.31981 | 2.8917
53 | 0.108 | 0.027265 | -0.10783 | -0.027155 | 0.00017229 | 0.00011004 | 0.16161 | 0.16161 | 0.16161 | 0.99482 | -0.098066 | 0.99309 | -0.13142 | 44.3987
54 | -0.50744 | -0.12954 | 0.50831 | 0.1301 | 0.00086714 | 0.00055413 | 0.75985 | 0.75985 | 0.75985 | 0.99482 | -0.098066 | 0.99668 | -0.062769 | 52.1874
55 | -0.025094 | -0.0062891 | 0.025103 | 0.0062944 | 8.5801e-06 | 5.2861e-06 | 0.037798 | 0.037797 | 0.037798 | 0.9879 | -0.23193 | 0.98827 | -0.22476 | 10.3839
56 | -0.040029 | -0.010035 | 0.040051 | 0.010049 | 2.1974e-05 | 1.3856e-05 | 0.060272 | 0.060272 | 0.060272 | 0.98827 | -0.22476 | 0.98886 | -0.21324 | 16.5582
57 | -0.056805 | -0.014248 | 0.056859 | 0.014282 | 5.329e-05 | 3.3856e-05 | 0.085483 | 0.085483 | 0.085483 | 0.98886 | -0.21324 | 0.98988 | -0.19358 | 23.4844
58 | -0.072588 | -0.018224 | 0.072665 | 0.018273 | 7.6743e-05 | 4.8894e-05 | 0.10913 | 0.10913 | 0.10913 | 0.98988 | -0.19358 | 0.99102 | -0.17145 | 29.9802
59 | -0.094484 | -0.023772 | 0.094506 | 0.023785 | 2.1978e-05 | 1.3498e-05 | 0.14385 | 0.14385 | 0.14385 | 0.97757 | -0.43126 | 0.97782 | -0.4264 | 9.8801
60 | 0.091293 | 0.022972 | -0.091248 | -0.022944 | 4.5311e-05 | 2.7745e-05 | 0.139 | 0.139 | 0.139 | 0.97757 | -0.43126 | 0.97704 | -0.44165 | 9.5465
61 | -0.13999 | -0.035211 | 0.14003 | 0.035241 | 4.8259e-05 | 3.0317e-05 | 0.21307 | 0.21307 | 0.21307 | 0.97782 | -0.4264 | 0.97818 | -0.41918 | 14.6341
62 | 0.045479 | 0.011426 | -0.045463 | -0.011415 | 1.6303e-05 | 1.032e-05 | 0.069219 | 0.069219 | 0.069219 | 0.97782 | -0.4264 | 0.97743 | -0.43391 | 19.0161
63 | 0.048704 | 0.012244 | -0.048695 | -0.012239 | 9.6706e-06 | 5.2506e-06 | 0.07419 | 0.07419 | 0.07419 | 0.97704 | -0.44165 | 0.97683 | -0.44581 | 5.0955
64 | 0.0038023 | 0.00095194 | -0.0038006 | -0.00095253 | 1.6604e-06 | -5.902e-07 | 0.0057905 | 0.0057911 | 0.0057911 | 0.97704 | -0.44165 | 0.97657 | -0.45083 | 1.591
65 | 0.038741 | 0.009748 | -0.038677 | -0.0097074 | 6.435e-05 | 4.0568e-05 | 0.059016 | 0.059017 | 0.059017 | 0.97704 | -0.44165 | 0.97527 | -0.47648 | 16.2134
66 | -0.14323 | -0.036042 | 0.14339 | 0.036143 | 0.00016105 | 0.00010125 | 0.21793 | 0.21793 | 0.21793 | 0.97818 | -0.41918 | 0.97938 | -0.39568 | 14.9678
67 | 0.039945 | 0.010033 | -0.039911 | -0.010011 | 3.4065e-05 | 2.1494e-05 | 0.060819 | 0.060819 | 0.060819 | 0.97743 | -0.43391 | 0.97652 | -0.4518 | 16.7085
68 | 0.045868 | 0.011531 | -0.045866 | -0.01153 | 1.4983e-06 | 7.9503e-07 | 0.069884 | 0.069884 | 0.069884 | 0.97683 | -0.44581 | 0.97679 | -0.4465 | 4.7997
69 | 0.012813 | 0.0032121 | -0.012809 | -0.0032103 | 3.3825e-06 | 1.8704e-06 | 0.019549 | 0.019549 | 0.019549 | 0.97527 | -0.47648 | 0.97498 | -0.48202 | 5.3707
70 | 0.025864 | 0.0064953 | -0.025843 | -0.006482 | 2.1577e-05 | 1.3349e-05 | 0.039467 | 0.039468 | 0.039468 | 0.97527 | -0.47648 | 0.97438 | -0.49398 | 10.8428
71 | 0.036664 | 0.0091971 | -0.036662 | -0.009196 | 1.8114e-06 | 1.1399e-06 | 0.055871 | 0.055871 | 0.055871 | 0.97652 | -0.4518 | 0.97647 | -0.45283 | 15.349
72 | 0.043846 | 0.011023 | -0.04384 | -0.01102 | 5.7865e-06 | 3.011e-06 | 0.066806 | 0.066806 | 0.066806 | 0.97679 | -0.4465 | 0.97665 | -0.44926 | 4.5883
73 | 0.04384 | 0.01102 | -0.043837 | -0.011019 | 3.2787e-06 | 1.7062e-06 | 0.066806 | 0.066806 | 0.066806 | 0.97665 | -0.44926 | 0.97657 | -0.45083 | 4.5883
74 | 0.040447 | 0.01017 | -0.040416 | -0.010154 | 3.0674e-05 | 1.5326e-05 | 0.061642 | 0.061643 | 0.061643 | 0.97657 | -0.45083 | 0.97576 | -0.46672 | 4.2337
75 | 0.0033896 | 0.00084913 | -0.0033891 | -0.00084939 | 4.3629e-07 | -2.6642e-07 | 0.0051646 | 0.0051648 | 0.0051648 | 0.97657 | -0.45083 | 0.97643 | -0.45353 | 1.4189
76 | 0.025843 | 0.006482 | -0.025829 | -0.0064735 | 1.372e-05 | 8.4882e-06 | 0.039468 | 0.039468 | 0.039468 | 0.97438 | -0.49398 | 0.97381 | -0.50512 | 10.8428
77 | 0.013058 | 0.0032728 | -0.013058 | -0.0032727 | 2.5096e-07 | 1.3971e-07 | 0.019954 | 0.019954 | 0.019954 | 0.97381 | -0.50512 | 0.97379 | -0.50553 | 5.4818
78 | 0.029608 | 0.007428 | -0.029602 | -0.0074246 | 5.413e-06 | 3.3757e-06 | 0.045121 | 0.045121 | 0.045121 | 0.97647 | -0.45283 | 0.97628 | -0.45667 | 12.3958
79 | 0.010574 | 0.0026508 | -0.010572 | -0.0026495 | 2.4045e-06 | 1.231e-06 | 0.016126 | 0.016126 | 0.016126 | 0.97576 | -0.46672 | 0.97552 | -0.47149 | 4.4302
80 | 0.029842 | 0.0075035 | -0.029823 | -0.0074915 | 1.9346e-05 | 1.2071e-05 | 0.045518 | 0.045518 | 0.045518 | 0.97576 | -0.46672 | 0.97507 | -0.4803 | 12.5048
81 | -0.50831 | -0.1301 | 0.50961 | 0.13093 | 0.0013084 | 0.00083614 | 0.75985 | 0.75985 | 0.75985 | 0.99668 | -0.062769 | 0.99948 | -0.0097561 | 52.1874
82 | -0.52478 | -0.13473 | 0.52503 | 0.13489 | 0.00024865 | 0.00015891 | 0.78243 | 0.78243 | 0.78243 | 0.99948 | -0.0097561 | 1 | 0 | 53.7383
83 | 0.09192 | 0.023168 | -0.091744 | -0.023056 | 0.00017565 | 0.0001121 | 0.13778 | 0.13778 | 0.13778 | 0.99309 | -0.13142 | 0.99102 | -0.17145 | 37.8508
84 | 0.01908 | 0.0047831 | -0.019078 | -0.0047818 | 2.056e-06 | 1.2298e-06 | 0.028649 | 0.028649 | 0.028649 | 0.99102 | -0.17145 | 0.9909 | -0.17371 | 7.8706
85 | 0.0031371 | 0.00078569 | -0.0031368 | -0.00078587 | 2.1641e-07 | -1.8392e-07 | 0.0047559 | 0.004756 | 0.004756 | 0.98148 | -0.35486 | 0.98141 | -0.35631 | 1.3066
86 | 0.0011259 | 0.00028188 | -0.0011259 | -0.00028217 | 2.6568e-08 | -2.9021e-07 | 0.001707 | 0.0017071 | 0.0017071 | 0.98141 | -0.35631 | 0.98139 | -0.3568 | 0.46899
87 | 0.0064224 | 0.0016093 | -0.0064213 | -0.001609 | 1.0544e-06 | 2.9889e-07 | 0.0097291 | 0.0097292 | 0.0097292 | 0.98227 | -0.33977 | 0.98209 | -0.34322 | 2.6729
88 | -0.0092423 | -0.0023161 | 0.0092446 | 0.0023171 | 2.2289e-06 | 1.0426e-06 | 0.014001 | 0.014001 | 0.014001 | 0.98227 | -0.33977 | 0.98252 | -0.33471 | 3.8464
89 | 0.0046171 | 0.0011569 | -0.004617 | -0.0011569 | 1.5083e-07 | -7.462e-09 | 0.0069956 | 0.0069956 | 0.0069956 | 0.98209 | -0.34322 | 0.98205 | -0.3439 | 1.9219
90 | 0.0028149 | 0.00070524 | -0.0028148 | -0.00070545 | 1.7148e-07 | -2.0827e-07 | 0.0042651 | 0.0042652 | 0.0042652 | 0.98205 | -0.3439 | 0.98199 | -0.34518 | 1.1718
91 | 0.0032278 | 0.00080888 | -0.0032277 | -0.00080893 | 7.898e-08 | -5.7691e-08 | 0.0049261 | 0.0049261 | 0.0049261 | 0.975 | -0.48178 | 0.97497 | -0.4823 | 1.3533
92 | -0.0041973 | -0.0010519 | 0.0041976 | 0.0010518 | 2.9587e-07 | -5.046e-08 | 0.0064058 | 0.0064057 | 0.0064058 | 0.975 | -0.48178 | 0.97507 | -0.4803 | 1.7598
93 | 0.022412 | 0.0056348 | -0.022377 | -0.0056133 | 3.5167e-05 | 2.1509e-05 | 0.034208 | 0.034209 | 0.034209 | 0.97507 | -0.4803 | 0.9734 | -0.51321 | 9.398
94 | 0.0032133 | 0.00080487 | -0.0032132 | -0.00080497 | 1.3585e-07 | -1.0097e-07 | 0.0049035 | 0.0049036 | 0.0049036 | 0.97507 | -0.4803 | 0.97503 | -0.48119 | 1.3471
95 | 0.01566 | 0.00393 | -0.015646 | -0.0039218 | 1.4206e-05 | 8.271e-06 | 0.023941 | 0.023941 | 0.023941 | 0.9734 | -0.51321 | 0.97244 | -0.53225 | 6.5772
96 | 0.0067171 | 0.0016832 | -0.0067167 | -0.0016831 | 4.3211e-07 | 1.4071e-07 | 0.010268 | 0.010268 | 0.010268 | 0.9734 | -0.51321 | 0.97333 | -0.51457 | 2.8209
97 | 0.0032132 | 0.00080497 | -0.0032128 | -0.00080521 | 3.2908e-07 | -2.4451e-07 | 0.0049036 | 0.0049038 | 0.0049038 | 0.97503 | -0.48119 | 0.97492 | -0.48334 | 1.3472
98 | 0.0077921 | 0.0019529 | -0.0077916 | -0.0019527 | 4.9147e-07 | 1.9873e-07 | 0.011886 | 0.011886 | 0.011886 | 0.97552 | -0.47149 | 0.97545 | -0.47282 | 3.2653
99 | 0.0058846 | 0.0014745 | -0.0058839 | -0.0014743 | 7.077e-07 | 1.6421e-07 | 0.0090045 | 0.0090046 | 0.0090046 | 0.97244 | -0.53225 | 0.97231 | -0.53478 | 2.4738
100 | 0.0097609 | 0.0024473 | -0.0097577 | -0.0024457 | 3.2117e-06 | 1.5794e-06 | 0.014936 | 0.014937 | 0.014937 | 0.97244 | -0.53225 | 0.97209 | -0.53916 | 4.1035
101 | 0.0046575 | 0.001167 | -0.0046573 | -0.001167 | 1.2692e-07 | -1.7436e-09 | 0.0071202 | 0.0071202 | 0.0071202 | 0.97333 | -0.51457 | 0.9733 | -0.51514 | 1.9561
102 | 0.0097577 | 0.0024457 | -0.0097547 | -0.0024443 | 2.9476e-06 | 1.4498e-06 | 0.014937 | 0.014937 | 0.014937 | 0.97209 | -0.53916 | 0.97177 | -0.5455 | 4.1035
103 | 0.0066026 | 0.0016543 | -0.0066016 | -0.0016539 | 1.0209e-06 | 3.2345e-07 | 0.01011 | 0.01011 | 0.01011 | 0.97177 | -0.5455 | 0.9716 | -0.54875 | 2.7775
104 | 0.0024738 | 0.00061966 | -0.0024737 | -0.00061986 | 1.2068e-07 | -2.0124e-07 | 0.0037857 | 0.0037858 | 0.0037858 | 0.97231 | -0.53478 | 0.97226 | -0.5358 | 1.0401
105 | -0.0049869 | -0.0012498 | 0.0049875 | 0.0012499 | 5.7111e-07 | 3.7121e-08 | 0.0076083 | 0.0076082 | 0.0076083 | 0.97533 | -0.47522 | 0.97545 | -0.47282 | 2.0902
106 | 0.0021538 | 0.00053957 | -0.0021537 | -0.00053977 | 8.1925e-08 | -1.9798e-07 | 0.0032927 | 0.0032928 | 0.0032928 | 0.9733 | -0.51514 | 0.97326 | -0.51594 | 0.90461
107 | 0.0055147 | 0.0013815 | -0.0055129 | -0.0013812 | 1.7693e-06 | 3.1345e-07 | 0.0084456 | 0.0084459 | 0.0084459 | 0.9716 | -0.54875 | 0.97126 | -0.55549 | 2.3203
108 | 0.0055129 | 0.0013812 | -0.0055121 | -0.0013811 | 8.2545e-07 | 1.4645e-07 | 0.0084459 | 0.008446 | 0.008446 | 0.97126 | -0.55549 | 0.9711 | -0.55863 | 2.3203
109 | 0.0027004 | 0.00067639 | -0.0027002 | -0.00067665 | 2.0367e-07 | -2.6209e-07 | 0.0041377 | 0.0041378 | 0.0041378 | 0.9711 | -0.55863 | 0.97102 | -0.56022 | 1.1368
110 | 0.0027002 | 0.00067665 | -0.0027001 | -0.00067672 | 5.2387e-08 | -6.7399e-08 | 0.0041378 | 0.0041378 | 0.0041378 | 0.97102 | -0.56022 | 0.971 | -0.56062 | 1.1368
111 | 0.0012369 | 0.00030989 | -0.0012369 | -0.00030999 | 1.1577e-08 | -9.9434e-08 | 0.001893 | 0.001893 | 0.001893 | 0.97226 | -0.5358 | 0.97225 | -0.536 | 0.52005
112 | -0.01222 | -0.0030625 | 0.012221 | 0.0030634 | 1.6033e-06 | 8.626e-07 | 0.018353 | 0.018353 | 0.018353 | 0.99076 | -0.17646 | 0.9909 | -0.17371 | 5.0419
113 | -0.023341 | -0.005851 | 0.023342 | 0.0058515 | 7.7663e-07 | 4.7663e-07 | 0.035594 | 0.035594 | 0.035594 | 0.97579 | -0.46633 | 0.97582 | -0.46563 | 9.7786
114 | 0.016546 | 0.0041479 | -0.016544 | -0.0041469 | 1.6971e-06 | 9.9734e-07 | 0.025231 | 0.025231 | 0.025231 | 0.97579 | -0.46633 | 0.97568 | -0.46848 | 6.9317
115 | -0.026343 | -0.0066038 | 0.026355 | 0.0066107 | 1.1248e-05 | 6.9664e-06 | 0.040171 | 0.040171 | 0.040171 | 0.97582 | -0.46563 | 0.97628 | -0.45667 | 11.036
116 | 0.013542 | 0.0033947 | -0.013539 | -0.0033929 | 3.2051e-06 | 1.8011e-06 | 0.020654 | 0.020654 | 0.020654 | 0.97568 | -0.46848 | 0.97542 | -0.47345 | 5.6741
117 | 0.0071866 | 0.0018008 | -0.0071865 | -0.0018007 | 1.0504e-07 | 3.8134e-08 | 0.010963 | 0.010963 | 0.010963 | 0.97542 | -0.47345 | 0.97541 | -0.47375 | 3.0118
118 | 0.0018298 | 0.00045822 | -0.0018297 | -0.00045856 | 9.234e-08 | -3.3537e-07 | 0.0027912 | 0.0027914 | 0.0027914 | 0.97541 | -0.47375 | 0.97535 | -0.47481 | 0.76686
119 | 0.0059541 | 0.001492 | -0.0059531 | -0.0014918 | 9.3866e-07 | 2.1093e-07 | 0.0090172 | 0.0090173 | 0.0090173 | 0.98253 | -0.33457 | 0.98236 | -0.33788 | 2.4773
120 | 0.0030101 | 0.00075417 | -0.0030099 | -0.00075436 | 1.8784e-07 | -1.8482e-07 | 0.0045594 | 0.0045595 | 0.0045595 | 0.98236 | -0.33788 | 0.9823 | -0.33919 | 1.2526

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54145 | 0.13859

## res_load
| p_mw | q_mvar
0 | 0.012632 | 0.0031659
1 | 0.0045985 | 0.0011525
2 | 0.0082104 | 0.0020577
3 | 0.0019318 | 0.00048414
4 | 0.031127 | 0.0078011
5 | 0.0021779 | 0.00054584
6 | 0.0098117 | 0.0024591
7 | 0.0073856 | 0.001851
8 | 0.0040369 | 0.0010117
9 | 0.0078885 | 0.001977
10 | 0.0049106 | 0.0012307
11 | 0.0047426 | 0.0011886
12 | 0.0044408 | 0.001113
13 | 0.012108 | 0.0030346
14 | 0.0036628 | 0.00091797
15 | 0.0031669 | 0.00079371
16 | 0.0016225 | 0.00040663
17 | 0.0066487 | 0.0016663
18 | 0.0072407 | 0.0018147
19 | 0.017853 | 0.0044745
20 | 0.010147 | 0.0025432
21 | 0.0039284 | 0.00098454
22 | 0.0048626 | 0.0012187
23 | 0.0044787 | 0.0011225
24 | 0.0041562 | 0.0010416
25 | 0.0032969 | 0.00082628
26 | 0.0029858 | 0.00074831
27 | 0.0070579 | 0.0017689
28 | 0.025094 | 0.0062891
29 | 0.014926 | 0.0037409
30 | 0.016754 | 0.004199
31 | 0.015729 | 0.0039421
32 | 0.0031912 | 0.00079978
33 | 0.0031939 | 0.00080048
34 | 0.0055176 | 0.0013828
35 | 0.0028267 | 0.00070845
36 | 0.0038006 | 0.00095253
37 | 0.015107 | 0.0037861
38 | 0.0032475 | 0.00081391
39 | 0.0020207 | 0.00050643
40 | 0.012771 | 0.0032006
41 | 0.012809 | 0.0032103
42 | 0.0070542 | 0.0017679
43 | 0.0033891 | 0.00084939
44 | 0.013058 | 0.0032727
45 | 0.015168 | 0.0038015
46 | 0.015907 | 0.0039867
47 | 0.014765 | 0.0037005
48 | 0.0069554 | 0.0017432
49 | 0.0039377 | 0.00098689
50 | 0.0020109 | 0.00050399
51 | 0.0011259 | 0.00028217
52 | 0.0028199 | 0.00070675
53 | 0.0018042 | 0.00045218
54 | 0.0033544 | 0.00084069
55 | 0.0018021 | 0.00045164
56 | 0.0028148 | 0.00070545
57 | 0.00096953 | 0.00024299
58 | 0.0032277 | 0.00080893
59 | 0.0027798 | 0.00069668
60 | 0.0020592 | 0.00051608
61 | 0.0031521 | 0.00078999
62 | 0.0034101 | 0.00085466
63 | 0.0032128 | 0.00080521
64 | 0.0049869 | 0.0012498
65 | 0.0028041 | 0.00070278
66 | 0.0025036 | 0.00062745
67 | 0.0010869 | 0.00027241
68 | 0.0028117 | 0.00070468
69 | 0.0027001 | 0.00067672
70 | 0.0012368 | 0.00030997
71 | 0.01222 | 0.0030625
72 | 0.0068566 | 0.0017184
73 | 0.0067954 | 0.0017031
74 | 0.0030016 | 0.00075228
75 | 0.0030016 | 0.00075228
76 | 0.0032476 | 0.00081391
77 | 0.0063525 | 0.0015921
78 | 0.0053567 | 0.0013425
79 | 0.0018297 | 0.00045856
80 | 0.0061268 | 0.0015355
81 | 0.002943 | 0.00073759
82 | 0.0030099 | 0.00075436
83 | 0.0012369 | 0.00030999
84 | 0.0021537 | 0.00053977

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1