## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1058-19_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1058-19_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1058-19_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1058-19_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1058-19_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1058-19_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1058-19_0_4_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1058-19_0_4_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1058-19_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1058-19_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_1058-19_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1058-19_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1058-19_0_4_node_95 | 0.4 | n |  | TRUE
13 | bus_LV_1058-19_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1058-19_0_4_node_87 | 0.4 | n |  | TRUE
15 | bus_LV_1058-19_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1058-19_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1058-19_0_4_node_110 | 0.4 | n |  | TRUE
18 | bus_LV_1058-19_0_4_node_111 | 0.4 | n |  | TRUE
19 | bus_LV_1058-19_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1058-19_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1058-19_0_4_node_97 | 0.4 | n |  | TRUE
22 | bus_LV_1058-19_0_4_node_103 | 0.4 | n |  | TRUE
23 | bus_LV_1058-19_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1058-19_0_4_node_106 | 0.4 | n |  | TRUE
25 | bus_LV_1058-19_0_4_node_100 | 0.4 | n |  | TRUE
26 | bus_LV_1058-19_0_4_node_105 | 0.4 | n |  | TRUE
27 | bus_LV_1058-19_0_4_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1058-19_0_4_node_62 | 0.4 | n |  | TRUE
29 | bus_LV_1058-19_0_4_node_88 | 0.4 | n |  | TRUE
30 | bus_LV_1058-19_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1058-19_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1058-19_0_4_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_1058-19_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1058-19_0_4_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_1058-19_0_4_node_78 | 0.4 | n |  | TRUE
36 | bus_LV_1058-19_0_4_node_82 | 0.4 | n |  | TRUE
37 | bus_LV_1058-19_0_4_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_1058-19_0_4_node_50 | 0.4 | n |  | TRUE
39 | bus_LV_1058-19_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_1058-19_0_4_node_85 | 0.4 | n |  | TRUE
41 | bus_LV_1058-19_0_4_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_1058-19_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1058-19_0_4_node_77 | 0.4 | n |  | TRUE
44 | bus_LV_1058-19_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1058-19_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1058-19_0_4_node_96 | 0.4 | n |  | TRUE
47 | bus_LV_1058-19_0_4_node_13 | 0.4 | n |  | TRUE
48 | bus_LV_1058-19_0_4_node_14 | 0.4 | n |  | TRUE
49 | bus_LV_1058-19_0_4_node_113 | 0.4 | n |  | TRUE
50 | bus_LV_1058-19_0_4_node_84 | 0.4 | n |  | TRUE
51 | bus_LV_1058-19_0_4_node_102 | 0.4 | n |  | TRUE
52 | bus_LV_1058-19_0_4_node_93 | 0.4 | n |  | TRUE
53 | bus_LV_1058-19_0_4_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_1058-19_0_4_node_58 | 0.4 | n |  | TRUE
55 | bus_LV_1058-19_0_4_node_73 | 0.4 | n |  | TRUE
56 | bus_LV_1058-19_0_4_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_1058-19_0_4_node_83 | 0.4 | n |  | TRUE
58 | bus_LV_1058-19_0_4_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_1058-19_0_4_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_1058-19_0_4_node_94 | 0.4 | n |  | TRUE
61 | bus_LV_1058-19_0_4_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_1058-19_0_4_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_1058-19_0_4_node_99 | 0.4 | n |  | TRUE
64 | bus_LV_1058-19_0_4_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_1058-19_0_4_node_89 | 0.4 | n |  | TRUE
66 | bus_LV_1058-19_0_4_node_76 | 0.4 | n |  | TRUE
67 | bus_LV_1058-19_0_4_node_101 | 0.4 | n |  | TRUE
68 | bus_LV_1058-19_0_4_node_104 | 0.4 | n |  | TRUE
69 | bus_LV_1058-19_0_4_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_1058-19_0_4_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_1058-19_0_4_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_1058-19_0_4_node_32 | 0.4 | n |  | TRUE
73 | bus_LV_1058-19_0_4_node_33 | 0.4 | n |  | TRUE
74 | bus_LV_1058-19_0_4_node_34 | 0.4 | n |  | TRUE
75 | bus_LV_1058-19_0_4_node_35 | 0.4 | n |  | TRUE
76 | bus_LV_1058-19_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_1058-19_0_4_node_47 | 0.4 | n |  | TRUE
78 | bus_LV_1058-19_0_4_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_1058-19_0_4_node_46 | 0.4 | n |  | TRUE
80 | bus_LV_1058-19_0_4_node_36 | 0.4 | n |  | TRUE
81 | bus_LV_1058-19_0_4_node_37 | 0.4 | n |  | TRUE
82 | bus_LV_1058-19_0_4_node_38 | 0.4 | n |  | TRUE
83 | bus_LV_1058-19_0_4_node_39 | 0.4 | n |  | TRUE
84 | bus_LV_1058-19_0_4_node_40 | 0.4 | n |  | TRUE
85 | bus_LV_1058-19_0_4_node_42 | 0.4 | n |  | TRUE
86 | bus_LV_1058-19_0_4_node_92 | 0.4 | n |  | TRUE
87 | bus_LV_1058-19_0_4_node_41 | 0.4 | n |  | TRUE
88 | bus_LV_1058-19_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1058-19_0_4_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_1058-19_0_4_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_1058-19_0_4_node_107 | 0.4 | n |  | TRUE
92 | bus_LV_1058-19_0_4_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_1058-19_0_4_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_1058-19_0_4_node_48 | 0.4 | n |  | TRUE
95 | bus_LV_1058-19_0_4_node_49 | 0.4 | n |  | TRUE
96 | bus_LV_1058-19_0_4_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_1058-19_0_4_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1058-19_0_4_node_52 | 0.4 | n |  | TRUE
99 | bus_LV_1058-19_0_4_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_1058-19_0_4_node_67 | 0.4 | n |  | TRUE
101 | bus_LV_1058-19_0_4_node_68 | 0.4 | n |  | TRUE
102 | bus_LV_1058-19_0_4_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_1058-19_0_4_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_1058-19_0_4_node_108 | 0.4 | n |  | TRUE
105 | bus_LV_1058-19_0_4_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_1058-19_0_4_node_90 | 0.4 | n |  | TRUE
107 | bus_LV_1058-19_0_4_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_1058-19_0_4_node_109 | 0.4 | n |  | TRUE
109 | bus_MV_23_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1058-19_0_4_load_0 | 0 | 0.0045285 | 0.0011349 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1058-19_0_4_load_1 | 1 | 0.0030167 | 0.00075606 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1058-19_0_4_load_3 | 3 | 0.0039284 | 0.00098455 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1058-19_0_4_load_4 | 4 | 0.00040161 | 0.00010065 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1058-19_0_4_load_5 | 5 | 0.0015973 | 0.00040032 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1058-19_0_4_load_6 | 10 | 0.00053495 | 0.00013407 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1058-19_0_4_load_7 | 11 | 0.0010597 | 0.00026559 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1058-19_0_4_load_95 | 12 | 0.0023364 | 0.00058556 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1058-19_0_4_load_8 | 13 | 0.0012283 | 0.00030784 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1058-19_0_4_load_87 | 14 | 0.0017469 | 0.00043782 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1058-19_0_4_load_15 | 15 | 0.0027837 | 0.00069767 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1058-19_0_4_load_110 | 17 | 0.057615 | 0.01444 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1058-19_0_4_load_97 | 21 | 0.018284 | 0.0045823 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1058-19_0_4_load_106 | 24 | 0.018686 | 0.0046833 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1058-19_0_4_load_105 | 26 | 0.022442 | 0.0056245 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1058-19_0_4_load_88 | 29 | 0.0088107 | 0.0022082 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1058-19_0_4_load_98 | 32 | 0.0072276 | 0.0018114 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1058-19_0_4_load_78 | 35 | 0.0029277 | 0.00073376 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1058-19_0_4_load_82 | 36 | 0.0076229 | 0.0019105 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1058-19_0_4_load_53 | 37 | 0.001573 | 0.00039422 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1058-19_0_4_load_50 | 38 | 0.0013405 | 0.00033597 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1058-19_0_4_load_85 | 40 | 0.0039704 | 0.00099508 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1058-19_0_4_load_64 | 41 | 0.0037611 | 0.00094263 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1058-19_0_4_load_77 | 43 | 0.023309 | 0.0058419 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1058-19_0_4_load_43 | 44 | 0.032477 | 0.0081395 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1058-19_0_4_load_96 | 46 | 0.016812 | 0.0042136 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1058-19_0_4_load_13 | 47 | 0.00089132 | 0.00022339 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1058-19_0_4_load_14 | 48 | 0.0015031 | 0.00037672 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1058-19_0_4_load_113 | 49 | 0.0088529 | 0.0022187 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1058-19_0_4_load_102 | 51 | 0.018294 | 0.004585 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1058-19_0_4_load_93 | 52 | 0.0063365 | 0.0015881 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1058-19_0_4_load_73 | 55 | 0.0016869 | 0.00042277 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1058-19_0_4_load_83 | 57 | 0.010871 | 0.0027245 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1058-19_0_4_load_94 | 60 | 0.0050205 | 0.0012583 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1058-19_0_4_load_54 | 61 | 0.0082424 | 0.0020657 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1058-19_0_4_load_99 | 63 | 0.0039486 | 0.00098961 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1058-19_0_4_load_89 | 65 | 0.0050777 | 0.0012726 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1058-19_0_4_load_76 | 66 | 0.0028162 | 0.00070582 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1058-19_0_4_load_101 | 67 | 0.018685 | 0.004683 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1058-19_0_4_load_104 | 68 | 0.018285 | 0.0045827 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1058-19_0_4_load_44 | 69 | 0.020589 | 0.00516 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1058-19_0_4_load_60 | 70 | 0.0048515 | 0.0012159 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1058-19_0_4_load_51 | 71 | 0.0016399 | 0.00041101 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1058-19_0_4_load_32 | 72 | 0.002696 | 0.00067569 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1058-19_0_4_load_33 | 73 | 0.0046858 | 0.0011744 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1058-19_0_4_load_34 | 74 | 0.011979 | 0.0030023 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1058-19_0_4_load_69 | 76 | 0.0045088 | 0.00113 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1058-19_0_4_load_47 | 77 | 0.0032587 | 0.00081672 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1058-19_0_4_load_46 | 79 | 0.0022197 | 0.0005563 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1058-19_0_4_load_36 | 80 | 0.0031061 | 0.00077846 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1058-19_0_4_load_37 | 81 | 0.0053755 | 0.0013472 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1058-19_0_4_load_39 | 83 | 0.0026375 | 0.00066102 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1058-19_0_4_load_40 | 84 | 0.012089 | 0.0030297 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1058-19_0_4_load_92 | 86 | 0.0024185 | 0.00060613 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1058-19_0_4_load_70 | 89 | 0.013509 | 0.0033856 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1058-19_0_4_load_81 | 90 | 0.0020344 | 0.00050988 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1058-19_0_4_load_107 | 91 | 0.0046165 | 0.001157 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1058-19_0_4_load_66 | 92 | 0.017279 | 0.0043305 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1058-19_0_4_load_65 | 93 | 0.0062895 | 0.0015763 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1058-19_0_4_load_48 | 94 | 0.0042547 | 0.0010663 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1058-19_0_4_load_49 | 95 | 0.0059241 | 0.0014847 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1058-19_0_4_load_74 | 96 | 0.0065504 | 0.0016417 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1058-19_0_4_load_75 | 97 | 0.009503 | 0.0023817 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1058-19_0_4_load_52 | 98 | 0.0017558 | 0.00044005 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1058-19_0_4_load_112 | 99 | 0.0067553 | 0.001693 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1058-19_0_4_load_67 | 100 | 0.0030986 | 0.00077659 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1058-19_0_4_load_68 | 101 | 0.0045787 | 0.0011475 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1058-19_0_4_load_79 | 102 | 0.0015797 | 0.0003959 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1058-19_0_4_load_80 | 103 | 0.0039406 | 0.0009876 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1058-19_0_4_load_108 | 104 | 0.0033675 | 0.00084397 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1058-19_0_4_load_86 | 105 | 0.0011688 | 0.00029292 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1058-19_0_4_load_90 | 106 | 0.002274 | 0.00056992 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1058-19_0_4_load_91 | 107 | 0.0015733 | 0.00039431 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1058-19_0_4_load_109 | 108 | 0.0090071 | 0.0022574 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1058-19_0_4_line_0 |  | 0 | 1 | 0.025626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1058-19_0_4_line_1 |  | 0 | 2 | 0.0026979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1058-19_0_4_line_2 |  | 1 | 3 | 0.030957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1058-19_0_4_line_3 |  | 2 | 4 | 0.021331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1058-19_0_4_line_4 |  | 2 | 5 | 0.082633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1058-19_0_4_line_5 |  | 4 | 6 | 0.018636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1058-19_0_4_line_6 |  | 5 | 7 | 0.057326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1058-19_0_4_line_7 |  | 6 | 8 | 0.061141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1058-19_0_4_line_8 |  | 7 | 9 | 0.1401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1058-19_0_4_line_9 |  | 8 | 15 | 0.017525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1058-19_0_4_line_10 |  | 9 | 37 | 0.01333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1058-19_0_4_line_11 |  | 9 | 38 | 0.0092161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1058-19_0_4_line_12 |  | 10 | 11 | 0.35093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1058-19_0_4_line_13 |  | 10 | 12 | 0.32043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1058-19_0_4_line_14 |  | 11 | 13 | 0.020422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1058-19_0_4_line_15 |  | 12 | 14 | 0.00034683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1058-19_0_4_line_16 |  | 14 | 105 | 0.0039806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1058-19_0_4_line_17 |  | 15 | 47 | 0.025466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1058-19_0_4_line_18 |  | 16 | 17 | 0.014835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1058-19_0_4_line_19 |  | 16 | 18 | 0.020757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1058-19_0_4_line_20 |  | 16 | 19 | 0.035884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1058-19_0_4_line_21 |  | 18 | 49 | 0.018438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1058-19_0_4_line_22 |  | 18 | 50 | 0.027936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1058-19_0_4_line_23 |  | 19 | 44 | 0.012884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1058-19_0_4_line_24 |  | 19 | 42 | 0.013074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1058-19_0_4_line_25 |  | 20 | 21 | 0.016775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1058-19_0_4_line_26 |  | 20 | 22 | 0.025363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1058-19_0_4_line_27 |  | 21 | 45 | 0.029352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1058-19_0_4_line_28 |  | 22 | 51 | 0.022381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1058-19_0_4_line_29 |  | 23 | 24 | 0.01685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1058-19_0_4_line_30 |  | 23 | 25 | 0.046024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1058-19_0_4_line_31 |  | 23 | 26 | 0.041247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1058-19_0_4_line_32 |  | 25 | 67 | 0.044579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1058-19_0_4_line_33 |  | 25 | 63 | 0.0046894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1058-19_0_4_line_34 |  | 26 | 68 | 0.045673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1058-19_0_4_line_35 |  | 27 | 28 | 0.004021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1058-19_0_4_line_36 |  | 27 | 29 | 0.026675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1058-19_0_4_line_37 |  | 28 | 70 | 0.014088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1058-19_0_4_line_38 |  | 28 | 41 | 0.02645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1058-19_0_4_line_39 |  | 29 | 65 | 0.030818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1058-19_0_4_line_40 |  | 30 | 31 | 0.02813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1058-19_0_4_line_41 |  | 30 | 32 | 0.051242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1058-19_0_4_line_42 |  | 31 | 36 | 0.0036691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1058-19_0_4_line_43 |  | 31 | 33 | 0.018022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1058-19_0_4_line_44 |  | 32 | 63 | 0.10949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1058-19_0_4_line_45 |  | 33 | 34 | 0.004356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1058-19_0_4_line_46 |  | 33 | 35 | 0.04355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1058-19_0_4_line_47 |  | 34 | 64 | 0.004509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1058-19_0_4_line_48 |  | 38 | 71 | 0.030184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1058-19_0_4_line_49 |  | 39 | 40 | 0.015321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1058-19_0_4_line_50 |  | 39 | 41 | 0.021691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1058-19_0_4_line_51 |  | 40 | 52 | 0.012933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1058-19_0_4_line_52 |  | 42 | 43 | 0.063751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1058-19_0_4_line_53 |  | 43 | 66 | 0.030146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1058-19_0_4_line_54 |  | 44 | 69 | 0.019343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1058-19_0_4_line_55 |  | 45 | 46 | 0.056489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1058-19_0_4_line_56 |  | 47 | 48 | 0.022265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1058-19_0_4_line_57 |  | 50 | 99 | 0.019271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1058-19_0_4_line_58 |  | 50 | 56 | 0.038792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1058-19_0_4_line_59 |  | 51 | 67 | 0.037611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_1058-19_0_4_line_60 |  | 52 | 60 | 0.033259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_1058-19_0_4_line_61 |  | 53 | 54 | 0.010822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1058-19_0_4_line_62 |  | 53 | 55 | 0.011893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1058-19_0_4_line_63 |  | 54 | 59 | 0.006139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1058-19_0_4_line_64 |  | 54 | 60 | 0.066634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1058-19_0_4_line_65 |  | 55 | 62 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1058-19_0_4_line_66 |  | 56 | 57 | 0.016677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1058-19_0_4_line_67 |  | 56 | 58 | 0.019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1058-19_0_4_line_68 |  | 58 | 62 | 0.023312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1058-19_0_4_line_69 |  | 58 | 61 | 0.0091831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1058-19_0_4_line_70 |  | 59 | 91 | 0.060755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1058-19_0_4_line_71 |  | 62 | 89 | 0.036727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1058-19_0_4_line_72 |  | 64 | 65 | 0.016311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_1058-19_0_4_line_73 |  | 66 | 98 | 0.028863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1058-19_0_4_line_74 |  | 69 | 78 | 0.014172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1058-19_0_4_line_75 |  | 71 | 98 | 0.028749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1058-19_0_4_line_76 |  | 72 | 73 | 0.025729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1058-19_0_4_line_77 |  | 72 | 74 | 0.0069809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1058-19_0_4_line_78 |  | 73 | 75 | 0.017212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1058-19_0_4_line_79 |  | 75 | 76 | 0.023241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1058-19_0_4_line_80 |  | 75 | 77 | 0.054865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1058-19_0_4_line_81 |  | 76 | 78 | 0.014519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1058-19_0_4_line_82 |  | 77 | 79 | 0.0039095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1058-19_0_4_line_83 |  | 78 | 92 | 0.031601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1058-19_0_4_line_84 |  | 79 | 94 | 0.016318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1058-19_0_4_line_85 |  | 80 | 81 | 0.034588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1058-19_0_4_line_86 |  | 80 | 82 | 0.062788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1058-19_0_4_line_87 |  | 81 | 83 | 0.021136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1058-19_0_4_line_88 |  | 82 | 84 | 0.018535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1058-19_0_4_line_89 |  | 82 | 85 | 0.047755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1058-19_0_4_line_90 |  | 84 | 86 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1058-19_0_4_line_91 |  | 85 | 90 | 0.020883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1058-19_0_4_line_92 |  | 87 | 88 | 0.003249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1058-19_0_4_line_93 |  | 87 | 89 | 0.011833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1058-19_0_4_line_94 |  | 88 | 90 | 0.0038204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1058-19_0_4_line_95 |  | 91 | 104 | 0.0064186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1058-19_0_4_line_96 |  | 92 | 93 | 0.0096888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1058-19_0_4_line_97 |  | 93 | 100 | 0.016967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1058-19_0_4_line_98 |  | 94 | 95 | 0.00065611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1058-19_0_4_line_99 |  | 95 | 96 | 0.014308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1058-19_0_4_line_100 |  | 96 | 97 | 0.019848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1058-19_0_4_line_101 |  | 97 | 105 | 0.14251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1058-19_0_4_line_102 |  | 100 | 101 | 0.0039971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1058-19_0_4_line_103 |  | 101 | 102 | 0.021672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1058-19_0_4_line_104 |  | 102 | 103 | 0.0088742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1058-19_0_4_line_105 |  | 103 | 106 | 0.022352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1058-19_0_4_line_106 |  | 104 | 108 | 0.03068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1058-19_0_4_line_107 |  | 106 | 107 | 0.0096803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1058-19_0_4_trafo_83 | 0.63 MVA 20/0.4 kV | 109 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2665949.2112 | 1206689.8671 | 2665948.5842 | 1206679.7543 | 2665946.5958 | 1206664.3887
1 | 2665949.3781 | 1206692.5598 | 2665949.2112 | 1206689.8671
2 | 2665946.5958 | 1206664.3887 | 2665944.5904 | 1206648.8915 | 2665939.4894 | 1206634.4344
3 | 2665949.3781 | 1206692.5598 | 2665950.0702 | 1206706.3202 | 2665948.8016 | 1206713.7663
4 | 2665949.3781 | 1206692.5598 | 2665945.0752 | 1206687.6092 | 2665931.7923 | 1206624.6799 | 2665929.7441 | 1206613.1017
5 | 2665941.0939 | 1206730.6359 | 2665945.5438 | 1206718.8445 | 2665948.8016 | 1206713.7663
6 | 2665922.3566 | 1206556.312 | 2665924.8418 | 1206585.3904 | 2665929.7441 | 1206613.1017
7 | 2665921.6953 | 1206672.6531 | 2665934.0341 | 1206708.1331 | 2665941.0939 | 1206730.6359
8 | 2665854.5476 | 1206475.1034 | 2665868.5445 | 1206480.3276 | 2665890.4941 | 1206485.7619 | 2665893.8995 | 1206486.6111 | 2665894.6959 | 1206486.8089 | 2665896.1209 | 1206487.236 | 2665899.4866 | 1206488.2404 | 2665900.7829 | 1206488.6216 | 2665903.1514 | 1206489.0147 | 2665905.3148 | 1206489.3832 | 2665907.9218 | 1206490.2125 | 2665905.1199 | 1206504.9683 | 2665905.7909 | 1206506.1876 | 2665911.5472 | 1206506.9516 | 2665926.3681 | 1206509.172 | 2665924.2446 | 1206525.8476 | 2665922.3566 | 1206556.312
9 | 2665921.6953 | 1206672.6531 | 2665921.4544 | 1206677.2533 | 2665924.2522 | 1206686.2785 | 2665925.4104 | 1206689.5495
10 | 2665854.5476 | 1206475.1034 | 2665855.8735 | 1206462.4659 | 2665856.0355 | 1206461.8638
11 | 2665854.5476 | 1206475.1034 | 2665853.9122 | 1206484.2976
12 | 2665230.9932 | 1206689.3902 | 2665230.9932 | 1206689.3902 | 2665210.6777 | 1206673.6144 | 2665207.7777 | 1206668.2795 | 2665202.3484 | 1206670.9996 | 2665202.2691 | 1206680.3489 | 2665203.3052 | 1206698.2822 | 2665201.8283 | 1206712.3412 | 2665197.5723 | 1206714.8741 | 2665190.51 | 1206709.7606 | 2665183.194 | 1206696.5282 | 2665172.432 | 1206692.4416 | 2665146.6111 | 1206694.0164 | 2665136.3195 | 1206671.2126 | 2665129.7713 | 1206665.6711 | 2665125.0712 | 1206669.1664 | 2665122.9169 | 1206675.6357 | 2665123.8071 | 1206683.9616 | 2665127.5184 | 1206692.3183 | 2665128.3069 | 1206698.8086 | 2665127.9448 | 1206709.689 | 2665122.7862 | 1206712.7012 | 2665114.7929 | 1206713.4479 | 2665100.8766 | 1206707.1034 | 2665083.5444 | 1206700.8774 | 2665036.0633 | 1206677.4571 | 2665022.2106 | 1206665.2655 | 2665017.3554 | 1206663.6338
13 | 2665542.1078 | 1206612.7066 | 2665230.9932 | 1206689.3902
14 | 2665017.3554 | 1206663.6338 | 2665007.988 | 1206660.4856 | 2664998.5094 | 1206655.8775
15 | 2665542.1078 | 1206612.7066 | 2665542.4533 | 1206612.676 | 2665542.4533 | 1206612.676
16 | 2665544.1639 | 1206616.2702 | 2665542.4533 | 1206612.676
17 | 2665933.9105 | 1206713.5547 | 2665925.4104 | 1206689.5495
18 | 2665819.0923 | 1206668.1632 | 2665819.6288 | 1206670.5483 | 2665819.612 | 1206672.0713 | 2665819.2413 | 1206682.9294
19 | 2665798.474 | 1206671.0266 | 2665819.0923 | 1206668.1632
20 | 2665819.0923 | 1206668.1632 | 2665832.4369 | 1206666.298 | 2665839.9115 | 1206665.7134 | 2665841.9711 | 1206665.8362 | 2665841.934 | 1206665.0575 | 2665841.8131 | 1206662.2323 | 2665841.6914 | 1206659.4737 | 2665841.637 | 1206658.2056 | 2665846.8475 | 1206658.1075
21 | 2665798.474 | 1206671.0266 | 2665798.8925 | 1206673.7662 | 2665791.0425 | 1206675.9811 | 2665791.1801 | 1206683.5094
22 | 2665770.7264 | 1206674.89 | 2665798.474 | 1206671.0266
23 | 2665846.8475 | 1206658.1075 | 2665843.2316 | 1206652.9089 | 2665837.585 | 1206649.586
24 | 2665846.8475 | 1206658.1075 | 2665847.0796 | 1206658.4436 | 2665847.8776 | 1206662.6216 | 2665855.9746 | 1206664.9011
25 | 2665675.0038 | 1206952.5608 | 2665679.6637 | 1206956.1809 | 2665682.9596 | 1206957.2845 | 2665690.3524 | 1206957.5692
26 | 2665666.2493 | 1206929.2059 | 2665669.2923 | 1206942.2362 | 2665671.8416 | 1206948.9905 | 2665675.0038 | 1206952.5608
27 | 2665717.6886 | 1206966.3832 | 2665711.4749 | 1206962.3124 | 2665704.8907 | 1206959.416 | 2665698.7249 | 1206957.8917 | 2665690.3524 | 1206957.5692
28 | 2665666.2493 | 1206929.2059 | 2665661.1569 | 1206907.4121
29 | 2665592.2747 | 1206859.6729 | 2665585.6387 | 1206844.1795
30 | 2665627.6419 | 1206838.4708 | 2665625.7136 | 1206838.1606 | 2665602.5909 | 1206839.2294 | 2665591.9227 | 1206839.8014 | 2665586.9843 | 1206840.7589 | 2665584.5561 | 1206841.655 | 2665585.6387 | 1206844.1795
31 | 2665585.6387 | 1206844.1795 | 2665576.3435 | 1206847.8352 | 2665571.824 | 1206850.8096 | 2665569.5407 | 1206854.4423 | 2665569.2907 | 1206858.5087 | 2665570.6677 | 1206863.3045 | 2665574.0881 | 1206867.6114 | 2665578.0381 | 1206870.1007 | 2665580.0655 | 1206871.2382
32 | 2665627.6419 | 1206838.4708 | 2665628.8033 | 1206838.6615 | 2665634.8471 | 1206840.2289 | 2665641.2033 | 1206843.812 | 2665645.6202 | 1206848.7858 | 2665647.849 | 1206852.8795 | 2665649.5594 | 1206857.779 | 2665652.599 | 1206870.7875
33 | 2665627.6419 | 1206838.4708 | 2665630.2853 | 1206834.5975
34 | 2665601.9271 | 1206908.6541 | 2665601.9018 | 1206907.4633 | 2665601.2607 | 1206900.7521 | 2665594.4082 | 1206884.2002 | 2665590.5985 | 1206877.9545 | 2665585.2334 | 1206874.1377 | 2665580.0655 | 1206871.2382
35 | 2665810.9403 | 1206797.085 | 2665811.6151 | 1206797.9597 | 2665813.4149 | 1206800.2587
36 | 2665813.4149 | 1206800.2587 | 2665822.8871 | 1206811.6033 | 2665823.8801 | 1206814.6605 | 2665823.7322 | 1206818.4167 | 2665821.7515 | 1206822.9228
37 | 2665810.9403 | 1206797.085 | 2665805.7497 | 1206800.9079 | 2665799.795 | 1206802.988 | 2665798.5529 | 1206803.4743
38 | 2665810.9403 | 1206797.085 | 2665812.3751 | 1206795.9335 | 2665815.5641 | 1206791.566 | 2665818.2626 | 1206786.1591 | 2665820.3501 | 1206779.6114 | 2665821.3867 | 1206773.4102
39 | 2665821.7515 | 1206822.9228 | 2665821.3296 | 1206823.8825 | 2665814.965 | 1206836.9314 | 2665810.9535 | 1206840.0335 | 2665806.75 | 1206841.9217 | 2665801.1882 | 1206841.5744
40 | 2665773.9073 | 1206871.3778 | 2665774.1563 | 1206868.79 | 2665775.8801 | 1206864.184 | 2665779.1171 | 1206858.9053 | 2665782.2473 | 1206855.0375 | 2665783.0309 | 1206859.8379 | 2665787.5273 | 1206858.9647
41 | 2665773.9073 | 1206871.3778 | 2665772.0079 | 1206871.2123 | 2665769.3867 | 1206870.9944 | 2665768.7637 | 1206870.9431 | 2665767.8887 | 1206868.91 | 2665766.6432 | 1206865.9945 | 2665766.1315 | 1206864.8103 | 2665764.8637 | 1206861.8501 | 2665759.8042 | 1206849.6426 | 2665759.0006 | 1206848.722 | 2665741.8442 | 1206845.2755 | 2665737.7286 | 1206844.2151
42 | 2665787.5273 | 1206858.9647 | 2665788.2376 | 1206862.5643
43 | 2665787.5273 | 1206858.9647 | 2665785.5663 | 1206845.7684 | 2665780.943 | 1206845.0392
44 | 2665737.7286 | 1206844.2151 | 2665719.9816 | 1206839.6426 | 2665713.0804 | 1206836.5203 | 2665710.8462 | 1206835.6841 | 2665704.11 | 1206836.2214 | 2665692.7272 | 1206835.3845 | 2665676.9556 | 1206831.8645 | 2665666.8651 | 1206831.0753 | 2665658.979 | 1206831.7556 | 2665630.2853 | 1206834.5975 | 2665630.2853 | 1206834.5975
45 | 2665780.3898 | 1206840.7194 | 2665780.943 | 1206845.0392
46 | 2665780.943 | 1206845.0392 | 2665778.3806 | 1206842.932 | 2665773.693 | 1206824.5803 | 2665772.8354 | 1206809.9286 | 2665772.2922 | 1206803.3358
47 | 2665780.3898 | 1206840.7194 | 2665781.3256 | 1206840.6852 | 2665784.9089 | 1206840.558
48 | 2665853.9122 | 1206484.2976 | 2665852.2127 | 1206508.8871 | 2665852.2028 | 1206514.423
49 | 2665825.2093 | 1206752.0594 | 2665820.8021 | 1206751.0435 | 2665812.1084 | 1206744.638
50 | 2665825.2093 | 1206752.0594 | 2665822.7357 | 1206765.3402 | 2665821.3867 | 1206773.4102
51 | 2665801.6966 | 1206736.9665 | 2665812.1084 | 1206744.638
52 | 2665855.9746 | 1206664.9011 | 2665859.2821 | 1206652.5634 | 2665860.3187 | 1206642.7022 | 2665860.7427 | 1206631.1554 | 2665857.1125 | 1206601.872
53 | 2665853.4037 | 1206571.9555 | 2665857.1125 | 1206601.872
54 | 2665837.585 | 1206649.586 | 2665835.2223 | 1206648.1955 | 2665830.969 | 1206647.0035 | 2665818.8243 | 1206647.9892
55 | 2665717.6886 | 1206966.3832 | 2665719.9409 | 1206959.3593 | 2665721.0969 | 1206946.92 | 2665721.1582 | 1206932.3785 | 2665719.563 | 1206919.0974 | 2665717.938 | 1206910.5487
56 | 2665933.9105 | 1206713.5547 | 2665936.3618 | 1206720.4775 | 2665937.6829 | 1206735.3401
57 | 2665770.7264 | 1206674.89 | 2665771.1227 | 1206678.2631 | 2665763.0242 | 1206679.5636 | 2665762.9699 | 1206687.2565
58 | 2665734.7225 | 1206686.7897 | 2665736.047 | 1206685.2923 | 2665739.0316 | 1206682.9126 | 2665746.3458 | 1206678.9351 | 2665751.4028 | 1206677.5788 | 2665770.7264 | 1206674.89
59 | 2665652.599 | 1206870.7875 | 2665661.1569 | 1206907.4121
60 | 2665801.6966 | 1206736.9665 | 2665795.3121 | 1206732.2623 | 2665786.7359 | 1206735.5143 | 2665770.7166 | 1206733.4097
61 | 2665705.2457 | 1206729.6024 | 2665710.877 | 1206724.439 | 2665708.4817 | 1206722.3447
62 | 2665708.4817 | 1206722.3447 | 2665706.2447 | 1206720.3745 | 2665704.815 | 1206718.3019 | 2665704.1693 | 1206716.1602 | 2665703.725 | 1206713.6871 | 2665703.6579 | 1206712.0442
63 | 2665699.4617 | 1206731.3732 | 2665703.2325 | 1206730.7921 | 2665705.2457 | 1206729.6024
64 | 2665705.2457 | 1206729.6024 | 2665707.2383 | 1206730.9808 | 2665715.4918 | 1206731.4719 | 2665719.0581 | 1206731.5111 | 2665727.2462 | 1206728.9664 | 2665732.05 | 1206728.5078 | 2665752.9277 | 1206731.0726 | 2665770.7166 | 1206733.4097
65 | 2665700.7512 | 1206700.5909 | 2665701.7326 | 1206701.9359 | 2665703.2446 | 1206706.9 | 2665703.5932 | 1206710.4615 | 2665703.6579 | 1206712.0442
66 | 2665734.7225 | 1206686.7897 | 2665734.7061 | 1206703.4663
67 | 2665719.4226 | 1206693.5699 | 2665721.8681 | 1206693.1854 | 2665724.7619 | 1206694.2068 | 2665728.1179 | 1206695.3889 | 2665728.5082 | 1206694.4815 | 2665731.5037 | 1206690.412 | 2665734.7225 | 1206686.7897
68 | 2665719.4226 | 1206693.5699 | 2665718.3485 | 1206693.7359 | 2665717.419 | 1206694.5818 | 2665716.431 | 1206695.905 | 2665714.3837 | 1206699.4958 | 2665713.2494 | 1206700.9842 | 2665712.0772 | 1206701.7718 | 2665710.6485 | 1206702.3676 | 2665708.2736 | 1206702.5638 | 2665706.3272 | 1206702.5201 | 2665703.9916 | 1206701.9051 | 2665701.9456 | 1206700.5485 | 2665700.7512 | 1206700.5909
69 | 2665719.4226 | 1206693.5699 | 2665719.9637 | 1206691.3967 | 2665719.9474 | 1206690.118 | 2665719.7044 | 1206689.3927 | 2665719.2659 | 1206688.465 | 2665719.0858 | 1206687.5514 | 2665718.6997 | 1206684.6343
70 | 2665699.4617 | 1206731.3732 | 2665699.545 | 1206732.0968 | 2665697.5119 | 1206737.1664 | 2665693.4621 | 1206740.2904 | 2665686.2972 | 1206743.1578 | 2665679.563 | 1206745.5741 | 2665675.1495 | 1206750.6508 | 2665673.4215 | 1206755.646 | 2665673.4787 | 1206760.1271 | 2665675.7637 | 1206765.3332 | 2665679.7913 | 1206769.7468 | 2665682.9614 | 1206775.3329
71 | 2665700.7512 | 1206700.5909 | 2665699.0428 | 1206698.2707 | 2665696.468 | 1206697.2751 | 2665694.46 | 1206697.3086 | 2665693.6288 | 1206696.8214 | 2665692.7744 | 1206695.678 | 2665691.4338 | 1206693.7954 | 2665690.3072 | 1206692.5156 | 2665689.1638 | 1206692.0583 | 2665687.7176 | 1206692.1758 | 2665686.6539 | 1206692.7755 | 2665685.6544 | 1206694.4545 | 2665684.7725 | 1206696.5016 | 2665683.7839 | 1206697.8804 | 2665680.9551 | 1206699.239 | 2665678.0192 | 1206699.9627 | 2665675.3442 | 1206699.7888 | 2665671.3089 | 1206699.522
72 | 2665784.9089 | 1206840.558 | 2665801.1882 | 1206841.5744
73 | 2665853.4037 | 1206571.9555 | 2665852.118 | 1206561.5847 | 2665852.1511 | 1206543.1719
74 | 2665804.7629 | 1206649.6829 | 2665812.5179 | 1206648.501 | 2665818.8243 | 1206647.9892
75 | 2665852.1511 | 1206543.1719 | 2665852.2028 | 1206514.423
76 | 2665765.0415 | 1206611.64 | 2665766.436 | 1206637.3316
77 | 2665764.6632 | 1206604.6694 | 2665765.0415 | 1206611.64
78 | 2665767.3689 | 1206654.5184 | 2665766.436 | 1206637.3316
79 | 2665767.3689 | 1206654.5184 | 2665780.0235 | 1206653.8463 | 2665790.4455 | 1206652.0924
80 | 2665767.3689 | 1206654.5184 | 2665751.865 | 1206654.9591 | 2665743.7214 | 1206653.4463 | 2665715.0266 | 1206641.527
81 | 2665804.7629 | 1206649.6829 | 2665790.4455 | 1206652.0924
82 | 2665711.4162 | 1206640.0274 | 2665715.0266 | 1206641.527
83 | 2665804.7629 | 1206649.6829 | 2665802.7329 | 1206618.1472
84 | 2665711.4162 | 1206640.0274 | 2665708.9959 | 1206639.022 | 2665696.3056 | 1206633.8661
85 | 2665581.3495 | 1206688.6939 | 2665580.4715 | 1206692.9309 | 2665577.0888 | 1206703.8671 | 2665569.4997 | 1206721.0822
86 | 2665612.5895 | 1206668.5133 | 2665606.9517 | 1206659.0567 | 2665602.9161 | 1206655.3546 | 2665598.24 | 1206653.8801 | 2665594.7658 | 1206654.4534 | 2665591.0641 | 1206657.0477 | 2665585.6433 | 1206667.9726 | 2665581.3495 | 1206688.6939
87 | 2665569.4997 | 1206721.0822 | 2665564.3291 | 1206732.8112 | 2665561.0042 | 1206738.4893 | 2665559.9643 | 1206739.8816
88 | 2665612.5895 | 1206668.5133 | 2665609.7814 | 1206674.2193 | 2665609.3257 | 1206678.3167 | 2665610.1459 | 1206686.3275
89 | 2665612.5895 | 1206668.5133 | 2665617.8194 | 1206666.6585 | 2665624.6918 | 1206665.5 | 2665631.1204 | 1206668.7504 | 2665644.2876 | 1206681.614 | 2665647.7913 | 1206686.6556 | 2665644.8205 | 1206688.4796
90 | 2665611.9491 | 1206703.9389 | 2665610.1459 | 1206686.3275
91 | 2665644.8205 | 1206688.4796 | 2665647.51 | 1206692.1781 | 2665653.0998 | 1206701.1561 | 2665656.338 | 1206705.4388 | 2665656.5865 | 1206705.7062
92 | 2665661.8012 | 1206706.5662 | 2665659.1866 | 1206708.5053
93 | 2665661.8012 | 1206706.5662 | 2665671.3089 | 1206699.522
94 | 2665659.1866 | 1206708.5053 | 2665656.5865 | 1206705.7062
95 | 2665682.9614 | 1206775.3329 | 2665683.7975 | 1206776.8063 | 2665685.1368 | 1206781.337
96 | 2665802.1106 | 1206608.4785 | 2665802.7329 | 1206618.1472
97 | 2665802.1106 | 1206608.4785 | 2665801.0207 | 1206591.5467
98 | 2665695.6978 | 1206633.6192 | 2665696.3056 | 1206633.8661
99 | 2665695.6978 | 1206633.6192 | 2665691.5292 | 1206631.9255 | 2665682.389 | 1206628.3673 | 2665682.389 | 1206628.3673
100 | 2665662.9757 | 1206631.6113 | 2665662.9757 | 1206631.6113 | 2665675.4541 | 1206628.291 | 2665682.389 | 1206628.3673
101 | 2665662.9757 | 1206631.6113 | 2665662.88 | 1206643.0728 | 2665654.4305 | 1206650.7068 | 2665646.4855 | 1206649.8078 | 2665632.714 | 1206648.3111 | 2665623.4812 | 1206649.0323 | 2665612.0661 | 1206648.3286 | 2665598.8081 | 1206645.0921 | 2665581.5713 | 1206639.2104 | 2665564.6801 | 1206631.6314 | 2665547.2405 | 1206622.7346 | 2665544.1639 | 1206616.2702
102 | 2665800.7639 | 1206587.5578 | 2665801.0207 | 1206591.5467
103 | 2665800.7639 | 1206587.5578 | 2665799.3717 | 1206565.9301
104 | 2665798.8017 | 1206557.0742 | 2665799.3717 | 1206565.9301
105 | 2665798.8017 | 1206557.0742 | 2665797.3658 | 1206534.7681
106 | 2665697.318 | 1206808.6744 | 2665692.568 | 1206804.2528 | 2665689.1789 | 1206797.1 | 2665687.7177 | 1206790.9802 | 2665685.6671 | 1206783.1307 | 2665685.1368 | 1206781.337
107 | 2665796.744 | 1206525.1078 | 2665797.3658 | 1206534.7681

## bus_geodata
| x | y | coords
0 | 2665949.2112 | 1206689.8671
1 | 2665946.5958 | 1206664.3887
2 | 2665949.3781 | 1206692.5598
3 | 2665939.4894 | 1206634.4344
4 | 2665948.8016 | 1206713.7663
5 | 2665929.7441 | 1206613.1017
6 | 2665941.0939 | 1206730.6359
7 | 2665922.3567 | 1206556.312
8 | 2665921.6953 | 1206672.6531
9 | 2665854.5476 | 1206475.1034
10 | 2665230.9932 | 1206689.3902
11 | 2665017.3554 | 1206663.6338
12 | 2665542.1078 | 1206612.7066
13 | 2664998.5094 | 1206655.8775
14 | 2665542.4533 | 1206612.676
15 | 2665925.4104 | 1206689.5495
16 | 2665819.0923 | 1206668.1632
17 | 2665819.2413 | 1206682.9294
18 | 2665798.474 | 1206671.0266
19 | 2665846.8475 | 1206658.1075
20 | 2665675.0038 | 1206952.5608
21 | 2665690.3524 | 1206957.5692
22 | 2665666.2493 | 1206929.2059
23 | 2665585.6387 | 1206844.1795
24 | 2665592.2747 | 1206859.6729
25 | 2665627.6419 | 1206838.4708
26 | 2665580.0655 | 1206871.2382
27 | 2665813.4149 | 1206800.2587
28 | 2665810.9403 | 1206797.085
29 | 2665821.7515 | 1206822.9228
30 | 2665773.9073 | 1206871.3778
31 | 2665787.5273 | 1206858.9647
32 | 2665737.7286 | 1206844.2151
33 | 2665780.943 | 1206845.0392
34 | 2665780.3898 | 1206840.7194
35 | 2665772.2922 | 1206803.3358
36 | 2665788.2376 | 1206862.5643
37 | 2665856.0355 | 1206461.8638
38 | 2665853.9122 | 1206484.2976
39 | 2665825.2093 | 1206752.0594
40 | 2665812.1084 | 1206744.638
41 | 2665821.3867 | 1206773.4102
42 | 2665855.9746 | 1206664.9011
43 | 2665857.1125 | 1206601.872
44 | 2665837.585 | 1206649.586
45 | 2665717.6886 | 1206966.3832
46 | 2665717.938 | 1206910.5487
47 | 2665933.9105 | 1206713.5547
48 | 2665937.6829 | 1206735.3401
49 | 2665791.1801 | 1206683.5094
50 | 2665770.7264 | 1206674.89
51 | 2665661.1569 | 1206907.4121
52 | 2665801.6966 | 1206736.9665
53 | 2665708.4817 | 1206722.3447
54 | 2665705.2457 | 1206729.6024
55 | 2665703.6579 | 1206712.0442
56 | 2665734.7225 | 1206686.7897
57 | 2665734.7061 | 1206703.4663
58 | 2665719.4226 | 1206693.5699
59 | 2665699.4617 | 1206731.3732
60 | 2665770.7166 | 1206733.4097
61 | 2665718.6997 | 1206684.6343
62 | 2665700.7512 | 1206700.5909
63 | 2665630.2853 | 1206834.5975
64 | 2665784.9089 | 1206840.558
65 | 2665801.1882 | 1206841.5744
66 | 2665853.4037 | 1206571.9555
67 | 2665652.599 | 1206870.7875
68 | 2665601.9271 | 1206908.6541
69 | 2665818.8243 | 1206647.9892
70 | 2665798.5529 | 1206803.4743
71 | 2665852.2028 | 1206514.423
72 | 2665765.0415 | 1206611.64
73 | 2665766.436 | 1206637.3316
74 | 2665764.6632 | 1206604.6694
75 | 2665767.3689 | 1206654.5184
76 | 2665790.4455 | 1206652.0924
77 | 2665715.0266 | 1206641.527
78 | 2665804.7629 | 1206649.6829
79 | 2665711.4162 | 1206640.0274
80 | 2665581.3495 | 1206688.6939
81 | 2665569.4997 | 1206721.0822
82 | 2665612.5895 | 1206668.5133
83 | 2665559.9643 | 1206739.8816
84 | 2665610.1459 | 1206686.3275
85 | 2665644.8205 | 1206688.4796
86 | 2665611.9491 | 1206703.9389
87 | 2665661.8012 | 1206706.5662
88 | 2665659.1866 | 1206708.5053
89 | 2665671.3089 | 1206699.522
90 | 2665656.5865 | 1206705.7062
91 | 2665682.9614 | 1206775.3329
92 | 2665802.7329 | 1206618.1472
93 | 2665802.1106 | 1206608.4784
94 | 2665696.3056 | 1206633.8661
95 | 2665695.6978 | 1206633.6192
96 | 2665682.389 | 1206628.3673
97 | 2665662.9757 | 1206631.6113
98 | 2665852.1511 | 1206543.1718
99 | 2665762.9699 | 1206687.2565
100 | 2665801.0207 | 1206591.5467
101 | 2665800.7639 | 1206587.5578
102 | 2665799.3717 | 1206565.9301
103 | 2665798.8017 | 1206557.0742
104 | 2665685.1368 | 1206781.337
105 | 2665544.1639 | 1206616.2702
106 | 2665797.3658 | 1206534.7681
107 | 2665796.744 | 1206525.1078
108 | 2665697.318 | 1206808.6744
109 | 2665732.4122 | 1206706.6652

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9777 | -0.43043 | 0.0045285 | 0.0011349
1 | 0.97753 | -0.43368 | 0.0030167 | 0.00075606
2 | 0.97773 | -0.42987 | 0 | 0
3 | 0.97742 | -0.4359 | 0.0039284 | 0.00098455
4 | 0.97761 | -0.43204 | 0.00040161 | 0.00010065
5 | 0.97903 | -0.4042 | 0.0015973 | 0.00040032
6 | 0.97753 | -0.4338 | 0 | 0
7 | 0.98002 | -0.38477 | 0 | 0
8 | 0.97723 | -0.43958 | 0 | 0
9 | 0.98245 | -0.33743 | 0 | 0
10 | 0.97698 | -0.44481 | 0.00053495 | 0.00013407
11 | 0.97624 | -0.45952 | 0.0010597 | 0.00026559
12 | 0.97782 | -0.4282 | 0.0023364 | 0.00058556
13 | 0.97622 | -0.45998 | 0.0012283 | 0.00030784
14 | 0.97782 | -0.42817 | 0.0017469 | 0.00043782
15 | 0.97715 | -0.44124 | 0.0027837 | 0.00069767
16 | 0.99236 | -0.14558 | 0 | 0
17 | 0.99158 | -0.16072 | 0.057615 | 0.01444
18 | 0.99363 | -0.12117 | 0 | 0
19 | 0.98891 | -0.21201 | 0 | 0
20 | 0.97315 | -0.5174 | 0 | 0
21 | 0.9726 | -0.52824 | 0.018284 | 0.0045823
22 | 0.97398 | -0.50103 | 0 | 0
23 | 0.97481 | -0.48467 | 0 | 0
24 | 0.97452 | -0.49045 | 0.018686 | 0.0046833
25 | 0.97608 | -0.45963 | 0 | 0
26 | 0.97325 | -0.51554 | 0.022442 | 0.0056245
27 | 0.98602 | -0.26639 | 0 | 0
28 | 0.98618 | -0.26337 | 0 | 0
29 | 0.98498 | -0.28639 | 0.0088107 | 0.0022082
30 | 0.98138 | -0.35609 | 0 | 0
31 | 0.98232 | -0.33795 | 0 | 0
32 | 0.97968 | -0.38923 | 0.0072276 | 0.0018114
33 | 0.98295 | -0.32572 | 0 | 0
34 | 0.98311 | -0.32271 | 0 | 0
35 | 0.98283 | -0.32802 | 0.0029277 | 0.00073376
36 | 0.98229 | -0.33845 | 0.0076229 | 0.0019105
37 | 0.98243 | -0.33781 | 0.001573 | 0.00039422
38 | 0.98262 | -0.33406 | 0.0013405 | 0.00033597
39 | 0.98812 | -0.22598 | 0 | 0
40 | 0.98875 | -0.21397 | 0.0039704 | 0.00099508
41 | 0.98723 | -0.24301 | 0.0037611 | 0.00094263
42 | 0.98829 | -0.22393 | 0 | 0
43 | 0.98528 | -0.28225 | 0.023309 | 0.0058419
44 | 0.98797 | -0.2301 | 0.032477 | 0.0081395
45 | 0.97214 | -0.53734 | 0 | 0
46 | 0.97125 | -0.55487 | 0.016812 | 0.0042136
47 | 0.97709 | -0.44235 | 0.00089132 | 0.00022339
48 | 0.97706 | -0.44297 | 0.0015031 | 0.00037672
49 | 0.99348 | -0.12405 | 0.0088529 | 0.0022187
50 | 0.9954 | -0.087331 | 0 | 0
51 | 0.97471 | -0.48661 | 0.018294 | 0.004585
52 | 0.98929 | -0.20361 | 0.0063365 | 0.0015881
53 | 0.99421 | -0.10979 | 0 | 0
54 | 0.99368 | -0.11973 | 0 | 0
55 | 0.99478 | -0.098887 | 0.0016869 | 0.00042277
56 | 0.99792 | -0.039392 | 0 | 0
57 | 1 | 0 | -0.55084 | -0.14084
58 | 0.99672 | -0.062093 | 0 | 0
59 | 0.99359 | -0.12157 | 0 | 0
60 | 0.99073 | -0.17609 | 0.0050205 | 0.0012583
61 | 0.99665 | -0.063421 | 0.0082424 | 0.0020657
62 | 0.99537 | -0.087792 | 0 | 0
63 | 0.97623 | -0.45681 | 0.0039486 | 0.00098961
64 | 0.98327 | -0.31959 | 0 | 0
65 | 0.98385 | -0.30833 | 0.0050777 | 0.0012726
66 | 0.98451 | -0.29731 | 0.0028162 | 0.00070582
67 | 0.97534 | -0.47434 | 0.018685 | 0.004683
68 | 0.97247 | -0.53092 | 0.018285 | 0.0045827
69 | 0.98574 | -0.27334 | 0.020589 | 0.00516
70 | 0.98611 | -0.2646 | 0.0048515 | 0.0012159
71 | 0.98322 | -0.32231 | 0.0016399 | 0.00041101
72 | 0.98159 | -0.3542 | 0.002696 | 0.00067569
73 | 0.98194 | -0.34737 | 0.0046858 | 0.0011744
74 | 0.98152 | -0.35571 | 0.011979 | 0.0030023
75 | 0.98225 | -0.34135 | 0 | 0
76 | 0.98352 | -0.31654 | 0.0045088 | 0.00113
77 | 0.98023 | -0.38089 | 0.0032587 | 0.00081672
78 | 0.98438 | -0.29989 | 0 | 0
79 | 0.9801 | -0.38349 | 0.0022197 | 0.0005563
80 | 0.99126 | -0.16716 | 0.0031061 | 0.00077846
81 | 0.991 | -0.17208 | 0.0053755 | 0.0013472
82 | 0.9919 | -0.15478 | 0 | 0
83 | 0.99095 | -0.17307 | 0.0026375 | 0.00066102
84 | 0.99165 | -0.15955 | 0.012089 | 0.0030297
85 | 0.99302 | -0.13312 | 0 | 0
86 | 0.99161 | -0.16031 | 0.0024185 | 0.00060613
87 | 0.99368 | -0.12021 | 0 | 0
88 | 0.9936 | -0.1218 | 0 | 0
89 | 0.99398 | -0.11443 | 0.013509 | 0.0033856
90 | 0.99351 | -0.12366 | 0.0020344 | 0.00050988
91 | 0.99265 | -0.13981 | 0.0046165 | 0.001157
92 | 0.98319 | -0.323 | 0.017279 | 0.0043305
93 | 0.98299 | -0.32708 | 0.0062895 | 0.0015763
94 | 0.97958 | -0.39366 | 0.0042547 | 0.0010663
95 | 0.97956 | -0.39402 | 0.0059241 | 0.0014847
96 | 0.97924 | -0.4003 | 0.0065504 | 0.0016417
97 | 0.97892 | -0.40665 | 0.009503 | 0.0023817
98 | 0.98384 | -0.31028 | 0.0017558 | 0.00044005
99 | 0.99528 | -0.089621 | 0.0067553 | 0.001693
100 | 0.98272 | -0.3323 | 0.0030986 | 0.00077659
101 | 0.98267 | -0.33331 | 0.0045787 | 0.0011475
102 | 0.98248 | -0.33697 | 0.0015797 | 0.0003959
103 | 0.98242 | -0.33822 | 0.0039406 | 0.0009876
104 | 0.99257 | -0.14122 | 0.0033675 | 0.00084397
105 | 0.97785 | -0.42767 | 0.0011688 | 0.00029292
106 | 0.98234 | -0.33977 | 0.002274 | 0.00056992
107 | 0.98232 | -0.34005 | 0.0015733 | 0.00039431
108 | 0.99232 | -0.14611 | 0.0090071 | 0.0022574
109 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0069466 | 0.0017409 | -0.0069455 | -0.0017405 | 1.0741e-06 | 3.6614e-07 | 0.010572 | 0.010573 | 0.010573 | 0.9777 | -0.43043 | 0.97753 | -0.43368 | 2.9045
1 | -0.011475 | -0.0028758 | 0.011475 | 0.002876 | 3.0858e-07 | 1.6366e-07 | 0.017465 | 0.017465 | 0.017465 | 0.9777 | -0.43043 | 0.97773 | -0.42987 | 4.798
2 | 0.0039288 | 0.00098442 | -0.0039284 | -0.00098455 | 4.152e-07 | -1.2231e-07 | 0.0059804 | 0.0059805 | 0.0059805 | 0.97753 | -0.43368 | 0.97742 | -0.4359 | 1.643
3 | 0.0055828 | 0.0013983 | -0.0055822 | -0.0013982 | 5.7743e-07 | 1.0207e-07 | 0.0084962 | 0.0084963 | 0.0084963 | 0.97773 | -0.42987 | 0.97761 | -0.43204 | 2.3342
4 | -0.017058 | -0.0042742 | 0.017079 | 0.0042866 | 2.0884e-05 | 1.2328e-05 | 0.025961 | 0.02596 | 0.025961 | 0.97773 | -0.42987 | 0.97903 | -0.4042 | 7.1321
5 | 0.0051806 | 0.0012975 | -0.0051802 | -0.0012975 | 4.3452e-07 | 4.4438e-08 | 0.007885 | 0.0078851 | 0.0078851 | 0.97761 | -0.43204 | 0.97753 | -0.4338 | 2.1662
6 | -0.018676 | -0.0046869 | 0.018694 | 0.0046972 | 1.7324e-05 | 1.0366e-05 | 0.028388 | 0.028388 | 0.028388 | 0.97903 | -0.4042 | 0.98002 | -0.38477 | 7.7989
7 | 0.0051802 | 0.0012975 | -0.0051787 | -0.0012973 | 1.4256e-06 | 1.4613e-07 | 0.0078851 | 0.0078854 | 0.0078854 | 0.97753 | -0.4338 | 0.97723 | -0.43958 | 2.1663
8 | -0.018694 | -0.0046972 | 0.018736 | 0.0047226 | 4.2338e-05 | 2.5327e-05 | 0.028388 | 0.028387 | 0.028388 | 0.98002 | -0.38477 | 0.98245 | -0.33743 | 7.7989
9 | 0.0051787 | 0.0012973 | -0.0051783 | -0.0012973 | 4.0865e-07 | 4.1983e-08 | 0.0078854 | 0.0078855 | 0.0078855 | 0.97723 | -0.43958 | 0.97715 | -0.44124 | 2.1663
10 | 0.001573 | 0.00039407 | -0.001573 | -0.00039422 | 2.8374e-08 | -1.5064e-07 | 0.0023824 | 0.0023825 | 0.0023825 | 0.98245 | -0.33743 | 0.98243 | -0.33781 | 0.65452
11 | -0.020309 | -0.0051166 | 0.020312 | 0.0051186 | 3.2721e-06 | 1.9774e-06 | 0.03077 | 0.03077 | 0.03077 | 0.98245 | -0.33743 | 0.98262 | -0.33406 | 8.4532
12 | 0.0022896 | 0.00056982 | -0.002288 | -0.00057319 | 1.5998e-06 | -3.3673e-06 | 0.0034858 | 0.0034874 | 0.0034874 | 0.97698 | -0.44481 | 0.97624 | -0.45952 | 0.95807
13 | -0.0028246 | -0.00070389 | 0.0028268 | 0.0007013 | 2.2216e-06 | -2.5941e-06 | 0.0043006 | 0.0042992 | 0.0043006 | 0.97698 | -0.44481 | 0.97782 | -0.4282 | 1.1815
14 | 0.0012283 | 0.0003076 | -0.0012283 | -0.00030784 | 2.6842e-08 | -2.3815e-07 | 0.0018721 | 0.0018722 | 0.0018722 | 0.97624 | -0.45952 | 0.97622 | -0.45998 | 0.51435
15 | -0.0051632 | -0.0012869 | 0.0051632 | 0.0012869 | 8.0241e-09 | 7.8477e-10 | 0.0078546 | 0.0078546 | 0.0078546 | 0.97782 | -0.4282 | 0.97782 | -0.42817 | 2.1579
16 | -0.0069101 | -0.0017247 | 0.0069103 | 0.0017247 | 1.6498e-07 | 5.5654e-08 | 0.010513 | 0.010513 | 0.010513 | 0.97782 | -0.42817 | 0.97785 | -0.42767 | 2.8882
17 | 0.0023946 | 0.00059961 | -0.0023945 | -0.00059985 | 1.2698e-07 | -2.3771e-07 | 0.0036464 | 0.0036465 | 0.0036465 | 0.97715 | -0.44124 | 0.97709 | -0.44235 | 1.0018
18 | 0.057657 | 0.014466 | -0.057615 | -0.01444 | 4.1586e-05 | 2.6424e-05 | 0.08646 | 0.08646 | 0.08646 | 0.99236 | -0.14558 | 0.99158 | -0.16072 | 23.7528
19 | -0.26791 | -0.067848 | 0.26822 | 0.068049 | 0.00031443 | 0.00020016 | 0.40197 | 0.40197 | 0.40197 | 0.99236 | -0.14558 | 0.99363 | -0.12117 | 27.6079
20 | 0.21025 | 0.053382 | -0.20958 | -0.052955 | 0.00066979 | 0.00042774 | 0.31551 | 0.31551 | 0.31551 | 0.99236 | -0.14558 | 0.98891 | -0.21201 | 43.3396
21 | 0.0088541 | 0.0022193 | -0.0088529 | -0.0022187 | 1.2156e-06 | 5.3922e-07 | 0.01326 | 0.01326 | 0.01326 | 0.99363 | -0.12117 | 0.99348 | -0.12405 | 3.6427
22 | -0.27708 | -0.070268 | 0.27753 | 0.070555 | 0.00045156 | 0.00028755 | 0.41523 | 0.41523 | 0.41523 | 0.99363 | -0.12117 | 0.9954 | -0.087331 | 28.5186
23 | 0.15817 | 0.039954 | -0.15804 | -0.039867 | 0.00013697 | 8.7333e-05 | 0.23812 | 0.23812 | 0.23812 | 0.98891 | -0.21201 | 0.98797 | -0.2301 | 32.7083
24 | 0.051408 | 0.013001 | -0.051379 | -0.012982 | 2.9367e-05 | 1.8627e-05 | 0.077396 | 0.077396 | 0.077396 | 0.98891 | -0.21201 | 0.98829 | -0.22393 | 21.2625
25 | 0.035135 | 0.0088199 | -0.035117 | -0.0088085 | 1.816e-05 | 1.1414e-05 | 0.05373 | 0.05373 | 0.05373 | 0.97315 | -0.5174 | 0.9726 | -0.52824 | 14.761
26 | -0.035135 | -0.0088199 | 0.035163 | 0.0088372 | 2.7458e-05 | 1.7257e-05 | 0.05373 | 0.05373 | 0.05373 | 0.97315 | -0.5174 | 0.97398 | -0.50103 | 14.7609
27 | 0.016834 | 0.0042262 | -0.016826 | -0.0042219 | 7.3023e-06 | 4.3094e-06 | 0.025757 | 0.025757 | 0.025757 | 0.9726 | -0.52824 | 0.97214 | -0.53734 | 7.0761
28 | -0.035163 | -0.0088372 | 0.035187 | 0.0088524 | 2.4229e-05 | 1.5228e-05 | 0.05373 | 0.05373 | 0.05373 | 0.97398 | -0.50103 | 0.97471 | -0.48661 | 14.7609
29 | 0.018692 | 0.0046863 | -0.018686 | -0.0046833 | 5.1442e-06 | 3.0823e-06 | 0.028533 | 0.028533 | 0.028533 | 0.97481 | -0.48467 | 0.97452 | -0.49045 | 7.8387
30 | -0.059492 | -0.01494 | 0.059564 | 0.014984 | 7.1184e-05 | 4.4409e-05 | 0.090824 | 0.090823 | 0.090824 | 0.97481 | -0.48467 | 0.97608 | -0.45963 | 12.4758
31 | 0.040801 | 0.010253 | -0.040741 | -0.010215 | 6.0017e-05 | 3.7897e-05 | 0.062291 | 0.062291 | 0.062291 | 0.97481 | -0.48467 | 0.97325 | -0.51554 | 17.113
32 | 0.072249 | 0.018169 | -0.072198 | -0.018139 | 5.072e-05 | 3.0234e-05 | 0.11016 | 0.11016 | 0.11016 | 0.97608 | -0.45963 | 0.97534 | -0.47434 | 7.5663
33 | -0.13181 | -0.033153 | 0.13183 | 0.033164 | 1.7759e-05 | 1.1131e-05 | 0.20099 | 0.20099 | 0.20099 | 0.97608 | -0.45963 | 0.97623 | -0.45681 | 13.8041
34 | 0.018299 | 0.0045907 | -0.018285 | -0.0045827 | 1.3408e-05 | 8.0138e-06 | 0.027979 | 0.027979 | 0.027979 | 0.97325 | -0.51554 | 0.97247 | -0.53092 | 7.6866
35 | -0.16879 | -0.042935 | 0.16881 | 0.04295 | 2.4502e-05 | 1.5476e-05 | 0.25495 | 0.25495 | 0.25495 | 0.98602 | -0.26639 | 0.98618 | -0.26337 | 17.5102
36 | 0.16879 | 0.042935 | -0.16863 | -0.042832 | 0.00016255 | 0.00010267 | 0.25495 | 0.25495 | 0.25495 | 0.98602 | -0.26639 | 0.98498 | -0.28639 | 17.5102
37 | 0.0048518 | 0.0012159 | -0.0048515 | -0.0012159 | 2.8314e-07 | 1.4699e-09 | 0.0073208 | 0.0073208 | 0.0073208 | 0.98618 | -0.26337 | 0.98611 | -0.2646 | 2.0112
38 | -0.17367 | -0.044166 | 0.17384 | 0.044274 | 0.00017057 | 0.00010781 | 0.26227 | 0.26227 | 0.26227 | 0.98618 | -0.26337 | 0.98723 | -0.24301 | 18.013
39 | 0.15982 | 0.040624 | -0.15965 | -0.040518 | 0.0001687 | 0.0001064 | 0.24164 | 0.24164 | 0.24164 | 0.98498 | -0.28639 | 0.98385 | -0.30833 | 16.5961
40 | -0.14367 | -0.036385 | 0.1438 | 0.036464 | 0.00012531 | 7.8774e-05 | 0.21798 | 0.21798 | 0.21798 | 0.98138 | -0.35609 | 0.98232 | -0.33795 | 14.9712
41 | 0.14367 | 0.036385 | -0.14345 | -0.036241 | 0.00022826 | 0.0001435 | 0.21798 | 0.21798 | 0.21798 | 0.98138 | -0.35609 | 0.97968 | -0.38923 | 14.9713
42 | 0.0076231 | 0.0019106 | -0.0076229 | -0.0019105 | 1.8347e-07 | 7.0973e-08 | 0.011547 | 0.011548 | 0.011548 | 0.98232 | -0.33795 | 0.98229 | -0.33845 | 3.1724
43 | -0.15142 | -0.038374 | 0.15151 | 0.03843 | 8.9009e-05 | 5.6053e-05 | 0.22953 | 0.22953 | 0.22953 | 0.98232 | -0.33795 | 0.98295 | -0.32572 | 15.7643
44 | 0.13622 | 0.03443 | -0.13578 | -0.034154 | 0.00043985 | 0.00027601 | 0.207 | 0.20701 | 0.20701 | 0.97968 | -0.38923 | 0.97623 | -0.45681 | 14.2174
45 | -0.15444 | -0.039164 | 0.15446 | 0.039178 | 2.2353e-05 | 1.4085e-05 | 0.23396 | 0.23396 | 0.23396 | 0.98295 | -0.32572 | 0.98311 | -0.32271 | 16.0687
46 | 0.0029281 | 0.00073341 | -0.0029277 | -0.00073376 | 3.2087e-07 | -3.4661e-07 | 0.0044324 | 0.0044326 | 0.0044326 | 0.98295 | -0.32572 | 0.98283 | -0.32802 | 1.2178
47 | -0.15446 | -0.039178 | 0.15449 | 0.039192 | 2.3138e-05 | 1.458e-05 | 0.23396 | 0.23396 | 0.23396 | 0.98311 | -0.32271 | 0.98327 | -0.31959 | 16.0687
48 | -0.021653 | -0.0054546 | 0.021665 | 0.005462 | 1.2177e-05 | 7.4108e-06 | 0.0328 | 0.032799 | 0.0328 | 0.98262 | -0.33406 | 0.98322 | -0.32231 | 9.0109
49 | -0.17774 | -0.045309 | 0.17785 | 0.045374 | 0.00010312 | 6.521e-05 | 0.26794 | 0.26794 | 0.26794 | 0.98812 | -0.22598 | 0.98875 | -0.21397 | 18.4023
50 | 0.17774 | 0.045309 | -0.1776 | -0.045217 | 0.00014599 | 9.2323e-05 | 0.26794 | 0.26794 | 0.26794 | 0.98812 | -0.22598 | 0.98723 | -0.24301 | 18.4023
51 | -0.18182 | -0.046369 | 0.18191 | 0.046427 | 9.0968e-05 | 5.7556e-05 | 0.27391 | 0.27391 | 0.27391 | 0.98875 | -0.21397 | 0.98929 | -0.20361 | 18.8126
52 | 0.051379 | 0.012982 | -0.051236 | -0.012891 | 0.0001432 | 9.0836e-05 | 0.077396 | 0.077396 | 0.077396 | 0.98829 | -0.22393 | 0.98528 | -0.28225 | 21.2626
53 | 0.027926 | 0.0070492 | -0.027906 | -0.0070367 | 2.0125e-05 | 1.2496e-05 | 0.042193 | 0.042193 | 0.042193 | 0.98528 | -0.28225 | 0.98451 | -0.29731 | 11.5915
54 | 0.12556 | 0.031727 | -0.1253 | -0.031561 | 0.00025967 | 0.00016594 | 0.1892 | 0.1892 | 0.1892 | 0.98797 | -0.2301 | 0.98574 | -0.27334 | 51.9787
55 | 0.016826 | 0.0042219 | -0.016812 | -0.0042136 | 1.4054e-05 | 8.2947e-06 | 0.025757 | 0.025757 | 0.025757 | 0.97214 | -0.53734 | 0.97125 | -0.55487 | 7.0762
56 | 0.0015032 | 0.00037647 | -0.0015031 | -0.00037672 | 4.3752e-08 | -2.5086e-07 | 0.0022891 | 0.0022892 | 0.0022892 | 0.97709 | -0.44235 | 0.97706 | -0.44297 | 0.6289
57 | 0.006756 | 0.0016933 | -0.0067553 | -0.001693 | 7.3712e-07 | 2.2129e-07 | 0.0101 | 0.0101 | 0.0101 | 0.9954 | -0.087331 | 0.99528 | -0.089621 | 2.7746
58 | -0.28428 | -0.072249 | 0.28494 | 0.072668 | 0.00065791 | 0.00041904 | 0.42533 | 0.42533 | 0.42533 | 0.9954 | -0.087331 | 0.99792 | -0.039392 | 29.2122
59 | -0.053482 | -0.013437 | 0.053513 | 0.013456 | 3.1349e-05 | 1.8656e-05 | 0.081658 | 0.081658 | 0.081658 | 0.97471 | -0.48661 | 0.97534 | -0.47434 | 7.4779
60 | -0.18824 | -0.048015 | 0.18849 | 0.048174 | 0.0002505 | 0.00015861 | 0.28344 | 0.28344 | 0.28344 | 0.98929 | -0.20361 | 0.99073 | -0.17609 | 19.4672
61 | 0.21116 | 0.054101 | -0.21105 | -0.054036 | 0.0001016 | 6.4464e-05 | 0.31646 | 0.31646 | 0.31646 | 0.99421 | -0.10979 | 0.99368 | -0.11973 | 21.7346
62 | -0.21116 | -0.054101 | 0.21127 | 0.054172 | 0.00011165 | 7.0842e-05 | 0.31646 | 0.31646 | 0.31646 | 0.99421 | -0.10979 | 0.99478 | -0.098887 | 21.7346
63 | 0.01701 | 0.0042693 | -0.017009 | -0.0042684 | 1.494e-06 | 8.7663e-07 | 0.025475 | 0.025475 | 0.025475 | 0.99368 | -0.11973 | 0.99359 | -0.12157 | 6.9985
64 | 0.19404 | 0.049767 | -0.19352 | -0.049432 | 0.00052893 | 0.00033507 | 0.29098 | 0.29098 | 0.29098 | 0.99368 | -0.11973 | 0.99073 | -0.17609 | 19.9851
65 | -0.21295 | -0.054594 | 0.21307 | 0.054667 | 0.00011463 | 7.2736e-05 | 0.31898 | 0.31898 | 0.31898 | 0.99478 | -0.098887 | 0.99537 | -0.087792 | 21.9079
66 | -0.54814 | -0.14017 | 0.54919 | 0.14084 | 0.001047 | 0.00066921 | 0.81834 | 0.81834 | 0.81834 | 0.99792 | -0.039392 | 1 | 0 | 56.2049
67 | 0.2632 | 0.067507 | -0.26291 | -0.067322 | 0.00028945 | 0.00018421 | 0.39301 | 0.39301 | 0.39301 | 0.99792 | -0.039392 | 0.99672 | -0.062093 | 26.9928
68 | 0.25467 | 0.065256 | -0.25435 | -0.065055 | 0.00031677 | 0.00020152 | 0.38071 | 0.38071 | 0.38071 | 0.99672 | -0.062093 | 0.99537 | -0.087792 | 26.1476
69 | 0.0082429 | 0.002066 | -0.0082424 | -0.0020657 | 5.215e-07 | 2.1408e-07 | 0.012306 | 0.012306 | 0.012306 | 0.99672 | -0.062093 | 0.99665 | -0.063421 | 3.3808
70 | 0.017009 | 0.0042684 | -0.016994 | -0.0042598 | 1.4785e-05 | 8.6765e-06 | 0.025475 | 0.025475 | 0.025475 | 0.99359 | -0.12157 | 0.99265 | -0.13981 | 6.9986
71 | 0.041284 | 0.010388 | -0.041231 | -0.010355 | 5.2485e-05 | 3.3114e-05 | 0.061732 | 0.061732 | 0.061732 | 0.99537 | -0.087792 | 0.99398 | -0.11443 | 16.9593
72 | -0.15449 | -0.039192 | 0.15457 | 0.039245 | 8.3702e-05 | 5.2741e-05 | 0.23396 | 0.23396 | 0.23396 | 0.98327 | -0.31959 | 0.98385 | -0.30833 | 16.0687
73 | 0.02509 | 0.0063309 | -0.025074 | -0.0063213 | 1.5577e-05 | 9.6027e-06 | 0.037937 | 0.037937 | 0.037937 | 0.98451 | -0.29731 | 0.98384 | -0.31028 | 10.4222
74 | 0.10471 | 0.026401 | -0.10458 | -0.026316 | 0.00013288 | 8.486e-05 | 0.15812 | 0.15812 | 0.15812 | 0.98574 | -0.27334 | 0.98438 | -0.29989 | 43.4405
75 | -0.023305 | -0.005873 | 0.023318 | 0.0058812 | 1.342e-05 | 8.2237e-06 | 0.035281 | 0.035281 | 0.035281 | 0.98322 | -0.32231 | 0.98384 | -0.31028 | 9.6927
76 | -0.014676 | -0.0036784 | 0.014681 | 0.0036811 | 4.7756e-06 | 2.7311e-06 | 0.022248 | 0.022248 | 0.022248 | 0.98159 | -0.3542 | 0.98194 | -0.34737 | 6.112
77 | 0.01198 | 0.0030027 | -0.011979 | -0.0030023 | 8.634e-07 | 4.6434e-07 | 0.018161 | 0.018161 | 0.018161 | 0.98159 | -0.3542 | 0.98152 | -0.35571 | 4.9893
78 | -0.019367 | -0.0048555 | 0.019372 | 0.0048589 | 5.5595e-06 | 3.3403e-06 | 0.029349 | 0.029348 | 0.029349 | 0.98194 | -0.34737 | 0.98225 | -0.34135 | 8.0628
79 | -0.059279 | -0.014896 | 0.05935 | 0.014941 | 7.0307e-05 | 4.4702e-05 | 0.089817 | 0.089817 | 0.089817 | 0.98225 | -0.34135 | 0.98352 | -0.31654 | 24.6749
80 | 0.039907 | 0.010037 | -0.039832 | -0.0099897 | 7.5229e-05 | 4.7453e-05 | 0.060468 | 0.060469 | 0.060469 | 0.98225 | -0.34135 | 0.98023 | -0.38089 | 16.6123
81 | -0.063859 | -0.016071 | 0.063909 | 0.016103 | 5.0846e-05 | 3.2357e-05 | 0.096638 | 0.096638 | 0.096638 | 0.98352 | -0.31654 | 0.98438 | -0.29989 | 26.549
82 | 0.036573 | 0.009173 | -0.036569 | -0.0091701 | 4.5193e-06 | 2.8431e-06 | 0.055522 | 0.055522 | 0.055522 | 0.98023 | -0.38089 | 0.9801 | -0.38349 | 15.2532
83 | 0.04067 | 0.010213 | -0.040625 | -0.010185 | 4.48e-05 | 2.8271e-05 | 0.061485 | 0.061485 | 0.061485 | 0.98438 | -0.29989 | 0.98319 | -0.323 | 16.8916
84 | 0.034349 | 0.0086138 | -0.034332 | -0.0086034 | 1.6644e-05 | 1.0446e-05 | 0.052152 | 0.052152 | 0.052152 | 0.9801 | -0.38349 | 0.97958 | -0.39366 | 14.3274
85 | 0.008015 | 0.0020088 | -0.0080131 | -0.002008 | 1.8776e-06 | 7.5593e-07 | 0.012032 | 0.012032 | 0.012032 | 0.99126 | -0.16716 | 0.991 | -0.17208 | 3.3054
86 | -0.011121 | -0.0027873 | 0.011128 | 0.0027907 | 6.562e-06 | 3.3898e-06 | 0.016694 | 0.016694 | 0.016694 | 0.99126 | -0.16716 | 0.9919 | -0.15478 | 4.5864
87 | 0.0026376 | 0.00066083 | -0.0026375 | -0.00066102 | 1.2432e-07 | -1.9274e-07 | 0.0039604 | 0.0039605 | 0.0039605 | 0.991 | -0.17208 | 0.99095 | -0.17307 | 1.088
88 | 0.01451 | 0.0036375 | -0.014507 | -0.0036356 | 3.2937e-06 | 1.8688e-06 | 0.021768 | 0.021769 | 0.021769 | 0.9919 | -0.15478 | 0.99165 | -0.15955 | 5.9804
89 | -0.025638 | -0.0064282 | 0.025665 | 0.0064445 | 2.6493e-05 | 1.6338e-05 | 0.038463 | 0.038462 | 0.038463 | 0.9919 | -0.15478 | 0.99302 | -0.13312 | 10.5666
90 | 0.0024186 | 0.00060596 | -0.0024185 | -0.00060613 | 8.7438e-08 | -1.7243e-07 | 0.0036291 | 0.0036292 | 0.0036292 | 0.99165 | -0.15955 | 0.99161 | -0.16031 | 0.99703
91 | -0.025665 | -0.0064445 | 0.025676 | 0.0064517 | 1.1585e-05 | 7.1441e-06 | 0.038462 | 0.038462 | 0.038462 | 0.99302 | -0.13312 | 0.99351 | -0.12366 | 10.5666
92 | 0.027715 | 0.0069644 | -0.027713 | -0.0069631 | 2.0993e-06 | 1.3015e-06 | 0.041509 | 0.041509 | 0.041509 | 0.99368 | -0.12021 | 0.9936 | -0.1218 | 11.4036
93 | -0.027715 | -0.0069644 | 0.027723 | 0.0069691 | 7.6456e-06 | 4.7398e-06 | 0.041509 | 0.041509 | 0.041509 | 0.99368 | -0.12021 | 0.99398 | -0.11443 | 11.4036
94 | 0.027713 | 0.0069631 | -0.027711 | -0.0069615 | 2.4685e-06 | 1.5303e-06 | 0.041509 | 0.041509 | 0.041509 | 0.9936 | -0.1218 | 0.99351 | -0.12366 | 11.4037
95 | 0.012378 | 0.0031028 | -0.012377 | -0.0031023 | 8.2867e-07 | 4.4738e-07 | 0.018555 | 0.018555 | 0.018555 | 0.99265 | -0.13981 | 0.99257 | -0.14122 | 5.0975
96 | 0.023346 | 0.0058546 | -0.023342 | -0.0058518 | 4.5363e-06 | 2.7804e-06 | 0.035335 | 0.035335 | 0.035335 | 0.98319 | -0.323 | 0.98299 | -0.32708 | 9.7074
97 | 0.017052 | 0.0042755 | -0.017048 | -0.004273 | 4.2397e-06 | 2.4984e-06 | 0.025814 | 0.025814 | 0.025814 | 0.98299 | -0.32708 | 0.98272 | -0.3323 | 7.0917
98 | 0.030078 | 0.007537 | -0.030077 | -0.0075367 | 5.1361e-07 | 3.2045e-07 | 0.045689 | 0.045689 | 0.045689 | 0.97958 | -0.39366 | 0.97956 | -0.39402 | 12.5519
99 | 0.024153 | 0.006052 | -0.024146 | -0.0060476 | 7.2226e-06 | 4.4424e-06 | 0.03669 | 0.03669 | 0.03669 | 0.97956 | -0.39402 | 0.97924 | -0.4003 | 10.0796
100 | 0.017595 | 0.0044059 | -0.01759 | -0.0044027 | 5.3204e-06 | 3.1554e-06 | 0.026736 | 0.026736 | 0.026736 | 0.97924 | -0.4003 | 0.97892 | -0.40665 | 7.3451
101 | 0.0080871 | 0.002021 | -0.0080791 | -0.0020177 | 8.0733e-06 | 3.3773e-06 | 0.012291 | 0.012292 | 0.012292 | 0.97892 | -0.40665 | 0.97785 | -0.42767 | 3.3768
102 | 0.013949 | 0.0034964 | -0.013949 | -0.003496 | 6.6872e-07 | 3.7734e-07 | 0.021122 | 0.021122 | 0.021122 | 0.98272 | -0.3323 | 0.98267 | -0.33331 | 5.8028
103 | 0.00937 | 0.0023485 | -0.0093684 | -0.0023477 | 1.6362e-06 | 7.7264e-07 | 0.014189 | 0.014189 | 0.014189 | 0.98267 | -0.33331 | 0.98248 | -0.33697 | 3.898
104 | 0.0077887 | 0.0019518 | -0.0077882 | -0.0019516 | 4.6308e-07 | 1.84e-07 | 0.011796 | 0.011796 | 0.011796 | 0.98248 | -0.33697 | 0.98242 | -0.33822 | 3.2407
105 | 0.0038476 | 0.00096402 | -0.0038474 | -0.00096413 | 2.8468e-07 | -1.008e-07 | 0.0058277 | 0.0058278 | 0.0058278 | 0.98242 | -0.33822 | 0.98234 | -0.33977 | 1.6011
106 | 0.0090092 | 0.0022584 | -0.0090071 | -0.0022574 | 2.0988e-06 | 9.4677e-07 | 0.013506 | 0.013507 | 0.013507 | 0.99257 | -0.14122 | 0.99232 | -0.14611 | 3.7106
107 | 0.0015733 | 0.0003942 | -0.0015733 | -0.00039431 | 2.0618e-08 | -1.0935e-07 | 0.0023832 | 0.0023833 | 0.0023833 | 0.98234 | -0.33977 | 0.98232 | -0.34005 | 0.65474

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56171 | 0.14357

## res_load
| p_mw | q_mvar
0 | 0.0045285 | 0.0011349
1 | 0.0030167 | 0.00075606
2 | 0.0039284 | 0.00098455
3 | 0.00040161 | 0.00010065
4 | 0.0015973 | 0.00040032
5 | 0.00053495 | 0.00013407
6 | 0.0010597 | 0.00026559
7 | 0.0023364 | 0.00058556
8 | 0.0012283 | 0.00030784
9 | 0.0017469 | 0.00043782
10 | 0.0027837 | 0.00069767
11 | 0.057615 | 0.01444
12 | 0.018284 | 0.0045823
13 | 0.018686 | 0.0046833
14 | 0.022442 | 0.0056245
15 | 0.0088107 | 0.0022082
16 | 0.0072276 | 0.0018114
17 | 0.0029277 | 0.00073376
18 | 0.0076229 | 0.0019105
19 | 0.001573 | 0.00039422
20 | 0.0013405 | 0.00033597
21 | 0.0039704 | 0.00099508
22 | 0.0037611 | 0.00094263
23 | 0.023309 | 0.0058419
24 | 0.032477 | 0.0081395
25 | 0.016812 | 0.0042136
26 | 0.00089132 | 0.00022339
27 | 0.0015031 | 0.00037672
28 | 0.0088529 | 0.0022187
29 | 0.018294 | 0.004585
30 | 0.0063365 | 0.0015881
31 | 0.0016869 | 0.00042277
32 | 0.010871 | 0.0027245
33 | 0.0050205 | 0.0012583
34 | 0.0082424 | 0.0020657
35 | 0.0039486 | 0.00098961
36 | 0.0050777 | 0.0012726
37 | 0.0028162 | 0.00070582
38 | 0.018685 | 0.004683
39 | 0.018285 | 0.0045827
40 | 0.020589 | 0.00516
41 | 0.0048515 | 0.0012159
42 | 0.0016399 | 0.00041101
43 | 0.002696 | 0.00067569
44 | 0.0046858 | 0.0011744
45 | 0.011979 | 0.0030023
46 | 0.0045088 | 0.00113
47 | 0.0032587 | 0.00081672
48 | 0.0022197 | 0.0005563
49 | 0.0031061 | 0.00077846
50 | 0.0053755 | 0.0013472
51 | 0.0026375 | 0.00066102
52 | 0.012089 | 0.0030297
53 | 0.0024185 | 0.00060613
54 | 0.013509 | 0.0033856
55 | 0.0020344 | 0.00050988
56 | 0.0046165 | 0.001157
57 | 0.017279 | 0.0043305
58 | 0.0062895 | 0.0015763
59 | 0.0042547 | 0.0010663
60 | 0.0059241 | 0.0014847
61 | 0.0065504 | 0.0016417
62 | 0.009503 | 0.0023817
63 | 0.0017558 | 0.00044005
64 | 0.0067553 | 0.001693
65 | 0.0030986 | 0.00077659
66 | 0.0045787 | 0.0011475
67 | 0.0015797 | 0.0003959
68 | 0.0039406 | 0.0009876
69 | 0.0033675 | 0.00084397
70 | 0.0011688 | 0.00029292
71 | 0.002274 | 0.00056992
72 | 0.0015733 | 0.00039431
73 | 0.0090071 | 0.0022574

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1