## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1058-34_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1058-34_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1058-34_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1058-34_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1058-34_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1058-34_0_5_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1058-34_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1058-34_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1058-34_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1058-34_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1058-34_0_5_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1058-34_0_5_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_1058-34_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1058-34_0_5_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1058-34_0_5_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1058-34_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1058-34_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1058-34_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1058-34_0_5_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1058-34_0_5_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1058-34_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1058-34_0_5_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1058-34_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1058-34_0_5_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1058-34_0_5_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1058-34_0_5_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1058-34_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1058-34_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_MV_23_0_node_188 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1058-34_0_5_load_0 | 0 | 0.058968 | 0.014779 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1058-34_0_5_load_1 | 1 | 0.056514 | 0.014164 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1058-34_0_5_load_3 | 3 | 0.032552 | 0.0081582 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1058-34_0_5_load_13 | 7 | 0.014843 | 0.0037201 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1058-34_0_5_load_20 | 9 | 0.033537 | 0.0084051 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1058-34_0_5_load_27 | 10 | 0.034067 | 0.0085381 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1058-34_0_5_load_28 | 11 | 0.016807 | 0.0042122 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1058-34_0_5_load_19 | 13 | 0.084303 | 0.021128 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1058-34_0_5_load_17 | 14 | 0.031604 | 0.0079207 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1058-34_0_5_load_21 | 18 | 0.0015909 | 0.00039872 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1058-34_0_5_load_26 | 19 | 0.033074 | 0.0082891 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1058-34_0_5_load_16 | 21 | 0.013694 | 0.0034321 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1058-34_0_5_load_18 | 22 | 0.054869 | 0.013752 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1058-34_0_5_load_22 | 23 | 0.0059983 | 0.0015033 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1058-34_0_5_load_24 | 24 | 0.0011374 | 0.00028505 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1058-34_0_5_load_25 | 25 | 0.0013524 | 0.00033895 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1058-34_0_5_load_23 | 26 | 0.0049998 | 0.0012531 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1058-34_0_5_load_15 | 27 | 0.012792 | 0.0032059 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1058-34_0_5_line_0 |  | 0 | 1 | 0.030006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1058-34_0_5_line_1 |  | 0 | 2 | 0.016675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1058-34_0_5_line_2 |  | 1 | 3 | 0.020361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1058-34_0_5_line_3 |  | 2 | 4 | 0.004139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_1058-34_0_5_line_4 |  | 3 | 5 | 0.036829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1058-34_0_5_line_5 |  | 4 | 6 | 0.29606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1058-34_0_5_line_6 |  | 4 | 7 | 0.017095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1058-34_0_5_line_7 |  | 5 | 16 | 0.031417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1058-34_0_5_line_8 |  | 5 | 15 | 0.03951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1058-34_0_5_line_9 |  | 6 | 11 | 0.02095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1058-34_0_5_line_10 |  | 7 | 20 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1058-34_0_5_line_11 |  | 8 | 9 | 0.017766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1058-34_0_5_line_12 |  | 8 | 10 | 0.030765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1058-34_0_5_line_13 |  | 9 | 21 | 0.028101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1058-34_0_5_line_14 |  | 12 | 13 | 0.040889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1058-34_0_5_line_15 |  | 12 | 14 | 0.042948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1058-34_0_5_line_16 |  | 13 | 15 | 0.057045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1058-34_0_5_line_17 |  | 14 | 22 | 0.0041065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1058-34_0_5_line_18 |  | 16 | 19 | 0.02471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1058-34_0_5_line_19 |  | 16 | 17 | 0.11256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1058-34_0_5_line_20 |  | 17 | 18 | 0.022875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1058-34_0_5_line_21 |  | 18 | 23 | 0.041477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1058-34_0_5_line_22 |  | 19 | 24 | 0.028578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1058-34_0_5_line_23 |  | 20 | 27 | 0.058798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1058-34_0_5_line_24 |  | 20 | 21 | 0.028088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1058-34_0_5_line_25 |  | 24 | 26 | 0.090887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1058-34_0_5_line_26 |  | 25 | 26 | 0.00058037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1058-34_0_5_trafo_5 | 0.63 MVA 20/0.4 kV | 28 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2665864.2746 | 1206920.1716 | 2665869.6495 | 1206923.8983 | 2665882.5224 | 1206930.9557 | 2665890.6791 | 1206934.2194
1 | 2665855.5938 | 1206906.1769 | 2665862.4799 | 1206918.9273 | 2665864.2746 | 1206920.1716
2 | 2665890.6791 | 1206934.2194 | 2665894.6666 | 1206935.8149 | 2665910.2054 | 1206939.8993
3 | 2665856.5584 | 1206902.1518 | 2665855.5938 | 1206906.1769
4 | 2665944.2112 | 1206951.638 | 2665939.8582 | 1206947.7876 | 2665937.4372 | 1206946.6602 | 2665934.3893 | 1206945.826 | 2665919.6635 | 1206944.0513 | 2665911.8414 | 1206940.3294 | 2665910.2054 | 1206939.8993
5 | 2665717.6886 | 1206966.3832 | 2665716.6729 | 1206969.5407 | 2665736.1305 | 1206987.7325 | 2665741.3963 | 1206990.8702 | 2665745.563 | 1206992.3058 | 2665746.0046 | 1206997.7807 | 2665788.59 | 1207011.6136 | 2665808.9036 | 1206945.9308 | 2665835.3121 | 1206864.1166 | 2665842.2222 | 1206866.4275 | 2665838.177 | 1206880.8584 | 2665848.7091 | 1206895.3722 | 2665856.5584 | 1206902.1518
6 | 2665856.5584 | 1206902.1518 | 2665860.5386 | 1206885.5271
7 | 2665944.2112 | 1206951.638 | 2665947.9754 | 1206945.4536 | 2665951.2631 | 1206939.7198 | 2665954.3415 | 1206934.3505 | 2665956.7471 | 1206928.618 | 2665958.7465 | 1206923.8594
8 | 2665944.2112 | 1206951.638 | 2665935.4958 | 1206965.4502 | 2665925.8843 | 1206980.5199 | 2665922.7492 | 1206984.8324
9 | 2665717.6886 | 1206966.3832 | 2665719.9409 | 1206959.3593 | 2665721.0969 | 1206946.92 | 2665721.1015 | 1206945.8388
10 | 2665864.4589 | 1206869.1522 | 2665860.5386 | 1206885.5271
11 | 2665888.2557 | 1206922.7473 | 2665891.2853 | 1206905.2413
12 | 2665888.2557 | 1206922.7473 | 2665894.6872 | 1206925.6867 | 2665904.7125 | 1206928.9215 | 2665911.9743 | 1206930.3581 | 2665917.6723 | 1206931.1792
13 | 2665891.2853 | 1206905.2413 | 2665893.17 | 1206894.3509 | 2665890.3131 | 1206879.666 | 2665888.8503 | 1206878.1757
14 | 2665860.6835 | 1207006.5941 | 2665869.7093 | 1206966.7139
15 | 2665860.6835 | 1207006.5941 | 2665855.3929 | 1207002.2665 | 2665854.1714 | 1206997.8726 | 2665853.1287 | 1206990.3676 | 2665851.3638 | 1206985.6008 | 2665847.0828 | 1206981.4288 | 2665843.9485 | 1206979.4709 | 2665842.6421 | 1206975.8765 | 2665843.5471 | 1206970.5589
16 | 2665922.7492 | 1206984.8324 | 2665879.6195 | 1206965.9005 | 2665869.7093 | 1206966.7139
17 | 2665844.236 | 1206966.5106 | 2665843.5471 | 1206970.5589
18 | 2665958.7465 | 1206923.8594 | 2665959.6307 | 1206918.855 | 2665959.9376 | 1206912.4212 | 2665958.3601 | 1206899.3292
19 | 2665958.7465 | 1206923.8594 | 2665956.7471 | 1206928.618 | 2665957.8597 | 1206929.0973 | 2665960.925 | 1206930.4208 | 2665962.9072 | 1206925.8399 | 2665963.9934 | 1206914.256 | 2665962.6742 | 1206898.7542 | 2665953.3492 | 1206828.7086
20 | 2665953.3492 | 1206828.7086 | 2665930.5608 | 1206830.6937
21 | 2665889.2398 | 1206834.2932 | 2665930.5608 | 1206830.6937
22 | 2665958.3601 | 1206899.3292 | 2665957.9872 | 1206896.2342 | 2665954.9687 | 1206874.8435 | 2665954.4244 | 1206871.0242
23 | 2665864.4589 | 1206869.1522 | 2665880.4913 | 1206812.5825
24 | 2665864.4589 | 1206869.1522 | 2665870.312 | 1206868.0049 | 2665880.958 | 1206870.1348 | 2665888.8503 | 1206878.1757
25 | 2665942.3737 | 1206780.9427 | 2665944.8048 | 1206800.864 | 2665949.4426 | 1206836.07 | 2665954.4244 | 1206871.0242
26 | 2665942.3737 | 1206780.9427 | 2665942.3034 | 1206780.3666

## bus_geodata
| x | y | coords
0 | 2665864.2746 | 1206920.1716
1 | 2665890.6791 | 1206934.2194
2 | 2665855.5938 | 1206906.1769
3 | 2665910.2054 | 1206939.8993
4 | 2665856.5584 | 1206902.1518
5 | 2665944.2112 | 1206951.638
6 | 2665717.6886 | 1206966.3832
7 | 2665860.5386 | 1206885.5271
8 | 2665888.2557 | 1206922.7473
9 | 2665891.2853 | 1206905.2413
10 | 2665917.6723 | 1206931.1792
11 | 2665721.1015 | 1206945.8388
12 | 2665860.6835 | 1207006.5941
13 | 2665869.7093 | 1206966.7139
14 | 2665843.5471 | 1206970.5589
15 | 2665922.7492 | 1206984.8324
16 | 2665958.7465 | 1206923.8594
17 | 2665953.3492 | 1206828.7086
18 | 2665930.5608 | 1206830.6937
19 | 2665958.3601 | 1206899.3292
20 | 2665864.4589 | 1206869.1522
21 | 2665888.8503 | 1206878.1757
22 | 2665844.236 | 1206966.5106
23 | 2665889.2398 | 1206834.2932
24 | 2665954.4244 | 1206871.0242
25 | 2665942.3034 | 1206780.3666
26 | 2665942.3737 | 1206780.9427
27 | 2665880.4913 | 1206812.5825
28 | 2665887.6462 | 1206926.2872

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98785 | -0.23187 | 0.058968 | 0.014779
1 | 0.98571 | -0.27323 | 0.056514 | 0.014164
2 | 0.98927 | -0.20458 | 0 | 0
3 | 0.98452 | -0.29623 | 0.032552 | 0.0081582
4 | 0.98962 | -0.19782 | 0 | 0
5 | 0.98265 | -0.33255 | 0 | 0
6 | 0.98503 | -0.28682 | 0 | 0
7 | 0.99113 | -0.16867 | 0.014843 | 0.0037201
8 | 1 | 0 | -0.50154 | -0.12806
9 | 0.99812 | -0.035577 | 0.033537 | 0.0084051
10 | 0.99905 | -0.018285 | 0.034067 | 0.0085381
11 | 0.98471 | -0.29315 | 0.016807 | 0.0042122
12 | 0.97717 | -0.43947 | 0 | 0
13 | 0.97882 | -0.40725 | 0.084303 | 0.021128
14 | 0.97371 | -0.5075 | 0.031604 | 0.0079207
15 | 0.98108 | -0.36304 | 0 | 0
16 | 0.98125 | -0.3599 | 0 | 0
17 | 0.98046 | -0.37538 | 0 | 0
18 | 0.9803 | -0.37853 | 0.0015909 | 0.00039872
19 | 0.98032 | -0.37806 | 0.033074 | 0.0082891
20 | 0.99269 | -0.13895 | 0 | 0
21 | 0.99536 | -0.087977 | 0.013694 | 0.0034321
22 | 0.9735 | -0.51164 | 0.054869 | 0.013752
23 | 0.98007 | -0.38304 | 0.0059983 | 0.0015033
24 | 0.98013 | -0.38194 | 0.0011374 | 0.00028505
25 | 0.97959 | -0.39244 | 0.0013524 | 0.00033895
26 | 0.97959 | -0.39243 | 0.0049998 | 0.0012531
27 | 0.992 | -0.15226 | 0.012792 | 0.0032059
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.31042 | 0.07873 | -0.30981 | -0.078338 | 0.00061596 | 0.00039268 | 0.46793 | 0.46793 | 0.46793 | 0.98785 | -0.23187 | 0.98571 | -0.27323 | 32.1382
1 | -0.36939 | -0.093509 | 0.36988 | 0.093818 | 0.00048458 | 0.00030927 | 0.55676 | 0.55676 | 0.55676 | 0.98785 | -0.23187 | 0.98927 | -0.20458 | 38.2387
2 | 0.25329 | 0.064174 | -0.25301 | -0.063996 | 0.00027945 | 0.00017781 | 0.38262 | 0.38262 | 0.38262 | 0.98571 | -0.27323 | 0.98452 | -0.29623 | 26.2787
3 | -0.36988 | -0.093818 | 0.37 | 0.093895 | 0.00012028 | 7.6767e-05 | 0.55676 | 0.55676 | 0.55676 | 0.98927 | -0.20458 | 0.98962 | -0.19782 | 38.2387
4 | 0.22046 | 0.055838 | -0.22008 | -0.055594 | 0.00038383 | 0.00024378 | 0.33342 | 0.33342 | 0.33342 | 0.98452 | -0.29623 | 0.98265 | -0.33255 | 22.8997
5 | 0.016884 | 0.0042573 | -0.016812 | -0.0042152 | 7.1609e-05 | 4.2043e-05 | 0.025396 | 0.025397 | 0.025397 | 0.98962 | -0.19782 | 0.98503 | -0.28682 | 6.9773
6 | -0.38688 | -0.098153 | 0.38742 | 0.098499 | 0.00054312 | 0.00034672 | 0.58215 | 0.58215 | 0.58215 | 0.98962 | -0.19782 | 0.99113 | -0.16867 | 39.9829
7 | 0.048263 | 0.012135 | -0.0482 | -0.012095 | 6.2952e-05 | 3.9892e-05 | 0.073098 | 0.073099 | 0.073099 | 0.98265 | -0.33255 | 0.98125 | -0.3599 | 20.082
8 | 0.17182 | 0.043459 | -0.17157 | -0.043301 | 0.00025102 | 0.00015865 | 0.26032 | 0.26032 | 0.26032 | 0.98265 | -0.33255 | 0.98108 | -0.36304 | 17.8793
9 | 0.016812 | 0.0042152 | -0.016807 | -0.0042122 | 5.0676e-06 | 2.9767e-06 | 0.025397 | 0.025398 | 0.025398 | 0.98503 | -0.28682 | 0.98471 | -0.29315 | 6.9773
10 | -0.40227 | -0.10222 | 0.40284 | 0.10259 | 0.0005767 | 0.00036822 | 0.60444 | 0.60444 | 0.60444 | 0.99113 | -0.16867 | 0.99269 | -0.13895 | 41.5134
11 | 0.4658 | 0.1195 | -0.46499 | -0.11899 | 0.00080241 | 0.00051261 | 0.69409 | 0.69409 | 0.69409 | 1 | 0 | 0.99812 | -0.035577 | 47.6711
12 | 0.034097 | 0.0085567 | -0.034067 | -0.0085381 | 2.9703e-05 | 1.8607e-05 | 0.050741 | 0.050741 | 0.050741 | 1 | 0 | 0.99905 | -0.018285 | 13.9398
13 | 0.43146 | 0.11058 | -0.43036 | -0.10988 | 0.0010929 | 0.000698 | 0.64409 | 0.64409 | 0.64409 | 0.99812 | -0.035577 | 0.99536 | -0.087977 | 44.2373
14 | -0.086765 | -0.021859 | 0.086899 | 0.021943 | 0.00013392 | 8.4681e-05 | 0.13216 | 0.13216 | 0.13216 | 0.97717 | -0.43947 | 0.97882 | -0.40725 | 18.1545
15 | 0.086765 | 0.021859 | -0.086484 | -0.021679 | 0.00028132 | 0.00017951 | 0.13216 | 0.13216 | 0.13216 | 0.97717 | -0.43947 | 0.97371 | -0.5075 | 36.3091
16 | -0.1712 | -0.043072 | 0.17157 | 0.043301 | 0.00036242 | 0.00022908 | 0.26032 | 0.26032 | 0.26032 | 0.97882 | -0.40725 | 0.98108 | -0.36304 | 17.8794
17 | 0.05488 | 0.013758 | -0.054869 | -0.013752 | 1.0832e-05 | 6.8813e-06 | 0.083868 | 0.083868 | 0.083868 | 0.97371 | -0.5075 | 0.9735 | -0.51164 | 23.0408
18 | 0.040603 | 0.01019 | -0.040568 | -0.010168 | 3.5135e-05 | 2.2175e-05 | 0.061577 | 0.061577 | 0.061577 | 0.98125 | -0.3599 | 0.98032 | -0.37806 | 16.9169
19 | 0.0075973 | 0.0019049 | -0.0075916 | -0.0019028 | 5.603e-06 | 2.1653e-06 | 0.011521 | 0.011522 | 0.011522 | 0.98125 | -0.3599 | 0.98046 | -0.37538 | 3.1653
20 | 0.0075916 | 0.0019028 | -0.0075905 | -0.0019023 | 1.1387e-06 | 4.4035e-07 | 0.011522 | 0.011522 | 0.011522 | 0.98046 | -0.37538 | 0.9803 | -0.37853 | 3.1653
21 | 0.0059996 | 0.0015036 | -0.0059983 | -0.0015033 | 1.29e-06 | 3.0281e-07 | 0.0091069 | 0.0091071 | 0.0091071 | 0.9803 | -0.37853 | 0.98007 | -0.38304 | 2.502
22 | 0.0074942 | 0.0018785 | -0.0074928 | -0.001878 | 1.3867e-06 | 5.2728e-07 | 0.011375 | 0.011375 | 0.011375 | 0.98032 | -0.37806 | 0.98013 | -0.38194 | 3.1251
23 | 0.0128 | 0.0032104 | -0.012792 | -0.0032059 | 8.1179e-06 | 4.4358e-06 | 0.019188 | 0.019188 | 0.019188 | 0.99269 | -0.13895 | 0.992 | -0.15226 | 5.2714
24 | -0.41564 | -0.1058 | 0.41667 | 0.10645 | 0.0010241 | 0.00065397 | 0.62362 | 0.62362 | 0.62362 | 0.99269 | -0.13895 | 0.99536 | -0.087977 | 42.8312
25 | 0.0063554 | 0.0015929 | -0.0063523 | -0.001592 | 3.1732e-06 | 8.8601e-07 | 0.0096488 | 0.0096492 | 0.0096492 | 0.98013 | -0.38194 | 0.97959 | -0.39243 | 2.6509
26 | -0.0013524 | -0.00033895 | 0.0013524 | 0.00033894 | 9.1837e-10 | -6.7186e-09 | 0.0020544 | 0.0020544 | 0.0020544 | 0.97959 | -0.39244 | 0.97959 | -0.39243 | 0.56439

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50154 | 0.12806

## res_load
| p_mw | q_mvar
0 | 0.058968 | 0.014779
1 | 0.056514 | 0.014164
2 | 0.032552 | 0.0081582
3 | 0.014843 | 0.0037201
4 | 0.033537 | 0.0084051
5 | 0.034067 | 0.0085381
6 | 0.016807 | 0.0042122
7 | 0.084303 | 0.021128
8 | 0.031604 | 0.0079207
9 | 0.0015909 | 0.00039872
10 | 0.033074 | 0.0082891
11 | 0.013694 | 0.0034321
12 | 0.054869 | 0.013752
13 | 0.0059983 | 0.0015033
14 | 0.0011374 | 0.00028505
15 | 0.0013524 | 0.00033895
16 | 0.0049998 | 0.0012531
17 | 0.012792 | 0.0032059

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1