## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1058-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1058-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1058-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1058-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1058-7_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1058-7_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1058-7_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1058-7_0_3_node_53 | 0.4 | n |  | TRUE
8 | bus_LV_1058-7_0_3_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_1058-7_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1058-7_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1058-7_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1058-7_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1058-7_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1058-7_0_3_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1058-7_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1058-7_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1058-7_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1058-7_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1058-7_0_3_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1058-7_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1058-7_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1058-7_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1058-7_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1058-7_0_3_node_72 | 0.4 | n |  | TRUE
25 | bus_LV_1058-7_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1058-7_0_3_node_98 | 0.4 | n |  | TRUE
27 | bus_LV_1058-7_0_3_node_97 | 0.4 | n |  | TRUE
28 | bus_LV_1058-7_0_3_node_94 | 0.4 | n |  | TRUE
29 | bus_LV_1058-7_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1058-7_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1058-7_0_3_node_50 | 0.4 | n |  | TRUE
32 | bus_LV_1058-7_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1058-7_0_3_node_59 | 0.4 | n |  | TRUE
34 | bus_LV_1058-7_0_3_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_1058-7_0_3_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_1058-7_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1058-7_0_3_node_99 | 0.4 | n |  | TRUE
38 | bus_LV_1058-7_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1058-7_0_3_node_106 | 0.4 | n |  | TRUE
40 | bus_LV_1058-7_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1058-7_0_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1058-7_0_3_node_105 | 0.4 | n |  | TRUE
43 | bus_LV_1058-7_0_3_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1058-7_0_3_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_1058-7_0_3_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_1058-7_0_3_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1058-7_0_3_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1058-7_0_3_node_92 | 0.4 | n |  | TRUE
49 | bus_LV_1058-7_0_3_node_24 | 0.4 | n |  | TRUE
50 | bus_LV_1058-7_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_1058-7_0_3_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_1058-7_0_3_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_1058-7_0_3_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_1058-7_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1058-7_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_1058-7_0_3_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_1058-7_0_3_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_1058-7_0_3_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_1058-7_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_1058-7_0_3_node_30 | 0.4 | n |  | TRUE
61 | bus_LV_1058-7_0_3_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1058-7_0_3_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_1058-7_0_3_node_120 | 0.4 | n |  | TRUE
64 | bus_LV_1058-7_0_3_node_121 | 0.4 | n |  | TRUE
65 | bus_LV_1058-7_0_3_node_114 | 0.4 | n |  | TRUE
66 | bus_LV_1058-7_0_3_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_1058-7_0_3_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_1058-7_0_3_node_51 | 0.4 | n |  | TRUE
69 | bus_LV_1058-7_0_3_node_68 | 0.4 | n |  | TRUE
70 | bus_LV_1058-7_0_3_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_1058-7_0_3_node_113 | 0.4 | n |  | TRUE
72 | bus_LV_1058-7_0_3_node_112 | 0.4 | n |  | TRUE
73 | bus_LV_1058-7_0_3_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_1058-7_0_3_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_1058-7_0_3_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_1058-7_0_3_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_1058-7_0_3_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_1058-7_0_3_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_1058-7_0_3_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_1058-7_0_3_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_1058-7_0_3_node_81 | 0.4 | n |  | TRUE
82 | bus_LV_1058-7_0_3_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_1058-7_0_3_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_1058-7_0_3_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_1058-7_0_3_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_1058-7_0_3_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_1058-7_0_3_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_1058-7_0_3_node_100 | 0.4 | n |  | TRUE
89 | bus_LV_1058-7_0_3_node_118 | 0.4 | n |  | TRUE
90 | bus_LV_1058-7_0_3_node_102 | 0.4 | n |  | TRUE
91 | bus_LV_1058-7_0_3_node_101 | 0.4 | n |  | TRUE
92 | bus_LV_1058-7_0_3_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_1058-7_0_3_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_1058-7_0_3_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_1058-7_0_3_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_1058-7_0_3_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_1058-7_0_3_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_1058-7_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_1058-7_0_3_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_1058-7_0_3_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_1058-7_0_3_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_1058-7_0_3_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_1058-7_0_3_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_1058-7_0_3_node_109 | 0.4 | n |  | TRUE
105 | bus_LV_1058-7_0_3_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_1058-7_0_3_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_1058-7_0_3_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_1058-7_0_3_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_1058-7_0_3_node_82 | 0.4 | n |  | TRUE
110 | bus_LV_1058-7_0_3_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_1058-7_0_3_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_1058-7_0_3_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_1058-7_0_3_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_1058-7_0_3_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_1058-7_0_3_node_119 | 0.4 | n |  | TRUE
116 | bus_LV_1058-7_0_3_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_1058-7_0_3_node_115 | 0.4 | n |  | TRUE
118 | bus_LV_1058-7_0_3_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_1058-7_0_3_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_1058-7_0_3_node_110 | 0.4 | n |  | TRUE
121 | bus_MV_23_0_node_177 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1058-7_0_3_load_0 | 0 | 0.0019308 | 0.0004839 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1058-7_0_3_load_1 | 1 | 0.0044913 | 0.0011256 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1058-7_0_3_load_2 | 2 | 0.0077665 | 0.0019465 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1058-7_0_3_load_3 | 3 | 0.0014799 | 0.0003709 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1058-7_0_3_load_4 | 4 | 0.0038232 | 0.00095819 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1058-7_0_3_load_5 | 5 | 0.00060378 | 0.00015132 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1058-7_0_3_load_6 | 6 | 0.00049354 | 0.00012369 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1058-7_0_3_load_53 | 7 | 0.0039363 | 0.00098652 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1058-7_0_3_load_52 | 8 | 0.0032698 | 0.00081948 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1058-7_0_3_load_7 | 9 | 0.0024402 | 0.00061156 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1058-7_0_3_load_12 | 14 | 0.0019379 | 0.00048567 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1058-7_0_3_load_15 | 16 | 0.0024328 | 0.00060971 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1058-7_0_3_load_18 | 18 | 0.0030511 | 0.00076468 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1058-7_0_3_load_19 | 19 | 0.0021933 | 0.0005497 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1058-7_0_3_load_20 | 20 | 0.0021933 | 0.0005497 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1058-7_0_3_load_21 | 21 | 0.0019396 | 0.0004861 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1058-7_0_3_load_13 | 22 | 0.0041031 | 0.0010283 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1058-7_0_3_load_72 | 24 | 0.0019107 | 0.00047886 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1058-7_0_3_load_97 | 27 | 0.0028238 | 0.00070772 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1058-7_0_3_load_23 | 29 | 0.002842 | 0.00071228 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1058-7_0_3_load_25 | 30 | 0.0012098 | 0.0003032 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1058-7_0_3_load_50 | 31 | 0.00093996 | 0.00023558 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1058-7_0_3_load_59 | 33 | 0.0021064 | 0.00052791 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1058-7_0_3_load_57 | 34 | 0.0048374 | 0.0012124 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1058-7_0_3_load_40 | 35 | 0.0018739 | 0.00046965 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1058-7_0_3_load_99 | 37 | 0.0028237 | 0.00070769 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1058-7_0_3_load_106 | 39 | 0.0025704 | 0.00064421 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1058-7_0_3_load_105 | 42 | 0.002568 | 0.00064359 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1058-7_0_3_load_33 | 46 | 0.0017784 | 0.0004457 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1058-7_0_3_load_29 | 47 | 0.0017765 | 0.00044523 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1058-7_0_3_load_48 | 50 | 0.003657 | 0.00091652 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1058-7_0_3_load_55 | 53 | 0.00039019 | 9.7791e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1058-7_0_3_load_41 | 55 | 0.0025753 | 0.00064542 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1058-7_0_3_load_43 | 57 | 0.00093777 | 0.00023503 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1058-7_0_3_load_44 | 58 | 0.0013427 | 0.00033651 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1058-7_0_3_load_54 | 59 | 0.0016215 | 0.00040639 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1058-7_0_3_load_30 | 60 | 0.0018171 | 0.00045541 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1058-7_0_3_load_45 | 62 | 0.0018171 | 0.00045541 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1058-7_0_3_load_120 | 63 | 0.0025068 | 0.00062826 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1058-7_0_3_load_121 | 64 | 0.0025068 | 0.00062825 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1058-7_0_3_load_114 | 65 | 0.0020899 | 0.00052377 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1058-7_0_3_load_46 | 66 | 0.0012583 | 0.00031535 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1058-7_0_3_load_47 | 67 | 0.0012167 | 0.00030493 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1058-7_0_3_load_51 | 68 | 0.0010865 | 0.00027229 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1058-7_0_3_load_68 | 69 | 0.0026067 | 0.00065331 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1058-7_0_3_load_113 | 71 | 0.0012159 | 0.00030474 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1058-7_0_3_load_112 | 72 | 0.0011039 | 0.00027667 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1058-7_0_3_load_111 | 73 | 0.0035318 | 0.00088516 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1058-7_0_3_load_65 | 75 | 0.0003528 | 8.8421e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1058-7_0_3_load_56 | 76 | 0.0012503 | 0.00031335 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1058-7_0_3_load_58 | 77 | 0.0049011 | 0.0012283 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1058-7_0_3_load_60 | 78 | 0.0016572 | 0.00041532 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1058-7_0_3_load_61 | 79 | 0.0029823 | 0.00074744 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1058-7_0_3_load_80 | 80 | 0.0041775 | 0.001047 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1058-7_0_3_load_81 | 81 | 0.0013074 | 0.00032766 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1058-7_0_3_load_62 | 82 | 0.010952 | 0.0027448 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1058-7_0_3_load_63 | 83 | 0.0021799 | 0.00054632 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1058-7_0_3_load_64 | 84 | 0.0020545 | 0.00051491 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1058-7_0_3_load_66 | 85 | 0.0084058 | 0.0021067 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1058-7_0_3_load_70 | 86 | 0.0034282 | 0.0008592 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1058-7_0_3_load_71 | 87 | 0.0018495 | 0.00046352 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1058-7_0_3_load_100 | 88 | 0.0029807 | 0.00074704 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1058-7_0_3_load_118 | 89 | 0.0027955 | 0.00070063 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1058-7_0_3_load_102 | 90 | 0.0020548 | 0.00051499 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1058-7_0_3_load_101 | 91 | 0.0049592 | 0.0012429 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1058-7_0_3_load_116 | 92 | 0.0019915 | 0.00049911 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1058-7_0_3_load_73 | 93 | 0.0021663 | 0.00054294 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1058-7_0_3_load_74 | 94 | 0.0054077 | 0.0013553 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1058-7_0_3_load_75 | 95 | 0.0018056 | 0.00045253 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1058-7_0_3_load_76 | 96 | 0.00059352 | 0.00014875 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1058-7_0_3_load_78 | 99 | 0.0010721 | 0.0002687 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1058-7_0_3_load_79 | 100 | 0.0026067 | 0.00065329 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1058-7_0_3_load_88 | 101 | 0.0021069 | 0.00052804 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1058-7_0_3_load_83 | 103 | 0.0052448 | 0.0013145 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1058-7_0_3_load_109 | 104 | 0.0036475 | 0.00091416 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1058-7_0_3_load_84 | 105 | 0.0013723 | 0.00034392 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1058-7_0_3_load_85 | 106 | 0.001994 | 0.00049974 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1058-7_0_3_load_87 | 107 | 0.00085672 | 0.00021471 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1058-7_0_3_load_89 | 108 | 0.0062332 | 0.0015622 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1058-7_0_3_load_82 | 109 | 0.0021752 | 0.00054516 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1058-7_0_3_load_107 | 110 | 0.00043888 | 0.00010999 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1058-7_0_3_load_91 | 111 | 0.0032745 | 0.00082067 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1058-7_0_3_load_96 | 114 | 0.0026316 | 0.00065955 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1058-7_0_3_load_119 | 115 | 0.0042834 | 0.0010735 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1058-7_0_3_load_103 | 116 | 0.0047476 | 0.0011899 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1058-7_0_3_load_115 | 117 | 0.0029187 | 0.00073151 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1058-7_0_3_load_104 | 118 | 0.0070567 | 0.0017686 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1058-7_0_3_load_108 | 119 | 0.0019899 | 0.00049871 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1058-7_0_3_load_110 | 120 | 0.0018865 | 0.0004728 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1058-7_0_3_line_0 |  | 0 | 1 | 0.035857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1058-7_0_3_line_1 |  | 0 | 2 | 0.031259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1058-7_0_3_line_2 |  | 1 | 3 | 0.002269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1058-7_0_3_line_3 |  | 2 | 4 | 0.08548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1058-7_0_3_line_4 |  | 2 | 5 | 0.028181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1058-7_0_3_line_5 |  | 5 | 6 | 0.012862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1058-7_0_3_line_6 |  | 6 | 7 | 0.0052428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1058-7_0_3_line_7 |  | 7 | 8 | 0.016405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1058-7_0_3_line_8 |  | 8 | 68 | 0.010383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1058-7_0_3_line_9 |  | 9 | 10 | 0.017097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1058-7_0_3_line_10 |  | 10 | 15 | 0.006663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1058-7_0_3_line_11 |  | 10 | 16 | 0.024112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1058-7_0_3_line_12 |  | 10 | 17 | 0.064674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1058-7_0_3_line_13 |  | 11 | 12 | 0.012957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1058-7_0_3_line_14 |  | 11 | 13 | 0.005656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1058-7_0_3_line_15 |  | 11 | 14 | 0.025324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1058-7_0_3_line_16 |  | 12 | 18 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1058-7_0_3_line_17 |  | 13 | 19 | 0.017907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1058-7_0_3_line_18 |  | 13 | 20 | 0.017196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1058-7_0_3_line_19 |  | 14 | 21 | 1.589e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1058-7_0_3_line_20 |  | 15 | 19 | 0.017533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1058-7_0_3_line_21 |  | 17 | 24 | 0.028205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1058-7_0_3_line_22 |  | 18 | 28 | 0.014118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1058-7_0_3_line_23 |  | 20 | 29 | 0.021746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1058-7_0_3_line_24 |  | 21 | 26 | 0.02352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1058-7_0_3_line_25 |  | 22 | 23 | 0.048212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1058-7_0_3_line_26 |  | 23 | 30 | 0.015937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1058-7_0_3_line_27 |  | 23 | 31 | 0.017758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1058-7_0_3_line_28 |  | 24 | 32 | 0.037267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1058-7_0_3_line_29 |  | 25 | 26 | 0.00367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1058-7_0_3_line_30 |  | 25 | 27 | 0.010988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1058-7_0_3_line_31 |  | 26 | 35 | 0.0035472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1058-7_0_3_line_32 |  | 27 | 36 | 0.0081083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1058-7_0_3_line_33 |  | 28 | 48 | 0.003035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1058-7_0_3_line_34 |  | 30 | 49 | 0.026507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1058-7_0_3_line_35 |  | 31 | 50 | 0.0052982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1058-7_0_3_line_36 |  | 32 | 51 | 0.045929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1058-7_0_3_line_37 |  | 32 | 33 | 0.029282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1058-7_0_3_line_38 |  | 33 | 34 | 0.03385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1058-7_0_3_line_39 |  | 34 | 76 | 0.075298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1058-7_0_3_line_40 |  | 36 | 37 | 0.0079897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1058-7_0_3_line_41 |  | 37 | 38 | 0.0077839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1058-7_0_3_line_42 |  | 38 | 39 | 0.0090808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1058-7_0_3_line_43 |  | 38 | 40 | 0.011359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1058-7_0_3_line_44 |  | 39 | 41 | 0.0064625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1058-7_0_3_line_45 |  | 40 | 46 | 0.0008932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1058-7_0_3_line_46 |  | 40 | 47 | 0.006913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1058-7_0_3_line_47 |  | 41 | 42 | 0.008678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1058-7_0_3_line_48 |  | 42 | 43 | 0.017234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1058-7_0_3_line_49 |  | 43 | 44 | 0.020842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1058-7_0_3_line_50 |  | 43 | 45 | 0.002954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1058-7_0_3_line_51 |  | 44 | 63 | 0.003631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1058-7_0_3_line_52 |  | 44 | 64 | 0.004579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1058-7_0_3_line_53 |  | 45 | 61 | 0.039478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1058-7_0_3_line_54 |  | 45 | 60 | 0.0015584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1058-7_0_3_line_55 |  | 48 | 111 | 0.008454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1058-7_0_3_line_56 |  | 49 | 51 | 0.007246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1058-7_0_3_line_57 |  | 51 | 54 | 0.009221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1058-7_0_3_line_58 |  | 51 | 55 | 0.0022494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1058-7_0_3_line_59 |  | 52 | 53 | 0.019342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1058-7_0_3_line_60 |  | 52 | 54 | 0.003899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1058-7_0_3_line_61 |  | 53 | 56 | 0.039373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1058-7_0_3_line_62 |  | 54 | 57 | 0.015792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1058-7_0_3_line_63 |  | 54 | 58 | 0.049133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1058-7_0_3_line_64 |  | 56 | 75 | 0.02435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1058-7_0_3_line_65 |  | 57 | 59 | 0.063883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1058-7_0_3_line_66 |  | 58 | 68 | 0.028339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1058-7_0_3_line_67 |  | 59 | 69 | 0.071301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1058-7_0_3_line_68 |  | 61 | 62 | 0.010737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1058-7_0_3_line_69 |  | 62 | 65 | 0.094141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1058-7_0_3_line_70 |  | 65 | 71 | 0.091002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1058-7_0_3_line_71 |  | 66 | 67 | 0.028695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1058-7_0_3_line_72 |  | 67 | 70 | 0.013106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1058-7_0_3_line_73 |  | 69 | 74 | 0.010726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1058-7_0_3_line_74 |  | 70 | 71 | 0.018558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1058-7_0_3_line_75 |  | 70 | 72 | 0.011282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1058-7_0_3_line_76 |  | 72 | 73 | 0.010931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1058-7_0_3_line_77 |  | 74 | 86 | 0.03105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1058-7_0_3_line_78 |  | 74 | 87 | 0.077805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1058-7_0_3_line_79 |  | 75 | 84 | 0.027331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1058-7_0_3_line_80 |  | 76 | 77 | 0.00014588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1058-7_0_3_line_81 |  | 77 | 78 | 0.013565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1058-7_0_3_line_82 |  | 78 | 79 | 0.027742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1058-7_0_3_line_83 |  | 79 | 80 | 0.031583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1058-7_0_3_line_84 |  | 80 | 81 | 0.023269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1058-7_0_3_line_85 |  | 81 | 109 | 0.030105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1058-7_0_3_line_86 |  | 82 | 83 | 0.0044889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1058-7_0_3_line_87 |  | 82 | 84 | 0.049124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1058-7_0_3_line_88 |  | 83 | 85 | 0.22938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1058-7_0_3_line_89 |  | 86 | 88 | 0.053965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1058-7_0_3_line_90 |  | 87 | 89 | 0.035366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1058-7_0_3_line_91 |  | 88 | 90 | 0.024941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1058-7_0_3_line_92 |  | 89 | 92 | 0.021172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1058-7_0_3_line_93 |  | 90 | 116 | 0.018454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1058-7_0_3_line_94 |  | 91 | 92 | 0.037716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1058-7_0_3_line_95 |  | 92 | 117 | 0.03175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1058-7_0_3_line_96 |  | 93 | 94 | 0.0048705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1058-7_0_3_line_97 |  | 93 | 95 | 0.067491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1058-7_0_3_line_98 |  | 94 | 96 | 0.012333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1058-7_0_3_line_99 |  | 95 | 97 | 0.019777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1058-7_0_3_line_100 |  | 95 | 98 | 0.13125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1058-7_0_3_line_101 |  | 96 | 99 | 0.0030208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1058-7_0_3_line_102 |  | 97 | 100 | 0.049173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1058-7_0_3_line_103 |  | 98 | 101 | 0.015191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1058-7_0_3_line_104 |  | 99 | 103 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1058-7_0_3_line_105 |  | 100 | 104 | 0.065461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1058-7_0_3_line_106 |  | 101 | 102 | 0.0097116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1058-7_0_3_line_107 |  | 102 | 108 | 0.027193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1058-7_0_3_line_108 |  | 102 | 105 | 0.009645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1058-7_0_3_line_109 |  | 103 | 109 | 0.0078325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1058-7_0_3_line_110 |  | 104 | 110 | 0.10819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1058-7_0_3_line_111 |  | 105 | 106 | 0.042956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1058-7_0_3_line_112 |  | 106 | 107 | 0.011462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1058-7_0_3_line_113 |  | 110 | 119 | 0.0057427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1058-7_0_3_line_114 |  | 111 | 112 | 0.01224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1058-7_0_3_line_115 |  | 112 | 113 | 0.005255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1058-7_0_3_line_116 |  | 113 | 114 | 0.0070518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1058-7_0_3_line_117 |  | 114 | 115 | 0.019354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1058-7_0_3_line_118 |  | 116 | 118 | 0.021341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1058-7_0_3_line_119 |  | 119 | 120 | 0.049074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1058-7_0_3_trafo_59 | 0.63 MVA 20/0.4 kV | 121 | 33 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2668125.7059 | 1208552.2379 | 2668096.3243 | 1208531.6838
1 | 2668151.32 | 1208570.1564 | 2668125.7059 | 1208552.2379
2 | 2668094.4651 | 1208530.3832 | 2668096.3243 | 1208531.6838
3 | 2668151.32 | 1208570.1564 | 2668153.2419 | 1208560.3056 | 2668152.7005 | 1208552.4613 | 2668146.1219 | 1208532.0291 | 2668146.3904 | 1208527.1514 | 2668153.1848 | 1208510.0629 | 2668153.4191 | 1208507.5196 | 2668149.2279 | 1208502.3797 | 2668140.1992 | 1208492.1036
4 | 2668151.32 | 1208570.1564 | 2668145.6771 | 1208597.7663
5 | 2668143.1015 | 1208610.368 | 2668145.6771 | 1208597.7663
6 | 2668141.2563 | 1208615.2248 | 2668142.6714 | 1208612.4726 | 2668143.1015 | 1208610.368
7 | 2668125.3684 | 1208612.7948 | 2668137.7725 | 1208616.0522 | 2668141.2563 | 1208615.2248 | 2668141.2563 | 1208615.2248
8 | 2668125.3684 | 1208612.7948 | 2668115.3257 | 1208610.1575
9 | 2667976.3413 | 1208454.3569 | 2667964.4875 | 1208466.6768
10 | 2667980.6703 | 1208459.4316 | 2667976.3413 | 1208454.3569
11 | 2667976.3413 | 1208454.3569 | 2667960.8509 | 1208435.8788
12 | 2668014.8442 | 1208498.8339 | 2668010.3415 | 1208491 | 2667999.3836 | 1208474.5206 | 2667979.8496 | 1208450.7169 | 2667976.3413 | 1208454.3569
13 | 2667948.6624 | 1208494.1552 | 2667956.9084 | 1208491.0805 | 2667957.4725 | 1208486.9399
14 | 2667962.3484 | 1208484.0492 | 2667961.6212 | 1208484.4856 | 2667957.4725 | 1208486.9399
15 | 2667957.4725 | 1208486.9399 | 2667952.2237 | 1208489.2038 | 2667947.1491 | 1208490.8471 | 2667942.7431 | 1208491.1971 | 2667932.8929 | 1208491.4535
16 | 2667948.6624 | 1208494.1552 | 2667949.2928 | 1208504.8912 | 2667949.714 | 1208510.7709
17 | 2667962.3484 | 1208484.0492 | 2667960.9493 | 1208481.3983 | 2667960.7662 | 1208478.1164 | 2667961.1944 | 1208475.2307 | 2667963.3325 | 1208471.7417 | 2667966.6266 | 1208468.5126
18 | 2667962.3484 | 1208484.0492 | 2667964.6351 | 1208486.877 | 2667975.2071 | 1208495.3681
19 | 2667932.8929 | 1208491.4535 | 2667932.8913 | 1208491.4535
20 | 2667980.6703 | 1208459.4316 | 2667979.9572 | 1208459.29 | 2667978.2018 | 1208459.2144 | 2667976.4862 | 1208459.6507 | 2667972.705 | 1208462.5539 | 2667966.6266 | 1208468.5126
21 | 2668014.8442 | 1208498.8339 | 2668015.5822 | 1208500.1209 | 2668018.6973 | 1208506.3046 | 2668024.315 | 1208522.3674 | 2668024.6764 | 1208525.1241
22 | 2667950.7229 | 1208524.8531 | 2667949.714 | 1208510.7709
23 | 2667975.2071 | 1208495.3681 | 2667979.5897 | 1208498.888 | 2667985.4692 | 1208504.0025 | 2667991.7514 | 1208509.476
24 | 2667914.3723 | 1208500.9803 | 2667914.3963 | 1208500.2135 | 2667915.4183 | 1208497.2566 | 2667917.0149 | 1208494.5842 | 2667918.7002 | 1208493.4694 | 2667922.3585 | 1208492.0101 | 2667926.9932 | 1208491.607 | 2667932.8913 | 1208491.4535
25 | 2667997.1462 | 1208620.1403 | 2667991.9532 | 1208592.831 | 2667990.1874 | 1208572.4943
26 | 2667997.1462 | 1208620.1403 | 2668012.7137 | 1208616.7279
27 | 2667997.1462 | 1208620.1403 | 2667979.6149 | 1208622.9668
28 | 2668031.8849 | 1208561.2554 | 2668028.7145 | 1208555.9271 | 2668024.6764 | 1208525.1241
29 | 2667918.0526 | 1208500.9333 | 2667914.3723 | 1208500.9803
30 | 2667918.0526 | 1208500.9333 | 2667924.5844 | 1208500.8409 | 2667924.7406 | 1208505.2937
31 | 2667914.3723 | 1208500.9803 | 2667914.256 | 1208504.5256
32 | 2667922.6664 | 1208512.3817 | 2667922.7368 | 1208510.8705 | 2667923.5345 | 1208509.5899 | 2667924.8657 | 1208508.8601 | 2667924.7406 | 1208505.2937
33 | 2667950.7229 | 1208524.8531 | 2667950.9393 | 1208527.8796
34 | 2668029.6012 | 1208604.178 | 2668029.3554 | 1208609.7341 | 2668029.9803 | 1208612.9432 | 2668012.7137 | 1208616.7279
35 | 2667974.3843 | 1208623.8102 | 2667979.6149 | 1208622.9668
36 | 2668031.8849 | 1208561.2554 | 2668031.3761 | 1208586.5429 | 2668033.1824 | 1208603.485 | 2668035.9862 | 1208602.95 | 2668036.7176 | 1208602.8138
37 | 2668042.2625 | 1208533.9235 | 2668040.9917 | 1208536.0214 | 2668032.9129 | 1208557.776 | 2668031.8849 | 1208561.2554
38 | 2668042.2625 | 1208533.9235 | 2668058.8439 | 1208504.4126
39 | 2668100.5059 | 1208442.0345 | 2668092.1026 | 1208450.9296 | 2668076.2526 | 1208473.4293 | 2668058.8439 | 1208504.4126
40 | 2667922.6664 | 1208512.3817 | 2667923.2006 | 1208513.5441 | 2667924.1793 | 1208514.389 | 2667925.4222 | 1208514.7367 | 2667925.7609 | 1208518.8496
41 | 2667926.222 | 1208526.6198 | 2667925.7695 | 1208518.9544 | 2667925.7609 | 1208518.8496
42 | 2667926.222 | 1208526.6198 | 2667926.7547 | 1208535.6849
43 | 2667914.8794 | 1208527.2356 | 2667917.9452 | 1208527.0704 | 2667926.222 | 1208526.6198
44 | 2667924.4693 | 1208541.0087 | 2667924.7734 | 1208539.6669 | 2667925.6372 | 1208538.5872 | 2667926.8907 | 1208538.0011 | 2667926.7547 | 1208535.6849
45 | 2667914.8794 | 1208527.2356 | 2667914.8549 | 1208526.3427
46 | 2667914.8794 | 1208527.2356 | 2667915.234 | 1208534.1395
47 | 2667924.4693 | 1208541.0087 | 2667924.9302 | 1208542.5927 | 2667926.1417 | 1208543.6961 | 2667927.7573 | 1208544.0257 | 2667927.9482 | 1208547.7617
48 | 2667919.3445 | 1208556.4154 | 2667928.3666 | 1208555.9511 | 2667927.9482 | 1208547.7617
49 | 2667919.3445 | 1208556.4154 | 2667920.2342 | 1208570.4231 | 2667927.0343 | 1208570.1336
50 | 2667919.3445 | 1208556.4154 | 2667916.3854 | 1208556.5596
51 | 2667929.016 | 1208573.0357 | 2667927.6383 | 1208571.8415 | 2667927.0343 | 1208570.1336
52 | 2667929.4611 | 1208566.6591 | 2667928.568 | 1208566.9713 | 2667927.3815 | 1208568.3475 | 2667927.0343 | 1208570.1336
53 | 2667916.3854 | 1208556.5596 | 2667917.6617 | 1208578.6878 | 2667910.0464 | 1208580.4689 | 2667900.6145 | 1208581.54
54 | 2667916.3854 | 1208556.5596 | 2667916.3055 | 1208555.0033
55 | 2667950.9393 | 1208527.8796 | 2667951.5452 | 1208536.3119
56 | 2668029.6012 | 1208604.178 | 2668030.546 | 1208603.9997 | 2668033.1824 | 1208603.485 | 2668035.9862 | 1208602.95 | 2668036.7176 | 1208602.8138
57 | 2668036.7176 | 1208602.8138 | 2668037.5042 | 1208607.1699 | 2668038.7134 | 1208611.8087
58 | 2668036.7176 | 1208602.8138 | 2668036.2535 | 1208600.6127
59 | 2668034.8448 | 1208612.3761 | 2668040.4785 | 1208630.8789
60 | 2668038.7134 | 1208611.8087 | 2668034.8448 | 1208612.3761
61 | 2668053.6277 | 1208667.9688 | 2668044.4446 | 1208643.9049 | 2668040.4785 | 1208630.8789
62 | 2668038.7134 | 1208611.8087 | 2668039.6309 | 1208615.3547 | 2668043.2011 | 1208626.947
63 | 2668038.7134 | 1208611.8087 | 2668079.8512 | 1208605.7962 | 2668087.4087 | 1208605.8825
64 | 2668053.6277 | 1208667.9688 | 2668049.9471 | 1208673.3857 | 2668048.9047 | 1208677.4653 | 2668050.8189 | 1208682.9349 | 2668055.1191 | 1208689.4365
65 | 2668043.2011 | 1208626.947 | 2668047.7257 | 1208641.5186 | 2668051.9907 | 1208654.1861 | 2668057.8249 | 1208667.9166 | 2668067.2705 | 1208685.9305
66 | 2668115.3257 | 1208610.1575 | 2668105.2851 | 1208607.5207 | 2668089.3001 | 1208605.904 | 2668087.4087 | 1208605.8825
67 | 2668067.2705 | 1208685.9305 | 2668068.0707 | 1208687.4566 | 2668082.5016 | 1208713.9819 | 2668087.8158 | 1208725.305 | 2668091.9674 | 1208735.2363 | 2668096.6818 | 1208747.82 | 2668097.4362 | 1208750.3823
68 | 2667900.6145 | 1208581.54 | 2667895.7965 | 1208578.6835 | 2667891.9188 | 1208575.3165
69 | 2667891.9188 | 1208575.3165 | 2667811.199 | 1208623.7608
70 | 2667811.199 | 1208623.7608 | 2667802.411 | 1208610.9976 | 2667795.3591 | 1208594.6519 | 2667788.4183 | 1208568.5237 | 2667785.0699 | 1208560.1027 | 2667781.2914 | 1208553.4113 | 2667775.0858 | 1208543.5347 | 2667773.9675 | 1208541.5732
71 | 2667799.9035 | 1208502.7988 | 2667787.8179 | 1208510.2811 | 2667775.7236 | 1208518.2438
72 | 2667764.7767 | 1208525.4511 | 2667775.7236 | 1208518.2438
73 | 2668100.4655 | 1208760.6711 | 2668097.4362 | 1208750.3823
74 | 2667764.7767 | 1208525.4511 | 2667773.9675 | 1208541.5732
75 | 2667764.7767 | 1208525.4511 | 2667754.5216 | 1208530.1541
76 | 2667744.5853 | 1208534.7109 | 2667754.5216 | 1208530.1541
77 | 2668100.4655 | 1208760.6711 | 2668101.9439 | 1208760.3655 | 2668104.4508 | 1208761.1947 | 2668105.9161 | 1208762.0341 | 2668106.9109 | 1208762.8015 | 2668110.2512 | 1208769.2102 | 2668115.7805 | 1208784.9978
78 | 2668100.4655 | 1208760.6711 | 2668101.2268 | 1208763.248 | 2668106.0835 | 1208780.6697 | 2668111.9909 | 1208803.2844 | 2668116.0222 | 1208817.7504 | 2668120.2259 | 1208827.1041 | 2668123.0232 | 1208831.7945 | 2668124.7616 | 1208834.147
79 | 2668055.1191 | 1208689.4365 | 2668056.8502 | 1208692.0537 | 2668059.6943 | 1208700.647 | 2668061.5264 | 1208712.653 | 2668061.4456 | 1208715.6483
80 | 2668100.5059 | 1208442.0345 | 2668100.6061 | 1208441.9284
81 | 2668109.9216 | 1208432.0677 | 2668100.6061 | 1208441.9284
82 | 2668109.9216 | 1208432.0677 | 2668128.973 | 1208411.9014
83 | 2668150.9695 | 1208389.2385 | 2668129.8122 | 1208411.013 | 2668128.973 | 1208411.9014
84 | 2668150.9695 | 1208389.2385 | 2668167.1851 | 1208372.5499
85 | 2668167.1851 | 1208372.5499 | 2668181.5345 | 1208357.7818 | 2668186.8615 | 1208349.8988
86 | 2668060.434 | 1208763.1084 | 2668061.4609 | 1208767.4783
87 | 2668060.434 | 1208763.1084 | 2668057.4176 | 1208750.2738 | 2668055.7693 | 1208743.4841 | 2668056.293 | 1208738.8984 | 2668058.3287 | 1208734.3855 | 2668061.0914 | 1208728.7913 | 2668061.4456 | 1208715.6483
88 | 2668061.4609 | 1208767.4783 | 2667853.442 | 1208864.1442
89 | 2668115.7805 | 1208784.9978 | 2668119.329 | 1208795.1297 | 2668122.3391 | 1208799.8336 | 2668127.621 | 1208801.3171 | 2668134.5487 | 1208801.8075 | 2668140.9171 | 1208798.0223 | 2668155.4906 | 1208787.7924
90 | 2668124.7616 | 1208834.147 | 2668116.2489 | 1208868.4731
91 | 2668169.5895 | 1208769.0763 | 2668168.7018 | 1208775.5702 | 2668165.9932 | 1208780.42 | 2668155.4906 | 1208787.7924
92 | 2668116.2489 | 1208868.4731 | 2668128.7978 | 1208885.5258
93 | 2668169.5895 | 1208769.0763 | 2668169.5895 | 1208769.0763 | 2668168.8459 | 1208762.964 | 2668165.3258 | 1208751.1818
94 | 2668156.5167 | 1208859.9497 | 2668128.7978 | 1208885.5258
95 | 2668148.1245 | 1208910.6132 | 2668145.9687 | 1208908.8594 | 2668128.7978 | 1208885.5258
96 | 2668203.758 | 1208307.1883 | 2668202.4443 | 1208311.8783
97 | 2668203.758 | 1208307.1883 | 2668216.3378 | 1208262.2762 | 2668221.9559 | 1208242.1964
98 | 2668198.8708 | 1208323.6819 | 2668201.8164 | 1208314.12 | 2668202.4443 | 1208311.8783
99 | 2668228.8601 | 1208223.7067 | 2668226.6742 | 1208228.0288 | 2668222.1642 | 1208241.4522 | 2668221.9559 | 1208242.1964
100 | 2668221.9559 | 1208242.1964 | 2668095.9533 | 1208205.4559
101 | 2668197.9815 | 1208326.5688 | 2668198.8708 | 1208323.6819
102 | 2668228.8601 | 1208223.7067 | 2668232.9751 | 1208215.5821 | 2668257.5404 | 1208183.9304
103 | 2668095.9533 | 1208205.4559 | 2668093.9202 | 1208190.4015
104 | 2668197.9815 | 1208326.5688 | 2668196.2261 | 1208332.2673 | 2668192.3076 | 1208341.8395 | 2668191.2469 | 1208343.4091
105 | 2668296.3134 | 1208131.2156 | 2668278.1343 | 1208157.3959 | 2668257.5404 | 1208183.9304
106 | 2668093.2856 | 1208180.7214 | 2668093.5066 | 1208187.3391 | 2668093.9202 | 1208190.4015
107 | 2668079.1783 | 1208157.7019 | 2668088.4917 | 1208175.7303 | 2668093.2856 | 1208180.7214
108 | 2668093.2856 | 1208180.7214 | 2668095.2365 | 1208177.664 | 2668099.0389 | 1208172.9992
109 | 2668186.8615 | 1208349.8988 | 2668191.2469 | 1208343.4091
110 | 2668296.3134 | 1208131.2156 | 2668397.1808 | 1208092.0962
111 | 2668099.0389 | 1208172.9992 | 2668099.2771 | 1208172.707 | 2668103.0337 | 1208165.9902 | 2668104.4294 | 1208160.2804 | 2668104.0356 | 1208156.1511 | 2668101.7342 | 1208151.2774 | 2668091.9966 | 1208134.4207
112 | 2668086.2632 | 1208124.4956 | 2668091.9966 | 1208134.4207
113 | 2668397.1808 | 1208092.0962 | 2668402.7787 | 1208093.378
114 | 2667952.4224 | 1208548.5203 | 2667951.5452 | 1208536.3119
115 | 2667952.4224 | 1208548.5203 | 2667952.7961 | 1208553.7611
116 | 2667952.7961 | 1208553.7611 | 2667953.3007 | 1208560.7948
117 | 2667954.6857 | 1208580.0988 | 2667953.3007 | 1208560.7948
118 | 2668159.2169 | 1208730.7343 | 2668165.3258 | 1208751.1818
119 | 2668449.8345 | 1208085.1716 | 2668448.5181 | 1208086.1363 | 2668434.3702 | 1208092.6115 | 2668420.7798 | 1208094.8905 | 2668405.8183 | 1208094.0741 | 2668402.7787 | 1208093.378

## bus_geodata
| x | y | coords
0 | 2668125.7059 | 1208552.2379
1 | 2668096.3243 | 1208531.6838
2 | 2668151.32 | 1208570.1564
3 | 2668094.4651 | 1208530.3832
4 | 2668140.1992 | 1208492.1036
5 | 2668145.6771 | 1208597.7663
6 | 2668143.1015 | 1208610.368
7 | 2668141.2563 | 1208615.2248
8 | 2668125.3684 | 1208612.7948
9 | 2667964.4875 | 1208466.6768
10 | 2667976.3413 | 1208454.3569
11 | 2667957.4725 | 1208486.9399
12 | 2667948.6624 | 1208494.1552
13 | 2667962.3484 | 1208484.0492
14 | 2667932.8929 | 1208491.4535
15 | 2667980.6703 | 1208459.4316
16 | 2667960.8509 | 1208435.8788
17 | 2668014.8442 | 1208498.8339
18 | 2667949.714 | 1208510.7709
19 | 2667966.6266 | 1208468.5126
20 | 2667975.2071 | 1208495.3681
21 | 2667932.8913 | 1208491.4535
22 | 2667990.1874 | 1208572.4943
23 | 2667997.1462 | 1208620.1403
24 | 2668024.6764 | 1208525.1241
25 | 2667918.0526 | 1208500.9333
26 | 2667914.3723 | 1208500.9803
27 | 2667924.7406 | 1208505.2937
28 | 2667950.7229 | 1208524.8531
29 | 2667991.7514 | 1208509.476
30 | 2668012.7137 | 1208616.7279
31 | 2667979.6149 | 1208622.9668
32 | 2668031.8849 | 1208561.2554
33 | 2668042.2625 | 1208533.9235
34 | 2668058.8439 | 1208504.4126
35 | 2667914.256 | 1208504.5256
36 | 2667922.6664 | 1208512.3817
37 | 2667925.7609 | 1208518.8496
38 | 2667926.222 | 1208526.6198
39 | 2667926.7547 | 1208535.6849
40 | 2667914.8794 | 1208527.2356
41 | 2667924.4693 | 1208541.0087
42 | 2667927.9482 | 1208547.7617
43 | 2667919.3445 | 1208556.4154
44 | 2667927.0343 | 1208570.1336
45 | 2667916.3854 | 1208556.5596
46 | 2667914.8549 | 1208526.3427
47 | 2667915.234 | 1208534.1395
48 | 2667950.9393 | 1208527.8796
49 | 2668029.6012 | 1208604.178
50 | 2667974.3843 | 1208623.8102
51 | 2668036.7176 | 1208602.8138
52 | 2668034.8448 | 1208612.3761
53 | 2668040.4785 | 1208630.8789
54 | 2668038.7134 | 1208611.8087
55 | 2668036.2535 | 1208600.6127
56 | 2668053.6277 | 1208667.9688
57 | 2668043.2011 | 1208626.947
58 | 2668087.4087 | 1208605.8825
59 | 2668067.2705 | 1208685.9305
60 | 2667916.3055 | 1208555.0033
61 | 2667900.6145 | 1208581.54
62 | 2667891.9188 | 1208575.3165
63 | 2667929.016 | 1208573.0357
64 | 2667929.4611 | 1208566.6591
65 | 2667811.199 | 1208623.7608
66 | 2667799.9035 | 1208502.7988
67 | 2667775.7236 | 1208518.2438
68 | 2668115.3257 | 1208610.1575
69 | 2668097.4362 | 1208750.3823
70 | 2667764.7767 | 1208525.4511
71 | 2667773.9675 | 1208541.5732
72 | 2667754.5216 | 1208530.1541
73 | 2667744.5853 | 1208534.7109
74 | 2668100.4655 | 1208760.6711
75 | 2668055.1191 | 1208689.4365
76 | 2668100.5059 | 1208442.0345
77 | 2668100.6061 | 1208441.9284
78 | 2668109.9216 | 1208432.0677
79 | 2668128.973 | 1208411.9014
80 | 2668150.9695 | 1208389.2385
81 | 2668167.1851 | 1208372.5499
82 | 2668060.434 | 1208763.1084
83 | 2668061.4609 | 1208767.4783
84 | 2668061.4456 | 1208715.6483
85 | 2667853.442 | 1208864.1442
86 | 2668115.7805 | 1208784.9978
87 | 2668124.7616 | 1208834.147
88 | 2668155.4906 | 1208787.7924
89 | 2668116.2489 | 1208868.4731
90 | 2668169.5895 | 1208769.0763
91 | 2668156.5167 | 1208859.9497
92 | 2668128.7978 | 1208885.5258
93 | 2668203.758 | 1208307.1883
94 | 2668202.4443 | 1208311.8783
95 | 2668221.9559 | 1208242.1964
96 | 2668198.8708 | 1208323.6819
97 | 2668228.8601 | 1208223.7067
98 | 2668095.9533 | 1208205.4559
99 | 2668197.9815 | 1208326.5688
100 | 2668257.5404 | 1208183.9304
101 | 2668093.9202 | 1208190.4015
102 | 2668093.2856 | 1208180.7214
103 | 2668191.2469 | 1208343.4091
104 | 2668296.3134 | 1208131.2156
105 | 2668099.0389 | 1208172.9992
106 | 2668091.9966 | 1208134.4207
107 | 2668086.2632 | 1208124.4956
108 | 2668079.1783 | 1208157.7019
109 | 2668186.8615 | 1208349.8988
110 | 2668397.1808 | 1208092.0962
111 | 2667951.5452 | 1208536.3119
112 | 2667952.4224 | 1208548.5203
113 | 2667952.7961 | 1208553.7611
114 | 2667953.3007 | 1208560.7948
115 | 2667954.6857 | 1208580.0988
116 | 2668165.3258 | 1208751.1818
117 | 2668148.1245 | 1208910.6132
118 | 2668159.2169 | 1208730.7343
119 | 2668402.7787 | 1208093.378
120 | 2668449.8345 | 1208085.1716
121 | 2668031.8849 | 1208561.2554

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98854 | -0.22015 | 0.0019308 | 0.0004839
1 | 0.98834 | -0.22397 | 0.0044913 | 0.0011256
2 | 0.98877 | -0.21575 | 0.0077665 | 0.0019465
3 | 0.98834 | -0.22403 | 0.0014799 | 0.0003709
4 | 0.98847 | -0.22158 | 0.0038232 | 0.00095819
5 | 0.98927 | -0.20596 | 0.00060378 | 0.00015132
6 | 0.98951 | -0.20135 | 0.00049354 | 0.00012369
7 | 0.98961 | -0.19943 | 0.0039363 | 0.00098652
8 | 0.98998 | -0.19227 | 0.0032698 | 0.00081948
9 | 0.98983 | -0.19458 | 0.0024402 | 0.00061156
10 | 0.98987 | -0.19384 | 0 | 0
11 | 0.98732 | -0.24321 | 0 | 0
12 | 0.98716 | -0.24628 | 0 | 0
13 | 0.98759 | -0.23791 | 0 | 0
14 | 0.98641 | -0.26096 | 0.0019379 | 0.00048567
15 | 0.9895 | -0.20091 | 0 | 0
16 | 0.98982 | -0.19488 | 0.0024328 | 0.00060971
17 | 0.99371 | -0.1199 | 0 | 0
18 | 0.98696 | -0.25022 | 0.0030511 | 0.00076468
19 | 0.98854 | -0.21955 | 0.0021933 | 0.0005497
20 | 0.98752 | -0.23946 | 0.0021933 | 0.0005497
21 | 0.98641 | -0.26097 | 0.0019396 | 0.0004861
22 | 0.99254 | -0.14272 | 0.0041031 | 0.0010283
23 | 0.99272 | -0.13922 | 0 | 0
24 | 0.99539 | -0.087827 | 0.0019107 | 0.00047886
25 | 0.98553 | -0.27805 | 0 | 0
26 | 0.98564 | -0.27585 | 0 | 0
27 | 0.98519 | -0.28464 | 0.0028238 | 0.00070772
28 | 0.98683 | -0.2528 | 0 | 0
29 | 0.98746 | -0.24056 | 0.002842 | 0.00071228
30 | 0.99285 | -0.13677 | 0.0012098 | 0.0003032
31 | 0.99265 | -0.14066 | 0.00093996 | 0.00023558
32 | 0.99767 | -0.044372 | 0 | 0
33 | 1 | 0 | -0.24052 | -0.060898
34 | 0.99805 | -0.037088 | 0.0048374 | 0.0012124
35 | 0.98564 | -0.27597 | 0.0018739 | 0.00046965
36 | 0.98496 | -0.2891 | 0 | 0
37 | 0.98474 | -0.29349 | 0.0028237 | 0.00070769
38 | 0.98454 | -0.29737 | 0 | 0
39 | 0.98434 | -0.30133 | 0.0025704 | 0.00064421
40 | 0.9845 | -0.2981 | 0 | 0
41 | 0.98421 | -0.30385 | 0 | 0
42 | 0.98403 | -0.30723 | 0.002568 | 0.00064359
43 | 0.98373 | -0.31315 | 0 | 0
44 | 0.98363 | -0.31503 | 0 | 0
45 | 0.98369 | -0.31389 | 0 | 0
46 | 0.9845 | -0.29813 | 0.0017784 | 0.0004457
47 | 0.98449 | -0.29832 | 0.0017765 | 0.00044523
48 | 0.9868 | -0.25335 | 0 | 0
49 | 0.99309 | -0.13212 | 0 | 0
50 | 0.99263 | -0.141 | 0.003657 | 0.00091652
51 | 0.99315 | -0.13085 | 0 | 0
52 | 0.99227 | -0.14795 | 0 | 0
53 | 0.99183 | -0.15629 | 0.00039019 | 9.7791e-05
54 | 0.99235 | -0.14627 | 0 | 0
55 | 0.99315 | -0.13095 | 0.0025753 | 0.00064542
56 | 0.99097 | -0.17302 | 0 | 0
57 | 0.99177 | -0.15745 | 0.00093777 | 0.00023503
58 | 0.99099 | -0.1726 | 0.0013427 | 0.00033651
59 | 0.98948 | -0.20173 | 0.0016215 | 0.00040639
60 | 0.98369 | -0.31394 | 0.0018171 | 0.00045541
61 | 0.98325 | -0.3226 | 0 | 0
62 | 0.98312 | -0.32497 | 0.0018171 | 0.00045541
63 | 0.98362 | -0.31519 | 0.0025068 | 0.00062826
64 | 0.98362 | -0.31523 | 0.0025068 | 0.00062825
65 | 0.98222 | -0.34269 | 0.0020899 | 0.00052377
66 | 0.98133 | -0.36002 | 0.0012583 | 0.00031535
67 | 0.98137 | -0.35937 | 0.0012167 | 0.00030493
68 | 0.99024 | -0.18714 | 0.0010865 | 0.00027229
69 | 0.98702 | -0.24932 | 0.0026067 | 0.00065331
70 | 0.9814 | -0.35878 | 0 | 0
71 | 0.98152 | -0.35639 | 0.0012159 | 0.00030474
72 | 0.98135 | -0.35973 | 0.0011039 | 0.00027667
73 | 0.98131 | -0.36043 | 0.0035318 | 0.00088516
74 | 0.98668 | -0.256 | 0 | 0
75 | 0.99043 | -0.18337 | 0.0003528 | 8.8421e-05
76 | 0.99405 | -0.11368 | 0.0012503 | 0.00031335
77 | 0.99404 | -0.11383 | 0.0049011 | 0.0012283
78 | 0.99339 | -0.12622 | 0.0016572 | 0.00041532
79 | 0.99212 | -0.15079 | 0.0029823 | 0.00074744
80 | 0.99075 | -0.17717 | 0.0041775 | 0.001047
81 | 0.98983 | -0.19493 | 0.0013074 | 0.00032766
82 | 0.98887 | -0.21369 | 0.010952 | 0.0027448
83 | 0.98883 | -0.21454 | 0.0021799 | 0.00054632
84 | 0.98984 | -0.19484 | 0.0020545 | 0.00051491
85 | 0.98706 | -0.24898 | 0.0084058 | 0.0021067
86 | 0.9861 | -0.26727 | 0.0034282 | 0.0008592
87 | 0.98564 | -0.27624 | 0.0018495 | 0.00046352
88 | 0.98526 | -0.28358 | 0.0029807 | 0.00074704
89 | 0.98523 | -0.28429 | 0.0027955 | 0.00070063
90 | 0.98495 | -0.28979 | 0.0020548 | 0.00051499
91 | 0.98486 | -0.2914 | 0.0049592 | 0.0012429
92 | 0.98504 | -0.28804 | 0.0019915 | 0.00049911
93 | 0.98724 | -0.24518 | 0.0021663 | 0.00054294
94 | 0.98736 | -0.24282 | 0.0054077 | 0.0013553
95 | 0.98569 | -0.27535 | 0.0018056 | 0.00045253
96 | 0.98773 | -0.23565 | 0.00059352 | 0.00014875
97 | 0.9855 | -0.27911 | 0 | 0
98 | 0.98417 | -0.30499 | 0 | 0
99 | 0.98782 | -0.23386 | 0.0010721 | 0.0002687
100 | 0.98502 | -0.28844 | 0.0026067 | 0.00065329
101 | 0.98399 | -0.30843 | 0.0021069 | 0.00052804
102 | 0.9839 | -0.31026 | 0 | 0
103 | 0.9884 | -0.22275 | 0.0052448 | 0.0013145
104 | 0.98454 | -0.29782 | 0.0036475 | 0.00091416
105 | 0.98386 | -0.31099 | 0.0013723 | 0.00034392
106 | 0.98375 | -0.3132 | 0.001994 | 0.00049974
107 | 0.98374 | -0.31337 | 0.00085672 | 0.00021471
108 | 0.98374 | -0.31331 | 0.0062332 | 0.0015622
109 | 0.98868 | -0.21724 | 0.0021752 | 0.00054516
110 | 0.98411 | -0.30623 | 0.00043888 | 0.00010999
111 | 0.98672 | -0.2549 | 0.0032745 | 0.00082067
112 | 0.98664 | -0.25641 | 0 | 0
113 | 0.98661 | -0.25706 | 0 | 0
114 | 0.98657 | -0.25793 | 0.0026316 | 0.00065955
115 | 0.98649 | -0.25942 | 0.0042834 | 0.0010735
116 | 0.98475 | -0.2937 | 0.0047476 | 0.0011899
117 | 0.98495 | -0.2897 | 0.0029187 | 0.00073151
118 | 0.98461 | -0.29641 | 0.0070567 | 0.0017686
119 | 0.98409 | -0.30663 | 0.0019899 | 0.00049871
120 | 0.984 | -0.30829 | 0.0018865 | 0.0004728
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0059723 | 0.0014967 | -0.0059712 | -0.0014965 | 1.0868e-06 | 2.3591e-07 | 0.0089899 | 0.0089901 | 0.0089901 | 0.98854 | -0.22015 | 0.98834 | -0.22397 | 2.4698
1 | -0.0079031 | -0.0019806 | 0.0079048 | 0.0019813 | 1.6589e-06 | 6.6087e-07 | 0.011896 | 0.011896 | 0.011896 | 0.98854 | -0.22015 | 0.98877 | -0.21575 | 3.2682
2 | 0.0014799 | 0.00037088 | -0.0014799 | -0.0003709 | 4.2241e-09 | -2.6374e-08 | 0.0022281 | 0.0022281 | 0.0022281 | 0.98834 | -0.22397 | 0.98834 | -0.22403 | 0.61212
3 | 0.0038243 | 0.00095778 | -0.0038232 | -0.00095819 | 1.0617e-06 | -4.1654e-07 | 0.005755 | 0.0057554 | 0.0057554 | 0.98877 | -0.21575 | 0.98847 | -0.22158 | 1.5812
4 | -0.019496 | -0.0048856 | 0.019505 | 0.004891 | 9.0966e-06 | 5.4602e-06 | 0.029339 | 0.029339 | 0.029339 | 0.98877 | -0.21575 | 0.98927 | -0.20596 | 8.0602
5 | -0.020109 | -0.0050423 | 0.020113 | 0.005045 | 4.4128e-06 | 2.659e-06 | 0.030247 | 0.030247 | 0.030247 | 0.98927 | -0.20596 | 0.98951 | -0.20135 | 8.3097
6 | -0.020606 | -0.0051687 | 0.020608 | 0.0051698 | 1.8881e-06 | 1.141e-06 | 0.030989 | 0.030989 | 0.030989 | 0.98951 | -0.20135 | 0.98961 | -0.19943 | 8.5136
7 | -0.024545 | -0.0061564 | 0.024553 | 0.0061615 | 8.3803e-06 | 5.1525e-06 | 0.036908 | 0.036908 | 0.036908 | 0.98961 | -0.19943 | 0.98998 | -0.19227 | 10.1396
8 | -0.027823 | -0.006981 | 0.02783 | 0.0069852 | 6.8107e-06 | 4.2253e-06 | 0.041823 | 0.041823 | 0.041823 | 0.98998 | -0.19227 | 0.99024 | -0.18714 | 11.4898
9 | -0.0024402 | -0.00061156 | 0.0024402 | 0.0006114 | 8.6269e-08 | -1.6455e-07 | 0.0036683 | 0.0036682 | 0.0036683 | 0.98983 | -0.19458 | 0.98987 | -0.19384 | 1.0078
10 | 0.059902 | 0.015111 | -0.059881 | -0.015098 | 2.0276e-05 | 1.2891e-05 | 0.090082 | 0.090082 | 0.090082 | 0.98987 | -0.19384 | 0.9895 | -0.20091 | 24.7477
11 | 0.0024329 | 0.00060947 | -0.0024328 | -0.00060971 | 1.2094e-07 | -2.3254e-07 | 0.0036571 | 0.0036572 | 0.0036572 | 0.98987 | -0.19384 | 0.98982 | -0.19488 | 1.0047
12 | -0.064775 | -0.016332 | 0.065005 | 0.016479 | 0.00023011 | 0.00014644 | 0.097407 | 0.097407 | 0.097407 | 0.98987 | -0.19384 | 0.99371 | -0.1199 | 26.7602
13 | 0.013249 | 0.0033223 | -0.013247 | -0.0033212 | 1.9374e-06 | 1.0742e-06 | 0.019968 | 0.019968 | 0.019968 | 0.98732 | -0.24321 | 0.98716 | -0.24628 | 5.4858
14 | -0.052535 | -0.013212 | 0.052548 | 0.013221 | 1.3302e-05 | 8.4408e-06 | 0.079193 | 0.079193 | 0.079193 | 0.98732 | -0.24321 | 0.98759 | -0.23791 | 21.7563
15 | 0.039286 | 0.0098902 | -0.039253 | -0.0098692 | 3.3309e-05 | 2.0994e-05 | 0.059225 | 0.059225 | 0.059225 | 0.98732 | -0.24321 | 0.98641 | -0.26096 | 16.2706
16 | 0.013247 | 0.0033212 | -0.013244 | -0.0033198 | 2.4895e-06 | 1.3804e-06 | 0.019968 | 0.019968 | 0.019968 | 0.98716 | -0.24628 | 0.98696 | -0.25022 | 5.4858
17 | -0.057584 | -0.014483 | 0.057635 | 0.014515 | 5.0569e-05 | 3.2135e-05 | 0.08678 | 0.08678 | 0.08678 | 0.98759 | -0.23791 | 0.98854 | -0.21955 | 23.8408
18 | 0.0050359 | 0.0012618 | -0.0050355 | -0.0012618 | 3.7125e-07 | 1.7577e-08 | 0.0075875 | 0.0075876 | 0.0075876 | 0.98759 | -0.23791 | 0.98752 | -0.23946 | 2.0845
19 | 0.037315 | 0.0093835 | -0.037315 | -0.0093835 | 1.8888e-09 | 1.2088e-09 | 0.056302 | 0.056302 | 0.056302 | 0.98641 | -0.26096 | 0.98641 | -0.26097 | 15.4675
20 | 0.059881 | 0.015098 | -0.059828 | -0.015065 | 5.3354e-05 | 3.3922e-05 | 0.090082 | 0.090082 | 0.090082 | 0.9895 | -0.20091 | 0.98854 | -0.21955 | 24.7477
21 | -0.065005 | -0.016479 | 0.065105 | 0.016543 | 0.00010035 | 6.386e-05 | 0.097407 | 0.097407 | 0.097407 | 0.99371 | -0.1199 | 0.99539 | -0.087827 | 26.7601
22 | 0.010193 | 0.0025552 | -0.010192 | -0.0025545 | 1.2504e-06 | 6.1987e-07 | 0.015368 | 0.015368 | 0.015368 | 0.98696 | -0.25022 | 0.98683 | -0.2528 | 4.222
23 | 0.0028422 | 0.0007121 | -0.002842 | -0.00071228 | 1.4957e-07 | -1.8247e-07 | 0.0042826 | 0.0042827 | 0.0042827 | 0.98752 | -0.23946 | 0.98746 | -0.24056 | 1.1766
24 | 0.035375 | 0.0088974 | -0.03535 | -0.0088816 | 2.5128e-05 | 1.5782e-05 | 0.053376 | 0.053376 | 0.053376 | 0.98641 | -0.26097 | 0.98564 | -0.27585 | 14.6637
25 | -0.0041031 | -0.0010283 | 0.0041038 | 0.0010282 | 6.8409e-07 | -1.854e-07 | 0.0061514 | 0.0061512 | 0.0061514 | 0.99254 | -0.14272 | 0.99272 | -0.13922 | 1.6899
26 | -0.0087011 | -0.0021802 | 0.0087021 | 0.0021806 | 1.0166e-06 | 4.4453e-07 | 0.013042 | 0.013042 | 0.013042 | 0.99272 | -0.13922 | 0.99285 | -0.13677 | 3.583
27 | 0.0045973 | 0.001152 | -0.004597 | -0.0011521 | 3.1622e-07 | -2.7194e-08 | 0.006891 | 0.006891 | 0.006891 | 0.99272 | -0.13922 | 0.99265 | -0.14066 | 1.8931
28 | -0.067016 | -0.017021 | 0.067156 | 0.017111 | 0.00014049 | 8.9425e-05 | 0.10026 | 0.10026 | 0.10026 | 0.99539 | -0.087827 | 0.99767 | -0.044372 | 27.5447
29 | -0.033473 | -0.0084098 | 0.033476 | 0.008412 | 3.5163e-06 | 2.2037e-06 | 0.050547 | 0.050547 | 0.050547 | 0.98553 | -0.27805 | 0.98564 | -0.27585 | 13.8865
30 | 0.033473 | 0.0084098 | -0.033462 | -0.0084032 | 1.0528e-05 | 6.5979e-06 | 0.050547 | 0.050547 | 0.050547 | 0.98553 | -0.27805 | 0.98519 | -0.28464 | 13.8865
31 | 0.0018739 | 0.00046961 | -0.0018739 | -0.00046965 | 1.0646e-08 | -3.8396e-08 | 0.002829 | 0.002829 | 0.002829 | 0.98564 | -0.27585 | 0.98564 | -0.27597 | 0.77721
32 | 0.030638 | 0.0076955 | -0.030632 | -0.0076914 | 6.513e-06 | 4.0651e-06 | 0.046282 | 0.046282 | 0.046282 | 0.98519 | -0.28464 | 0.98496 | -0.2891 | 12.7148
33 | 0.010192 | 0.0025545 | -0.010192 | -0.0025544 | 2.688e-07 | 1.3326e-07 | 0.015368 | 0.015368 | 0.015368 | 0.98683 | -0.2528 | 0.9868 | -0.25335 | 4.222
34 | -0.0099119 | -0.0024838 | 0.0099141 | 0.0024849 | 2.1936e-06 | 1.061e-06 | 0.014855 | 0.014855 | 0.014855 | 0.99285 | -0.13677 | 0.99309 | -0.13212 | 4.0811
35 | 0.003657 | 0.00091649 | -0.003657 | -0.00091652 | 5.9709e-08 | -3.0275e-08 | 0.005482 | 0.005482 | 0.005482 | 0.99265 | -0.14066 | 0.99263 | -0.141 | 1.5061
36 | 0.10795 | 0.02741 | -0.1075 | -0.027125 | 0.0004472 | 0.00028561 | 0.16113 | 0.16113 | 0.16113 | 0.99767 | -0.044372 | 0.99315 | -0.13085 | 44.2678
37 | -0.17511 | -0.044521 | 0.17548 | 0.04476 | 0.00037515 | 0.00023933 | 0.2614 | 0.2614 | 0.2614 | 0.99767 | -0.044372 | 1 | 0 | 35.9062
38 | 0.063386 | 0.016138 | -0.063273 | -0.016066 | 0.00011314 | 7.1966e-05 | 0.094409 | 0.094409 | 0.094409 | 1 | 0 | 0.99805 | -0.037088 | 25.9364
39 | 0.058436 | 0.014853 | -0.058221 | -0.014717 | 0.00021469 | 0.00013642 | 0.087197 | 0.087197 | 0.087197 | 0.99805 | -0.037088 | 0.99405 | -0.11368 | 23.9552
40 | 0.030632 | 0.0076914 | -0.030626 | -0.0076874 | 6.4177e-06 | 4.0057e-06 | 0.046282 | 0.046282 | 0.046282 | 0.98496 | -0.2891 | 0.98474 | -0.29349 | 12.7148
41 | 0.027802 | 0.0069797 | -0.027797 | -0.0069765 | 5.1527e-06 | 3.1987e-06 | 0.042015 | 0.042015 | 0.042015 | 0.98474 | -0.29349 | 0.98454 | -0.29737 | 11.5426
42 | 0.024242 | 0.0060858 | -0.024237 | -0.0060829 | 4.5721e-06 | 2.8107e-06 | 0.036642 | 0.036642 | 0.036642 | 0.98454 | -0.29737 | 0.98434 | -0.30133 | 10.0665
43 | 0.003555 | 0.00089078 | -0.0035549 | -0.00089084 | 1.2297e-07 | -6.5746e-08 | 0.0053729 | 0.005373 | 0.005373 | 0.98454 | -0.29737 | 0.9845 | -0.2981 | 1.4761
44 | 0.021667 | 0.0054387 | -0.021664 | -0.0054371 | 2.6003e-06 | 1.5821e-06 | 0.032756 | 0.032757 | 0.032757 | 0.98434 | -0.30133 | 0.98421 | -0.30385 | 8.999
45 | 0.0017784 | 0.00044569 | -0.0017784 | -0.0004457 | 2.4199e-09 | -9.8091e-09 | 0.0026879 | 0.0026879 | 0.0026879 | 0.9845 | -0.2981 | 0.9845 | -0.29813 | 0.73843
46 | 0.0017765 | 0.00044516 | -0.0017765 | -0.00044523 | 1.869e-08 | -7.5942e-08 | 0.0026851 | 0.0026851 | 0.0026851 | 0.9845 | -0.2981 | 0.98449 | -0.29832 | 0.73767
47 | 0.021664 | 0.0054371 | -0.021661 | -0.005435 | 3.4918e-06 | 2.1245e-06 | 0.032757 | 0.032757 | 0.032757 | 0.98421 | -0.30385 | 0.98403 | -0.30723 | 8.9991
48 | 0.019093 | 0.0047914 | -0.019087 | -0.0047882 | 5.3879e-06 | 3.2294e-06 | 0.028873 | 0.028873 | 0.028873 | 0.98403 | -0.30723 | 0.98373 | -0.31315 | 7.9323
49 | 0.0050141 | 0.0012565 | -0.0050136 | -0.0012564 | 4.4958e-07 | 2.3152e-08 | 0.0075843 | 0.0075844 | 0.0075844 | 0.98373 | -0.31315 | 0.98363 | -0.31503 | 2.0836
50 | 0.014073 | 0.0035317 | -0.014073 | -0.0035315 | 5.0206e-07 | 2.8382e-07 | 0.021289 | 0.021289 | 0.021289 | 0.98373 | -0.31315 | 0.98369 | -0.31389 | 5.8487
51 | 0.0025068 | 0.00062823 | -0.0025068 | -0.00062826 | 1.9582e-08 | -3.3557e-08 | 0.0037922 | 0.0037923 | 0.0037923 | 0.98363 | -0.31503 | 0.98362 | -0.31519 | 1.0418
52 | 0.0025068 | 0.00062821 | -0.0025068 | -0.00062825 | 2.4694e-08 | -4.2318e-08 | 0.0037922 | 0.0037922 | 0.0037922 | 0.98363 | -0.31503 | 0.98362 | -0.31523 | 1.0418
53 | 0.012256 | 0.0030761 | -0.01225 | -0.0030733 | 5.089e-06 | 2.756e-06 | 0.01854 | 0.018541 | 0.018541 | 0.98369 | -0.31389 | 0.98325 | -0.3226 | 5.0936
54 | 0.0018171 | 0.00045539 | -0.0018171 | -0.00045541 | 4.4154e-09 | -1.6958e-08 | 0.0027487 | 0.0027487 | 0.0027487 | 0.98369 | -0.31389 | 0.98369 | -0.31394 | 0.75514
55 | 0.010192 | 0.0025544 | -0.010191 | -0.002554 | 7.4876e-07 | 3.7121e-07 | 0.015368 | 0.015368 | 0.015368 | 0.9868 | -0.25335 | 0.98672 | -0.2549 | 4.2221
56 | -0.0099141 | -0.0024849 | 0.0099147 | 0.0024852 | 5.9962e-07 | 2.9e-07 | 0.014855 | 0.014855 | 0.014855 | 0.99309 | -0.13212 | 0.99315 | -0.13085 | 4.0811
57 | 0.095014 | 0.023994 | -0.094944 | -0.023949 | 7.0139e-05 | 4.477e-05 | 0.14242 | 0.14242 | 0.14242 | 0.99315 | -0.13085 | 0.99235 | -0.14627 | 39.1267
58 | 0.0025753 | 0.0006454 | -0.0025753 | -0.00064542 | 1.2558e-08 | -2.1071e-08 | 0.0038585 | 0.0038585 | 0.0038585 | 0.99315 | -0.13085 | 0.99315 | -0.13095 | 1.06
59 | 0.024422 | 0.0061498 | -0.024413 | -0.0061438 | 9.7343e-06 | 5.9802e-06 | 0.036634 | 0.036635 | 0.036635 | 0.99227 | -0.14795 | 0.99183 | -0.15629 | 10.0644
60 | -0.024422 | -0.0061498 | 0.024424 | 0.006151 | 1.9623e-06 | 1.2055e-06 | 0.036634 | 0.036634 | 0.036634 | 0.99227 | -0.14795 | 0.99235 | -0.14627 | 10.0644
61 | 0.024022 | 0.006046 | -0.024003 | -0.0060342 | 1.9188e-05 | 1.1772e-05 | 0.036049 | 0.036049 | 0.036049 | 0.99183 | -0.15629 | 0.99097 | -0.17302 | 9.9037
62 | 0.040202 | 0.010168 | -0.040181 | -0.010154 | 2.1544e-05 | 1.3584e-05 | 0.060316 | 0.060316 | 0.060316 | 0.99235 | -0.14627 | 0.99177 | -0.15745 | 16.5703
63 | 0.030317 | 0.0076302 | -0.030279 | -0.0076065 | 3.8096e-05 | 2.3747e-05 | 0.045471 | 0.045471 | 0.045471 | 0.99235 | -0.14627 | 0.99099 | -0.1726 | 12.4921
64 | 0.024003 | 0.0060342 | -0.023991 | -0.006027 | 1.1866e-05 | 7.281e-06 | 0.036049 | 0.036049 | 0.036049 | 0.99097 | -0.17302 | 0.99043 | -0.18337 | 9.9037
65 | 0.039243 | 0.0099194 | -0.03916 | -0.009867 | 8.3134e-05 | 5.2383e-05 | 0.058909 | 0.058909 | 0.058909 | 0.99177 | -0.15745 | 0.98948 | -0.20173 | 16.1838
66 | 0.028936 | 0.00727 | -0.028916 | -0.0072575 | 2.0068e-05 | 1.2479e-05 | 0.043455 | 0.043455 | 0.043455 | 0.99099 | -0.1726 | 0.99024 | -0.18714 | 11.9383
67 | 0.037539 | 0.0094606 | -0.037453 | -0.009407 | 8.5266e-05 | 5.3656e-05 | 0.056471 | 0.056471 | 0.056471 | 0.98948 | -0.20173 | 0.98702 | -0.24932 | 15.514
68 | 0.01225 | 0.0030733 | -0.012249 | -0.0030726 | 1.384e-06 | 7.4963e-07 | 0.018541 | 0.018541 | 0.018541 | 0.98325 | -0.3226 | 0.98312 | -0.32497 | 5.0936
69 | 0.010432 | 0.0026172 | -0.010423 | -0.0026127 | 8.8025e-06 | 4.441e-06 | 0.01579 | 0.015791 | 0.015791 | 0.98312 | -0.32497 | 0.98222 | -0.34269 | 4.3381
70 | 0.0083333 | 0.0020889 | -0.0083279 | -0.0020866 | 5.4393e-06 | 2.3302e-06 | 0.012625 | 0.012625 | 0.012625 | 0.98222 | -0.34269 | 0.98152 | -0.35639 | 3.4685
71 | -0.0012583 | -0.00031535 | 0.0012583 | 0.00031501 | 3.9167e-08 | -3.3747e-07 | 0.0019079 | 0.0019078 | 0.0019079 | 0.98133 | -0.36002 | 0.98137 | -0.35937 | 0.52415
72 | -0.002475 | -0.00061994 | 0.0024751 | 0.00061982 | 6.9212e-08 | -1.2131e-07 | 0.0037526 | 0.0037526 | 0.0037526 | 0.98137 | -0.35937 | 0.9814 | -0.35878 | 1.0309
73 | 0.034847 | 0.0087536 | -0.034835 | -0.0087467 | 1.1103e-05 | 6.969e-06 | 0.052541 | 0.052541 | 0.052541 | 0.98702 | -0.24932 | 0.98668 | -0.256 | 14.4344
74 | -0.0071112 | -0.0017816 | 0.007112 | 0.0017819 | 8.0899e-07 | 2.8323e-07 | 0.010782 | 0.010782 | 0.010782 | 0.9814 | -0.35878 | 0.98152 | -0.35639 | 2.9621
75 | 0.0046361 | 0.0011618 | -0.0046359 | -0.0011618 | 2.0905e-07 | -8.7587e-09 | 0.0070293 | 0.0070294 | 0.0070294 | 0.9814 | -0.35878 | 0.98135 | -0.35973 | 1.9311
76 | 0.0035319 | 0.0008851 | -0.0035318 | -0.00088516 | 1.1757e-07 | -6.2861e-08 | 0.0053554 | 0.0053555 | 0.0053555 | 0.98135 | -0.35973 | 0.98131 | -0.36043 | 1.4713
77 | 0.020299 | 0.0050977 | -0.020288 | -0.0050912 | 1.0915e-05 | 6.5893e-06 | 0.030617 | 0.030617 | 0.030617 | 0.98668 | -0.256 | 0.9861 | -0.26727 | 8.4113
78 | 0.014536 | 0.0036489 | -0.014522 | -0.0036409 | 1.4024e-05 | 7.9829e-06 | 0.021924 | 0.021924 | 0.021924 | 0.98668 | -0.256 | 0.98564 | -0.27624 | 6.0232
79 | 0.023639 | 0.0059385 | -0.023626 | -0.0059306 | 1.2931e-05 | 7.9241e-06 | 0.035519 | 0.03552 | 0.03552 | 0.99043 | -0.18337 | 0.98984 | -0.19484 | 9.7581
80 | 0.056971 | 0.014403 | -0.05697 | -0.014403 | 3.9828e-07 | 2.5301e-07 | 0.085325 | 0.085325 | 0.085325 | 0.99405 | -0.11368 | 0.99404 | -0.11383 | 23.441
81 | 0.052069 | 0.013175 | -0.052038 | -0.013155 | 3.094e-05 | 1.9626e-05 | 0.077989 | 0.077989 | 0.077989 | 0.99404 | -0.11383 | 0.99339 | -0.12622 | 21.4255
82 | 0.050381 | 0.01274 | -0.050322 | -0.012702 | 5.9312e-05 | 3.7601e-05 | 0.075506 | 0.075507 | 0.075507 | 0.99339 | -0.12622 | 0.99212 | -0.15079 | 20.7435
83 | 0.047339 | 0.011955 | -0.04728 | -0.011917 | 5.9759e-05 | 3.7839e-05 | 0.071034 | 0.071034 | 0.071034 | 0.99212 | -0.15079 | 0.99075 | -0.17717 | 19.5147
84 | 0.043102 | 0.01087 | -0.043066 | -0.010847 | 3.6595e-05 | 2.3121e-05 | 0.064759 | 0.06476 | 0.06476 | 0.99075 | -0.17717 | 0.98983 | -0.19493 | 17.7911
85 | 0.041758 | 0.010519 | -0.041714 | -0.010491 | 4.4516e-05 | 2.8104e-05 | 0.062794 | 0.062794 | 0.062794 | 0.98983 | -0.19493 | 0.98868 | -0.21724 | 17.2512
86 | 0.0106 | 0.0026591 | -0.010599 | -0.0026589 | 4.2831e-07 | 2.1653e-07 | 0.015951 | 0.015951 | 0.015951 | 0.98887 | -0.21369 | 0.98883 | -0.21454 | 4.3822
87 | -0.021552 | -0.0054039 | 0.021571 | 0.0054157 | 1.9375e-05 | 1.1769e-05 | 0.032431 | 0.032431 | 0.032431 | 0.98887 | -0.21369 | 0.98984 | -0.19484 | 8.9097
88 | 0.0084196 | 0.0021126 | -0.0084058 | -0.0021067 | 1.3811e-05 | 5.9021e-06 | 0.012671 | 0.012672 | 0.012672 | 0.98883 | -0.21454 | 0.98706 | -0.24898 | 3.4813
89 | 0.01686 | 0.004232 | -0.016847 | -0.0042243 | 1.3102e-05 | 7.6972e-06 | 0.025444 | 0.025444 | 0.025444 | 0.9861 | -0.26727 | 0.98526 | -0.28358 | 6.9902
90 | 0.012673 | 0.0031774 | -0.012668 | -0.0031748 | 4.8545e-06 | 2.6563e-06 | 0.019132 | 0.019132 | 0.019132 | 0.98564 | -0.27624 | 0.98523 | -0.28429 | 5.2561
91 | 0.013866 | 0.0034772 | -0.013862 | -0.0034749 | 4.1022e-06 | 2.3078e-06 | 0.020943 | 0.020943 | 0.020943 | 0.98526 | -0.28358 | 0.98495 | -0.28979 | 5.7535
92 | 0.0098722 | 0.0024741 | -0.0098704 | -0.0024733 | 1.7651e-06 | 8.6009e-07 | 0.01491 | 0.01491 | 0.01491 | 0.98523 | -0.28429 | 0.98504 | -0.28804 | 4.0962
93 | 0.011807 | 0.0029599 | -0.011805 | -0.0029588 | 2.2021e-06 | 1.1745e-06 | 0.017838 | 0.017839 | 0.017839 | 0.98495 | -0.28979 | 0.98475 | -0.2937 | 4.9007
94 | -0.0049592 | -0.0012429 | 0.00496 | 0.0012429 | 7.9402e-07 | 2.8147e-08 | 0.0074928 | 0.0074926 | 0.0074928 | 0.98486 | -0.2914 | 0.98504 | -0.28804 | 2.0585
95 | 0.002919 | 0.00073125 | -0.0029187 | -0.00073151 | 2.3149e-07 | -2.5597e-07 | 0.0044093 | 0.0044095 | 0.0044095 | 0.98504 | -0.28804 | 0.98495 | -0.2897 | 1.2114
96 | -0.027175 | -0.0068301 | 0.027178 | 0.006832 | 3.0651e-06 | 1.8994e-06 | 0.040966 | 0.040966 | 0.040966 | 0.98724 | -0.24518 | 0.98736 | -0.24282 | 11.2544
97 | 0.025008 | 0.0062872 | -0.024972 | -0.006265 | 3.5973e-05 | 2.2161e-05 | 0.037701 | 0.037701 | 0.037701 | 0.98724 | -0.24518 | 0.98569 | -0.27535 | 10.3574
98 | -0.032585 | -0.0081873 | 0.032597 | 0.0081943 | 1.1157e-05 | 6.9827e-06 | 0.049116 | 0.049116 | 0.049116 | 0.98736 | -0.24282 | 0.98773 | -0.23565 | 13.4933
99 | 0.010582 | 0.0026529 | -0.01058 | -0.002652 | 1.8925e-06 | 9.5919e-07 | 0.015974 | 0.015975 | 0.015975 | 0.98569 | -0.27535 | 0.9855 | -0.27911 | 4.3886
100 | 0.012585 | 0.0031596 | -0.012567 | -0.0031499 | 1.777e-05 | 9.7024e-06 | 0.019001 | 0.019001 | 0.019001 | 0.98569 | -0.27535 | 0.98417 | -0.30499 | 5.2202
101 | -0.03319 | -0.0083431 | 0.033193 | 0.0083448 | 2.8331e-06 | 1.7745e-06 | 0.05001 | 0.05001 | 0.05001 | 0.98773 | -0.23565 | 0.98782 | -0.23386 | 13.7389
102 | 0.01058 | 0.002652 | -0.010575 | -0.0026496 | 4.7057e-06 | 2.3854e-06 | 0.015975 | 0.015975 | 0.015975 | 0.9855 | -0.27911 | 0.98502 | -0.28844 | 4.3887
103 | 0.012567 | 0.0031499 | -0.012565 | -0.0031488 | 2.0568e-06 | 1.1233e-06 | 0.019001 | 0.019001 | 0.019001 | 0.98417 | -0.30499 | 0.98399 | -0.30843 | 5.2202
104 | -0.034265 | -0.0086135 | 0.034283 | 0.0086249 | 1.819e-05 | 1.1408e-05 | 0.051625 | 0.051625 | 0.051625 | 0.98782 | -0.23386 | 0.9884 | -0.22275 | 14.1826
105 | 0.0079683 | 0.0019963 | -0.0079647 | -0.0019948 | 3.5568e-06 | 1.4435e-06 | 0.012037 | 0.012037 | 0.012037 | 0.98502 | -0.28844 | 0.98454 | -0.29782 | 3.307
106 | 0.010458 | 0.0026207 | -0.010458 | -0.0026203 | 9.1092e-07 | 4.5964e-07 | 0.015815 | 0.015815 | 0.015815 | 0.98399 | -0.30843 | 0.9839 | -0.31026 | 4.3449
107 | 0.0062341 | 0.0015624 | -0.0062332 | -0.0015622 | 9.0648e-07 | 2.3484e-07 | 0.0094283 | 0.0094284 | 0.0094284 | 0.9839 | -0.31026 | 0.98374 | -0.31331 | 2.5902
108 | 0.0042234 | 0.0010579 | -0.0042233 | -0.0010579 | 1.4755e-07 | -2.8056e-08 | 0.0063871 | 0.0063872 | 0.0063872 | 0.9839 | -0.31026 | 0.98386 | -0.31099 | 1.7547
109 | -0.039528 | -0.0099394 | 0.039538 | 0.009946 | 1.0405e-05 | 6.5591e-06 | 0.059521 | 0.059521 | 0.059521 | 0.9884 | -0.22275 | 0.98868 | -0.21724 | 16.3518
110 | 0.0043172 | 0.0010807 | -0.0043155 | -0.0010809 | 1.7272e-06 | -2.6981e-07 | 0.0065245 | 0.006525 | 0.006525 | 0.98454 | -0.29782 | 0.98411 | -0.30623 | 1.7926
111 | 0.002851 | 0.00071396 | -0.0028507 | -0.00071431 | 2.9948e-07 | -3.5378e-07 | 0.0043117 | 0.0043119 | 0.0043119 | 0.98386 | -0.31099 | 0.98375 | -0.3132 | 1.1846
112 | 0.00085672 | 0.00021457 | -0.00085672 | -0.00021471 | 7.2178e-09 | -1.4091e-07 | 0.0012958 | 0.0012959 | 0.0012959 | 0.98375 | -0.3132 | 0.98374 | -0.31337 | 0.35601
113 | 0.0038766 | 0.00097095 | -0.0038765 | -0.00097098 | 7.3986e-08 | -2.5613e-08 | 0.0058614 | 0.0058614 | 0.0058614 | 0.98411 | -0.30623 | 0.98409 | -0.30663 | 1.6103
114 | 0.0069164 | 0.0017334 | -0.0069159 | -0.0017332 | 4.9933e-07 | 1.6324e-07 | 0.01043 | 0.01043 | 0.01043 | 0.98672 | -0.2549 | 0.98664 | -0.25641 | 2.8654
115 | 0.0069159 | 0.0017332 | -0.0069157 | -0.0017331 | 2.1438e-07 | 7.0095e-08 | 0.01043 | 0.01043 | 0.01043 | 0.98664 | -0.25641 | 0.98661 | -0.25706 | 2.8654
116 | 0.0069157 | 0.0017331 | -0.0069154 | -0.001733 | 2.8769e-07 | 9.4069e-08 | 0.01043 | 0.01043 | 0.01043 | 0.98661 | -0.25706 | 0.98657 | -0.25793 | 2.8655
117 | 0.0042837 | 0.0010735 | -0.0042834 | -0.0010735 | 3.0297e-07 | -5.3209e-08 | 0.006461 | 0.0064611 | 0.0064611 | 0.98657 | -0.25793 | 0.98649 | -0.25942 | 1.775
118 | 0.0070576 | 0.0017689 | -0.0070567 | -0.0017686 | 9.1018e-07 | 3.1106e-07 | 0.010665 | 0.010665 | 0.010665 | 0.98475 | -0.2937 | 0.98461 | -0.29641 | 2.9299
119 | 0.0018866 | 0.00047227 | -0.0018865 | -0.0004728 | 1.4975e-07 | -5.2759e-07 | 0.0028525 | 0.0028528 | 0.0028528 | 0.98409 | -0.30663 | 0.984 | -0.30829 | 0.78373

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.24262 | 0.061426

## res_load
| p_mw | q_mvar
0 | 0.0019308 | 0.0004839
1 | 0.0044913 | 0.0011256
2 | 0.0077665 | 0.0019465
3 | 0.0014799 | 0.0003709
4 | 0.0038232 | 0.00095819
5 | 0.00060378 | 0.00015132
6 | 0.00049354 | 0.00012369
7 | 0.0039363 | 0.00098652
8 | 0.0032698 | 0.00081948
9 | 0.0024402 | 0.00061156
10 | 0.0019379 | 0.00048567
11 | 0.0024328 | 0.00060971
12 | 0.0030511 | 0.00076468
13 | 0.0021933 | 0.0005497
14 | 0.0021933 | 0.0005497
15 | 0.0019396 | 0.0004861
16 | 0.0041031 | 0.0010283
17 | 0.0019107 | 0.00047886
18 | 0.0028238 | 0.00070772
19 | 0.002842 | 0.00071228
20 | 0.0012098 | 0.0003032
21 | 0.00093996 | 0.00023558
22 | 0.0021064 | 0.00052791
23 | 0.0048374 | 0.0012124
24 | 0.0018739 | 0.00046965
25 | 0.0028237 | 0.00070769
26 | 0.0025704 | 0.00064421
27 | 0.002568 | 0.00064359
28 | 0.0017784 | 0.0004457
29 | 0.0017765 | 0.00044523
30 | 0.003657 | 0.00091652
31 | 0.00039019 | 9.7791e-05
32 | 0.0025753 | 0.00064542
33 | 0.00093777 | 0.00023503
34 | 0.0013427 | 0.00033651
35 | 0.0016215 | 0.00040639
36 | 0.0018171 | 0.00045541
37 | 0.0018171 | 0.00045541
38 | 0.0025068 | 0.00062826
39 | 0.0025068 | 0.00062825
40 | 0.0020899 | 0.00052377
41 | 0.0012583 | 0.00031535
42 | 0.0012167 | 0.00030493
43 | 0.0010865 | 0.00027229
44 | 0.0026067 | 0.00065331
45 | 0.0012159 | 0.00030474
46 | 0.0011039 | 0.00027667
47 | 0.0035318 | 0.00088516
48 | 0.0003528 | 8.8421e-05
49 | 0.0012503 | 0.00031335
50 | 0.0049011 | 0.0012283
51 | 0.0016572 | 0.00041532
52 | 0.0029823 | 0.00074744
53 | 0.0041775 | 0.001047
54 | 0.0013074 | 0.00032766
55 | 0.010952 | 0.0027448
56 | 0.0021799 | 0.00054632
57 | 0.0020545 | 0.00051491
58 | 0.0084058 | 0.0021067
59 | 0.0034282 | 0.0008592
60 | 0.0018495 | 0.00046352
61 | 0.0029807 | 0.00074704
62 | 0.0027955 | 0.00070063
63 | 0.0020548 | 0.00051499
64 | 0.0049592 | 0.0012429
65 | 0.0019915 | 0.00049911
66 | 0.0021663 | 0.00054294
67 | 0.0054077 | 0.0013553
68 | 0.0018056 | 0.00045253
69 | 0.00059352 | 0.00014875
70 | 0.0010721 | 0.0002687
71 | 0.0026067 | 0.00065329
72 | 0.0021069 | 0.00052804
73 | 0.0052448 | 0.0013145
74 | 0.0036475 | 0.00091416
75 | 0.0013723 | 0.00034392
76 | 0.001994 | 0.00049974
77 | 0.00085672 | 0.00021471
78 | 0.0062332 | 0.0015622
79 | 0.0021752 | 0.00054516
80 | 0.00043888 | 0.00010999
81 | 0.0032745 | 0.00082067
82 | 0.0026316 | 0.00065955
83 | 0.0042834 | 0.0010735
84 | 0.0047476 | 0.0011899
85 | 0.0029187 | 0.00073151
86 | 0.0070567 | 0.0017686
87 | 0.0019899 | 0.00049871
88 | 0.0018865 | 0.0004728

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1