## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1058-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1058-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1058-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1058-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1058-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1058-9_0_4_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1058-9_0_4_node_94 | 0.4 | n |  | TRUE
7 | bus_LV_1058-9_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1058-9_0_4_node_103 | 0.4 | n |  | TRUE
9 | bus_LV_1058-9_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1058-9_0_4_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1058-9_0_4_node_106 | 0.4 | n |  | TRUE
12 | bus_LV_1058-9_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1058-9_0_4_node_95 | 0.4 | n |  | TRUE
14 | bus_LV_1058-9_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1058-9_0_4_node_99 | 0.4 | n |  | TRUE
16 | bus_LV_1058-9_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1058-9_0_4_node_98 | 0.4 | n |  | TRUE
18 | bus_LV_1058-9_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1058-9_0_4_node_96 | 0.4 | n |  | TRUE
20 | bus_LV_1058-9_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1058-9_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1058-9_0_4_node_78 | 0.4 | n |  | TRUE
23 | bus_LV_1058-9_0_4_node_101 | 0.4 | n |  | TRUE
24 | bus_LV_1058-9_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1058-9_0_4_node_57 | 0.4 | n |  | TRUE
26 | bus_LV_1058-9_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1058-9_0_4_node_110 | 0.4 | n |  | TRUE
28 | bus_LV_1058-9_0_4_node_111 | 0.4 | n |  | TRUE
29 | bus_LV_1058-9_0_4_node_141 | 0.4 | n |  | TRUE
30 | bus_LV_1058-9_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1058-9_0_4_node_104 | 0.4 | n |  | TRUE
32 | bus_LV_1058-9_0_4_node_118 | 0.4 | n |  | TRUE
33 | bus_LV_1058-9_0_4_node_79 | 0.4 | n |  | TRUE
34 | bus_LV_1058-9_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1058-9_0_4_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_1058-9_0_4_node_112 | 0.4 | n |  | TRUE
37 | bus_LV_1058-9_0_4_node_113 | 0.4 | n |  | TRUE
38 | bus_LV_1058-9_0_4_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_1058-9_0_4_node_102 | 0.4 | n |  | TRUE
40 | bus_LV_1058-9_0_4_node_100 | 0.4 | n |  | TRUE
41 | bus_LV_1058-9_0_4_node_81 | 0.4 | n |  | TRUE
42 | bus_LV_1058-9_0_4_node_107 | 0.4 | n |  | TRUE
43 | bus_LV_1058-9_0_4_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_1058-9_0_4_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_1058-9_0_4_node_143 | 0.4 | n |  | TRUE
46 | bus_LV_1058-9_0_4_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_1058-9_0_4_node_80 | 0.4 | n |  | TRUE
48 | bus_LV_1058-9_0_4_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_1058-9_0_4_node_115 | 0.4 | n |  | TRUE
50 | bus_LV_1058-9_0_4_node_116 | 0.4 | n |  | TRUE
51 | bus_LV_1058-9_0_4_node_109 | 0.4 | n |  | TRUE
52 | bus_LV_1058-9_0_4_node_83 | 0.4 | n |  | TRUE
53 | bus_LV_1058-9_0_4_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_1058-9_0_4_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_1058-9_0_4_node_130 | 0.4 | n |  | TRUE
56 | bus_LV_1058-9_0_4_node_131 | 0.4 | n |  | TRUE
57 | bus_LV_1058-9_0_4_node_128 | 0.4 | n |  | TRUE
58 | bus_LV_1058-9_0_4_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_1058-9_0_4_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_1058-9_0_4_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_1058-9_0_4_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_1058-9_0_4_node_76 | 0.4 | n |  | TRUE
63 | bus_LV_1058-9_0_4_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_1058-9_0_4_node_125 | 0.4 | n |  | TRUE
65 | bus_LV_1058-9_0_4_node_82 | 0.4 | n |  | TRUE
66 | bus_LV_1058-9_0_4_node_108 | 0.4 | n |  | TRUE
67 | bus_LV_1058-9_0_4_node_25 | 0.4 | n |  | TRUE
68 | bus_LV_1058-9_0_4_node_26 | 0.4 | n |  | TRUE
69 | bus_LV_1058-9_0_4_node_27 | 0.4 | n |  | TRUE
70 | bus_LV_1058-9_0_4_node_29 | 0.4 | n |  | TRUE
71 | bus_LV_1058-9_0_4_node_31 | 0.4 | n |  | TRUE
72 | bus_LV_1058-9_0_4_node_33 | 0.4 | n |  | TRUE
73 | bus_LV_1058-9_0_4_node_35 | 0.4 | n |  | TRUE
74 | bus_LV_1058-9_0_4_node_36 | 0.4 | n |  | TRUE
75 | bus_LV_1058-9_0_4_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_1058-9_0_4_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_1058-9_0_4_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_1058-9_0_4_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_1058-9_0_4_node_42 | 0.4 | n |  | TRUE
80 | bus_LV_1058-9_0_4_node_37 | 0.4 | n |  | TRUE
81 | bus_LV_1058-9_0_4_node_38 | 0.4 | n |  | TRUE
82 | bus_LV_1058-9_0_4_node_39 | 0.4 | n |  | TRUE
83 | bus_LV_1058-9_0_4_node_40 | 0.4 | n |  | TRUE
84 | bus_LV_1058-9_0_4_node_41 | 0.4 | n |  | TRUE
85 | bus_LV_1058-9_0_4_node_50 | 0.4 | n |  | TRUE
86 | bus_LV_1058-9_0_4_node_51 | 0.4 | n |  | TRUE
87 | bus_LV_1058-9_0_4_node_47 | 0.4 | n |  | TRUE
88 | bus_LV_1058-9_0_4_node_45 | 0.4 | n |  | TRUE
89 | bus_LV_1058-9_0_4_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_1058-9_0_4_node_145 | 0.4 | n |  | TRUE
91 | bus_LV_1058-9_0_4_node_46 | 0.4 | n |  | TRUE
92 | bus_LV_1058-9_0_4_node_144 | 0.4 | n |  | TRUE
93 | bus_LV_1058-9_0_4_node_123 | 0.4 | n |  | TRUE
94 | bus_LV_1058-9_0_4_node_52 | 0.4 | n |  | TRUE
95 | bus_LV_1058-9_0_4_node_132 | 0.4 | n |  | TRUE
96 | bus_LV_1058-9_0_4_node_48 | 0.4 | n |  | TRUE
97 | bus_LV_1058-9_0_4_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_1058-9_0_4_node_58 | 0.4 | n |  | TRUE
99 | bus_LV_1058-9_0_4_node_72 | 0.4 | n |  | TRUE
100 | bus_LV_1058-9_0_4_node_117 | 0.4 | n |  | TRUE
101 | bus_LV_1058-9_0_4_node_121 | 0.4 | n |  | TRUE
102 | bus_LV_1058-9_0_4_node_49 | 0.4 | n |  | TRUE
103 | bus_LV_1058-9_0_4_node_53 | 0.4 | n |  | TRUE
104 | bus_LV_1058-9_0_4_node_133 | 0.4 | n |  | TRUE
105 | bus_LV_1058-9_0_4_node_54 | 0.4 | n |  | TRUE
106 | bus_LV_1058-9_0_4_node_59 | 0.4 | n |  | TRUE
107 | bus_LV_1058-9_0_4_node_61 | 0.4 | n |  | TRUE
108 | bus_LV_1058-9_0_4_node_62 | 0.4 | n |  | TRUE
109 | bus_LV_1058-9_0_4_node_63 | 0.4 | n |  | TRUE
110 | bus_LV_1058-9_0_4_node_64 | 0.4 | n |  | TRUE
111 | bus_LV_1058-9_0_4_node_66 | 0.4 | n |  | TRUE
112 | bus_LV_1058-9_0_4_node_67 | 0.4 | n |  | TRUE
113 | bus_LV_1058-9_0_4_node_74 | 0.4 | n |  | TRUE
114 | bus_LV_1058-9_0_4_node_68 | 0.4 | n |  | TRUE
115 | bus_LV_1058-9_0_4_node_71 | 0.4 | n |  | TRUE
116 | bus_LV_1058-9_0_4_node_73 | 0.4 | n |  | TRUE
117 | bus_LV_1058-9_0_4_node_142 | 0.4 | n |  | TRUE
118 | bus_LV_1058-9_0_4_node_88 | 0.4 | n |  | TRUE
119 | bus_LV_1058-9_0_4_node_93 | 0.4 | n |  | TRUE
120 | bus_LV_1058-9_0_4_node_86 | 0.4 | n |  | TRUE
121 | bus_LV_1058-9_0_4_node_140 | 0.4 | n |  | TRUE
122 | bus_LV_1058-9_0_4_node_139 | 0.4 | n |  | TRUE
123 | bus_LV_1058-9_0_4_node_135 | 0.4 | n |  | TRUE
124 | bus_LV_1058-9_0_4_node_146 | 0.4 | n |  | TRUE
125 | bus_LV_1058-9_0_4_node_134 | 0.4 | n |  | TRUE
126 | bus_LV_1058-9_0_4_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_1058-9_0_4_node_136 | 0.4 | n |  | TRUE
128 | bus_LV_1058-9_0_4_node_137 | 0.4 | n |  | TRUE
129 | bus_LV_1058-9_0_4_node_85 | 0.4 | n |  | TRUE
130 | bus_LV_1058-9_0_4_node_87 | 0.4 | n |  | TRUE
131 | bus_LV_1058-9_0_4_node_89 | 0.4 | n |  | TRUE
132 | bus_LV_1058-9_0_4_node_92 | 0.4 | n |  | TRUE
133 | bus_LV_1058-9_0_4_node_90 | 0.4 | n |  | TRUE
134 | bus_LV_1058-9_0_4_node_91 | 0.4 | n |  | TRUE
135 | bus_LV_1058-9_0_4_node_119 | 0.4 | n |  | TRUE
136 | bus_LV_1058-9_0_4_node_120 | 0.4 | n |  | TRUE
137 | bus_LV_1058-9_0_4_node_122 | 0.4 | n |  | TRUE
138 | bus_LV_1058-9_0_4_node_124 | 0.4 | n |  | TRUE
139 | bus_LV_1058-9_0_4_node_127 | 0.4 | n |  | TRUE
140 | bus_MV_23_0_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1058-9_0_4_load_0 | 0 | 0.00085641 | 0.00021464 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1058-9_0_4_load_1 | 1 | 0.0010323 | 0.00025872 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1058-9_0_4_load_3 | 3 | 0.00053679 | 0.00013453 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1058-9_0_4_load_30 | 5 | 0.00049542 | 0.00012416 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1058-9_0_4_load_94 | 6 | 0.00023024 | 5.7705e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1058-9_0_4_load_103 | 8 | 0.00028778 | 7.2125e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1058-9_0_4_load_106 | 11 | 0.0017095 | 0.00042844 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1058-9_0_4_load_95 | 13 | 0.00036921 | 9.2534e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1058-9_0_4_load_99 | 15 | 0.0040697 | 0.00102 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1058-9_0_4_load_98 | 17 | 0.0012906 | 0.00032345 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1058-9_0_4_load_96 | 19 | 0.0018867 | 0.00047285 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1058-9_0_4_load_101 | 23 | 0.0008682 | 0.00021759 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1058-9_0_4_load_110 | 27 | 0.0025105 | 0.00062918 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1058-9_0_4_load_111 | 28 | 0.0078276 | 0.0019618 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1058-9_0_4_load_141 | 29 | 0.00046342 | 0.00011615 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1058-9_0_4_load_118 | 32 | 0.0011662 | 0.00029228 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1058-9_0_4_load_79 | 33 | 0.019293 | 0.0048353 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1058-9_0_4_load_112 | 36 | 0.0021633 | 0.00054217 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1058-9_0_4_load_113 | 37 | 0.0017797 | 0.00044603 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1058-9_0_4_load_102 | 39 | 0.00073213 | 0.00018349 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1058-9_0_4_load_100 | 40 | 0.00051301 | 0.00012857 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1058-9_0_4_load_107 | 42 | 0.0012158 | 0.0003047 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1058-9_0_4_load_143 | 45 | 0.0028987 | 0.00072648 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1058-9_0_4_load_105 | 46 | 0.0017399 | 0.00043605 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1058-9_0_4_load_80 | 47 | 0.018403 | 0.0046123 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1058-9_0_4_load_28 | 48 | 0.00019436 | 4.8712e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1058-9_0_4_load_115 | 49 | 0.0025665 | 0.00064321 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1058-9_0_4_load_116 | 50 | 0.0012834 | 0.00032164 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1058-9_0_4_load_109 | 51 | 0.0022428 | 0.0005621 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1058-9_0_4_load_77 | 53 | 0.012224 | 0.0030636 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1058-9_0_4_load_130 | 55 | 0.001179 | 0.00029548 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1058-9_0_4_load_131 | 56 | 0.0022432 | 0.00056219 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1058-9_0_4_load_128 | 57 | 0.00057959 | 0.00014526 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1058-9_0_4_load_129 | 59 | 0.0092086 | 0.0023079 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1058-9_0_4_load_55 | 60 | 0.0026178 | 0.00065608 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1058-9_0_4_load_32 | 61 | 0.0019544 | 0.00048981 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1058-9_0_4_load_76 | 62 | 0.0069587 | 0.001744 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1058-9_0_4_load_114 | 63 | 0.0028758 | 0.00072074 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1058-9_0_4_load_125 | 64 | 0.003306 | 0.00082855 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1058-9_0_4_load_108 | 66 | 0.00086171 | 0.00021597 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1058-9_0_4_load_25 | 67 | 0.00077144 | 0.00019334 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1058-9_0_4_load_26 | 68 | 0.00030987 | 7.766e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1058-9_0_4_load_29 | 70 | 0.00020288 | 5.0846e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1058-9_0_4_load_31 | 71 | 0.00080439 | 0.0002016 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1058-9_0_4_load_35 | 73 | 0.0037903 | 0.00094995 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1058-9_0_4_load_36 | 74 | 0.0025218 | 0.00063201 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1058-9_0_4_load_65 | 77 | 0.001177 | 0.00029499 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1058-9_0_4_load_60 | 78 | 0.0018772 | 0.00047047 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1058-9_0_4_load_42 | 79 | 0.0010395 | 0.00026052 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1058-9_0_4_load_37 | 80 | 0.0014353 | 0.00035971 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1058-9_0_4_load_38 | 81 | 0.0010176 | 0.00025504 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1058-9_0_4_load_50 | 85 | 0.0017586 | 0.00044075 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1058-9_0_4_load_51 | 86 | 0.0024265 | 0.00060813 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1058-9_0_4_load_47 | 87 | 0.00092349 | 0.00023145 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1058-9_0_4_load_69 | 89 | 0.0012465 | 0.0003124 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1058-9_0_4_load_145 | 90 | 0.0018827 | 0.00047186 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1058-9_0_4_load_144 | 92 | 0.0017004 | 0.00042616 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1058-9_0_4_load_52 | 94 | 0.00095905 | 0.00024036 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1058-9_0_4_load_132 | 95 | 0.0013672 | 0.00034266 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1058-9_0_4_load_48 | 96 | 0.0015248 | 0.00038214 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1058-9_0_4_load_70 | 97 | 0.001514 | 0.00037946 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1058-9_0_4_load_58 | 98 | 0.0020587 | 0.00051595 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1058-9_0_4_load_117 | 100 | 0.0013395 | 0.0003357 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1058-9_0_4_load_121 | 101 | 0.0014204 | 0.00035598 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1058-9_0_4_load_49 | 102 | 0.0024893 | 0.00062387 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1058-9_0_4_load_53 | 103 | 0.0020088 | 0.00050346 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1058-9_0_4_load_133 | 104 | 0.0074653 | 0.001871 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1058-9_0_4_load_54 | 105 | 0.0010787 | 0.00027034 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1058-9_0_4_load_59 | 106 | 0.001803 | 0.00045187 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1058-9_0_4_load_61 | 107 | 0.0018009 | 0.00045135 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1058-9_0_4_load_62 | 108 | 0.0018776 | 0.00047058 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1058-9_0_4_load_63 | 109 | 0.0018841 | 0.00047221 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1058-9_0_4_load_64 | 110 | 0.0018852 | 0.00047247 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1058-9_0_4_load_66 | 111 | 0.0018324 | 0.00045924 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1058-9_0_4_load_67 | 112 | 0.001833 | 0.00045938 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1058-9_0_4_load_68 | 114 | 0.0039357 | 0.00098638 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1058-9_0_4_load_71 | 115 | 0.0016766 | 0.00042018 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1058-9_0_4_load_142 | 117 | 0.0017372 | 0.00043537 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1058-9_0_4_load_93 | 119 | 0.00052757 | 0.00013222 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1058-9_0_4_load_86 | 120 | 0.00028514 | 7.1462e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1058-9_0_4_load_139 | 122 | 0.0015484 | 0.00038806 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1058-9_0_4_load_135 | 123 | 0.0020694 | 0.00051864 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1058-9_0_4_load_146 | 124 | 0.0020695 | 0.00051866 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1058-9_0_4_load_134 | 125 | 0.0017236 | 0.00043198 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1058-9_0_4_load_138 | 126 | 0.0015452 | 0.00038726 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1058-9_0_4_load_137 | 128 | 0.0043204 | 0.0010828 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1058-9_0_4_load_85 | 129 | 0.00066659 | 0.00016706 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1058-9_0_4_load_87 | 130 | 0.0015324 | 0.00038406 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1058-9_0_4_load_89 | 131 | 0.00019258 | 4.8264e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1058-9_0_4_load_92 | 132 | 0.00056944 | 0.00014272 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1058-9_0_4_load_90 | 133 | 0.0035655 | 0.00089359 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1058-9_0_4_load_91 | 134 | 0.0018211 | 0.00045641 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1058-9_0_4_load_119 | 135 | 0.0010902 | 0.00027322 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1058-9_0_4_load_120 | 136 | 0.0013147 | 0.0003295 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1058-9_0_4_load_122 | 137 | 0.0014453 | 0.00036224 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1058-9_0_4_load_124 | 138 | 0.0014547 | 0.00036458 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1058-9_0_4_load_127 | 139 | 0.0010705 | 0.00026829 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1058-9_0_4_line_0 |  | 0 | 1 | 0.00064475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1058-9_0_4_line_1 |  | 0 | 2 | 0.12755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1058-9_0_4_line_2 |  | 1 | 3 | 0.03094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1058-9_0_4_line_3 |  | 2 | 4 | 0.12467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1058-9_0_4_line_4 |  | 3 | 5 | 0.0049041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1058-9_0_4_line_5 |  | 4 | 6 | 0.0041144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1058-9_0_4_line_6 |  | 5 | 48 | 0.033942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1058-9_0_4_line_7 |  | 6 | 13 | 0.018123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1058-9_0_4_line_8 |  | 7 | 8 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1058-9_0_4_line_9 |  | 7 | 9 | 0.18664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1058-9_0_4_line_10 |  | 7 | 10 | 0.042143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1058-9_0_4_line_11 |  | 7 | 11 | 0.052562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1058-9_0_4_line_12 |  | 8 | 12 | 0.0072607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1058-9_0_4_line_13 |  | 9 | 29 | 0.021193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1058-9_0_4_line_14 |  | 9 | 18 | 0.004534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1058-9_0_4_line_15 |  | 10 | 41 | 0.11635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1058-9_0_4_line_16 |  | 10 | 42 | 0.051319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1058-9_0_4_line_17 |  | 12 | 13 | 0.0098159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1058-9_0_4_line_18 |  | 14 | 15 | 0.032156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1058-9_0_4_line_19 |  | 14 | 16 | 0.048555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1058-9_0_4_line_20 |  | 14 | 17 | 0.058769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1058-9_0_4_line_21 |  | 15 | 51 | 0.0044641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1058-9_0_4_line_22 |  | 16 | 28 | 0.015332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1058-9_0_4_line_23 |  | 16 | 24 | 0.010611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1058-9_0_4_line_24 |  | 17 | 21 | 0.0663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1058-9_0_4_line_25 |  | 18 | 19 | 0.09674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1058-9_0_4_line_26 |  | 20 | 21 | 0.031635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1058-9_0_4_line_27 |  | 20 | 22 | 0.072911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1058-9_0_4_line_28 |  | 20 | 23 | 0.02158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1058-9_0_4_line_29 |  | 22 | 52 | 0.044988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1058-9_0_4_line_30 |  | 22 | 53 | 0.016694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1058-9_0_4_line_31 |  | 23 | 43 | 0.00074631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1058-9_0_4_line_32 |  | 24 | 25 | 0.19443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1058-9_0_4_line_33 |  | 24 | 26 | 0.058082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1058-9_0_4_line_34 |  | 24 | 27 | 0.040874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1058-9_0_4_line_35 |  | 25 | 59 | 0.010059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1058-9_0_4_line_36 |  | 25 | 57 | 0.0036663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1058-9_0_4_line_37 |  | 26 | 33 | 0.00045285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1058-9_0_4_line_38 |  | 26 | 34 | 0.03941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1058-9_0_4_line_39 |  | 28 | 35 | 0.028018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1058-9_0_4_line_40 |  | 30 | 31 | 0.002589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1058-9_0_4_line_41 |  | 30 | 32 | 0.016695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1058-9_0_4_line_42 |  | 31 | 39 | 0.0059676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1058-9_0_4_line_43 |  | 31 | 46 | 0.021347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1058-9_0_4_line_44 |  | 34 | 47 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1058-9_0_4_line_45 |  | 35 | 36 | 0.029618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1058-9_0_4_line_46 |  | 35 | 37 | 0.017472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1058-9_0_4_line_47 |  | 36 | 63 | 0.058049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1058-9_0_4_line_48 |  | 37 | 64 | 0.0067551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1058-9_0_4_line_49 |  | 38 | 39 | 0.013325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1058-9_0_4_line_50 |  | 38 | 40 | 0.007188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1058-9_0_4_line_51 |  | 40 | 43 | 0.030415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1058-9_0_4_line_52 |  | 41 | 65 | 0.047923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1058-9_0_4_line_53 |  | 42 | 66 | 0.019164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1058-9_0_4_line_54 |  | 44 | 45 | 0.003566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1058-9_0_4_line_55 |  | 44 | 46 | 0.063316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1058-9_0_4_line_56 |  | 48 | 68 | 0.047223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1058-9_0_4_line_57 |  | 49 | 50 | 0.0049275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1058-9_0_4_line_58 |  | 50 | 100 | 0.0077519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1058-9_0_4_line_59 |  | 52 | 121 | 0.014038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1058-9_0_4_line_60 |  | 52 | 122 | 0.020494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1058-9_0_4_line_61 |  | 53 | 62 | 0.010305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1058-9_0_4_line_62 |  | 54 | 55 | 0.014891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1058-9_0_4_line_63 |  | 54 | 56 | 0.033101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1058-9_0_4_line_64 |  | 54 | 57 | 0.019411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_1058-9_0_4_line_65 |  | 54 | 58 | 0.15161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1058-9_0_4_line_66 |  | 58 | 60 | 0.0312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1058-9_0_4_line_67 |  | 58 | 61 | 0.016183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1058-9_0_4_line_68 |  | 61 | 71 | 0.025722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1058-9_0_4_line_69 |  | 65 | 121 | 0.025994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1058-9_0_4_line_70 |  | 65 | 123 | 0.023836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1058-9_0_4_line_71 |  | 67 | 68 | 0.0090269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1058-9_0_4_line_72 |  | 67 | 69 | 0.044915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1058-9_0_4_line_73 |  | 69 | 70 | 0.05757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1058-9_0_4_line_74 |  | 71 | 72 | 0.007966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1058-9_0_4_line_75 |  | 72 | 73 | 0.0077377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1058-9_0_4_line_76 |  | 72 | 74 | 0.023489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_1058-9_0_4_line_77 |  | 73 | 75 | 0.0079588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1058-9_0_4_line_78 |  | 74 | 76 | 0.086086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_1058-9_0_4_line_79 |  | 75 | 77 | 0.012412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1058-9_0_4_line_80 |  | 76 | 78 | 0.01591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1058-9_0_4_line_81 |  | 76 | 79 | 0.035512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1058-9_0_4_line_82 |  | 77 | 99 | 0.078642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1058-9_0_4_line_83 |  | 78 | 98 | 0.0029343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1058-9_0_4_line_84 |  | 79 | 82 | 0.030339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1058-9_0_4_line_85 |  | 80 | 81 | 0.0022027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1058-9_0_4_line_86 |  | 80 | 82 | 0.013521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1058-9_0_4_line_87 |  | 81 | 83 | 0.024306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1058-9_0_4_line_88 |  | 82 | 84 | 0.049606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1058-9_0_4_line_89 |  | 83 | 85 | 0.018907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1058-9_0_4_line_90 |  | 83 | 86 | 0.03396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1058-9_0_4_line_91 |  | 83 | 87 | 0.0094118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1058-9_0_4_line_92 |  | 84 | 88 | 0.051781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1058-9_0_4_line_93 |  | 84 | 89 | 0.011707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1058-9_0_4_line_94 |  | 85 | 94 | 0.0026888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1058-9_0_4_line_95 |  | 86 | 95 | 0.027777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1058-9_0_4_line_96 |  | 87 | 96 | 0.0036776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1058-9_0_4_line_97 |  | 88 | 90 | 0.019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1058-9_0_4_line_98 |  | 88 | 91 | 0.0080721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1058-9_0_4_line_99 |  | 89 | 97 | 0.024967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1058-9_0_4_line_100 |  | 91 | 92 | 0.020975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1058-9_0_4_line_101 |  | 91 | 93 | 0.034511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1058-9_0_4_line_102 |  | 93 | 100 | 0.020229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1058-9_0_4_line_103 |  | 93 | 101 | 0.018798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1058-9_0_4_line_104 |  | 94 | 103 | 0.025072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1058-9_0_4_line_105 |  | 95 | 104 | 0.019182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1058-9_0_4_line_106 |  | 96 | 102 | 0.016971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1058-9_0_4_line_107 |  | 97 | 115 | 0.026405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1058-9_0_4_line_108 |  | 98 | 106 | 0.013485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1058-9_0_4_line_109 |  | 99 | 113 | 0.19594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1058-9_0_4_line_110 |  | 101 | 135 | 0.0078577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1058-9_0_4_line_111 |  | 103 | 105 | 0.0043816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1058-9_0_4_line_112 |  | 106 | 107 | 0.006319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1058-9_0_4_line_113 |  | 107 | 108 | 0.0044125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1058-9_0_4_line_114 |  | 108 | 109 | 0.011916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1058-9_0_4_line_115 |  | 109 | 110 | 0.0067426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1058-9_0_4_line_116 |  | 110 | 111 | 0.0041618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1058-9_0_4_line_117 |  | 111 | 112 | 0.0064833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1058-9_0_4_line_118 |  | 112 | 114 | 0.008439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1058-9_0_4_line_119 |  | 113 | 119 | 0.034337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1058-9_0_4_line_120 |  | 113 | 116 | 0.075035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1058-9_0_4_line_121 |  | 116 | 117 | 0.175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1058-9_0_4_line_122 |  | 116 | 118 | 0.033622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1058-9_0_4_line_123 |  | 118 | 120 | 0.23473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1058-9_0_4_line_124 |  | 120 | 129 | 0.0059993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1058-9_0_4_line_125 |  | 121 | 124 | 0.00766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1058-9_0_4_line_126 |  | 122 | 126 | 0.010566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1058-9_0_4_line_127 |  | 123 | 125 | 0.041246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1058-9_0_4_line_128 |  | 125 | 127 | 0.02472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1058-9_0_4_line_129 |  | 127 | 128 | 0.02278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1058-9_0_4_line_130 |  | 129 | 130 | 0.0075018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1058-9_0_4_line_131 |  | 130 | 131 | 0.076517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1058-9_0_4_line_132 |  | 131 | 132 | 0.0061068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1058-9_0_4_line_133 |  | 132 | 133 | 0.091138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1058-9_0_4_line_134 |  | 133 | 134 | 0.0015788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1058-9_0_4_line_135 |  | 135 | 136 | 0.0090706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1058-9_0_4_line_136 |  | 136 | 137 | 0.015398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1058-9_0_4_line_137 |  | 137 | 138 | 0.013146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1058-9_0_4_line_138 |  | 138 | 139 | 0.0089422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1058-9_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 140 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2667795.2967 | 1207891.7633 | 2667794.6542 | 1207891.8169
1 | 2667683.9107 | 1207853.488 | 2667687.5882 | 1207857.0763 | 2667693.1708 | 1207863.6325 | 2667699.76 | 1207875.3032 | 2667705.9767 | 1207882.934 | 2667712.7618 | 1207887.3803 | 2667718.5016 | 1207889.4689 | 2667727.2352 | 1207891.0578 | 2667734.1704 | 1207891.6591 | 2667747.4038 | 1207892.0317 | 2667793.5281 | 1207891.9107 | 2667794.6542 | 1207891.8169
2 | 2667826.1352 | 1207889.2623 | 2667813.727 | 1207890.2279 | 2667795.2967 | 1207891.7633
3 | 2667683.9107 | 1207853.488 | 2667683.049 | 1207860.4158 | 2667680.6823 | 1207871.9849 | 2667677.2895 | 1207882.1861 | 2667674.0411 | 1207899.0929 | 2667668.7535 | 1207932.2311 | 2667663.589 | 1207960.5455 | 2667660.5798 | 1207975.8097
4 | 2667826.1352 | 1207889.2623 | 2667831.0245 | 1207888.8818
5 | 2667660.5798 | 1207975.8097 | 2667659.5898 | 1207979.8031
6 | 2667831.0245 | 1207888.8818 | 2667837.6612 | 1207888.3653 | 2667857.5916 | 1207882.2103 | 2667863.7389 | 1207880.3394
7 | 2667659.5898 | 1207979.8031 | 2667656.4844 | 1207992.3289 | 2667655.5763 | 1207997.4674
8 | 2667655.8013 | 1208033.8022 | 2667652.7617 | 1208028.9537 | 2667651.7588 | 1208022.8497 | 2667652.2269 | 1208017.107 | 2667652.7496 | 1208014.304
9 | 2667820.8477 | 1208103.284 | 2667757.4773 | 1208078.9496 | 2667738.289 | 1208072.0498 | 2667689.061 | 1208054.3362 | 2667653.1855 | 1208041.1993 | 2667653.759 | 1208039.5715 | 2667655.5186 | 1208034.5884 | 2667655.8013 | 1208033.8022
10 | 2667638.3722 | 1208064.8571 | 2667644.4745 | 1208062.447 | 2667651.7233 | 1208060.8503 | 2667650.0588 | 1208050.0693 | 2667650.9623 | 1208047.5002 | 2667652.7849 | 1208042.3288 | 2667653.1855 | 1208041.1993 | 2667653.759 | 1208039.5715 | 2667655.5186 | 1208034.5884 | 2667655.8013 | 1208033.8022
11 | 2667655.8013 | 1208033.8022 | 2667659.5075 | 1208036.179 | 2667665.1993 | 1208038.4671 | 2667696.7257 | 1208050.9321 | 2667704.2819 | 1208053.9157
12 | 2667654.0808 | 1208007.1664 | 2667652.7496 | 1208014.304
13 | 2667820.8477 | 1208103.284 | 2667841.4027 | 1208108.4456
14 | 2667820.8477 | 1208103.284 | 2667820.1809 | 1208107.7681
15 | 2667638.3722 | 1208064.8571 | 2667636.6156 | 1208065.5487 | 2667630.3235 | 1208068.6016 | 2667626.6398 | 1208071.6061 | 2667616.9938 | 1208081.4473 | 2667603.6751 | 1208093.326 | 2667589.0185 | 1208104.5225 | 2667572.0424 | 1208116.4377 | 2667556.9017 | 1208124.7381 | 2667543.4935 | 1208131.1125
16 | 2667638.3722 | 1208064.8571 | 2667639.3608 | 1208066.8473 | 2667642.1844 | 1208080.6878 | 2667643.1495 | 1208094.1514 | 2667640.1972 | 1208111.1173 | 2667640.5217 | 1208115.3569
17 | 2667654.0808 | 1208007.1664 | 2667654.7295 | 1208002.2596 | 2667655.5763 | 1207997.4674
18 | 2667436.6544 | 1208207.7074 | 2667436.8352 | 1208208.5321 | 2667438.1532 | 1208215.0177 | 2667442.7905 | 1208237.9397 | 2667443.0843 | 1208239.2129
19 | 2667436.6544 | 1208207.7074 | 2667428.5744 | 1208206.1818 | 2667418.1581 | 1208204.163 | 2667412.1461 | 1208202.6386 | 2667409.8652 | 1208201.9569 | 2667408.0858 | 1208200.636 | 2667406.4211 | 1208199.2608 | 2667402.1325 | 1208193.9091 | 2667399.2813 | 1208191.2197 | 2667397.3819 | 1208190.4311 | 2667393.4049 | 1208191.1533
20 | 2667436.6544 | 1208207.7074 | 2667451.8004 | 1208210.3468 | 2667462.2625 | 1208213.011 | 2667471.8397 | 1208217.2886 | 2667479.2486 | 1208221.0079 | 2667489.0122 | 1208227.6223 | 2667490.5459 | 1208228.9465
21 | 2667443.0843 | 1208239.2129 | 2667443.6675 | 1208241.7408 | 2667443.9658 | 1208243.5867
22 | 2667393.4049 | 1208191.1533 | 2667391.9683 | 1208191.793 | 2667386.6746 | 1208196.0025 | 2667380.1448 | 1208198.5145
23 | 2667388.1938 | 1208181.9889 | 2667391.1147 | 1208185.9131 | 2667392.8564 | 1208189.9019 | 2667393.4049 | 1208191.1533
24 | 2667529.8851 | 1208281.4731 | 2667523.6819 | 1208267.9613 | 2667514.4233 | 1208254.3593 | 2667504.7755 | 1208242.2206 | 2667497.4152 | 1208234.8773 | 2667490.5459 | 1208228.9465
25 | 2667820.1809 | 1208107.7681 | 2667816.9453 | 1208129.5447 | 2667817.8188 | 1208134.9802 | 2667819.9999 | 1208141.7535 | 2667835.6666 | 1208168.1477 | 2667837.4783 | 1208173.9719 | 2667837.5449 | 1208184.8349 | 2667835.1783 | 1208199.0862
26 | 2667529.8851 | 1208281.4731 | 2667534.1191 | 1208291.6272 | 2667538.8103 | 1208289.6012 | 2667534.0983 | 1208278.6857 | 2667537.5184 | 1208277.457
27 | 2667492.9141 | 1208220.7622 | 2667499.1697 | 1208225.6248 | 2667509.7074 | 1208235.7168 | 2667516.103 | 1208242.9825 | 2667520.8 | 1208249.1838 | 2667524.1636 | 1208253.6135 | 2667531.299 | 1208264.701 | 2667537.5184 | 1208277.457
28 | 2667537.5184 | 1208277.457 | 2667557.8322 | 1208270.1753
29 | 2667492.9141 | 1208220.7622 | 2667508.2192 | 1208216.0546 | 2667515.0562 | 1208212.5297 | 2667526.543 | 1208194.5264
30 | 2667492.9141 | 1208220.7622 | 2667489.0402 | 1208217.7499 | 2667479.2842 | 1208211.1356 | 2667479.2842 | 1208211.1356
31 | 2667557.8322 | 1208270.1753 | 2667558.5348 | 1208269.9234
32 | 2667293.908 | 1208051.1452 | 2667272.774 | 1208082.5597 | 2667281.9353 | 1208102.1749 | 2667286.9355 | 1208111.1812 | 2667293.9747 | 1208119.3878 | 2667301.6626 | 1208125.367 | 2667332.6824 | 1208140.9708 | 2667343.0089 | 1208147.5913 | 2667384.2845 | 1208176.7193 | 2667388.1938 | 1208181.9889
33 | 2667388.1938 | 1208181.9889 | 2667391.1147 | 1208185.9131 | 2667403.287 | 1208181.2255 | 2667436.7225 | 1208168.0505 | 2667438.0534 | 1208171.3787 | 2667438.2825 | 1208171.9594
34 | 2667388.1938 | 1208181.9889 | 2667383.8181 | 1208183.685 | 2667362.1802 | 1208192.3795 | 2667350.224 | 1208197.1204
35 | 2667293.908 | 1208051.1452 | 2667302.3773 | 1208056.6107
36 | 2667293.908 | 1208051.1452 | 2667290.9807 | 1208048.9379
37 | 2667438.2825 | 1208171.9594 | 2667438.7058 | 1208171.7984
38 | 2667438.2825 | 1208171.9594 | 2667438.0534 | 1208171.3787 | 2667436.7225 | 1208168.0505 | 2667435.3989 | 1208164.7446 | 2667435.0514 | 1208163.8735 | 2667443.483 | 1208160.5334 | 2667448.637 | 1208157.9233 | 2667452.8723 | 1208155.2028 | 2667449.9412 | 1208144.7855
39 | 2667353.2022 | 1208205.7419 | 2667356.9596 | 1208204.2612 | 2667372.6925 | 1208201.3814 | 2667380.1448 | 1208198.5145
40 | 2667612.0951 | 1208250.7291 | 2667612.9799 | 1208253.1628
41 | 2667612.9799 | 1208253.1628 | 2667618.6899 | 1208268.8508
42 | 2667612.0951 | 1208250.7291 | 2667606.4775 | 1208252.7426
43 | 2667612.0951 | 1208250.7291 | 2667632.2414 | 1208243.5084
44 | 2667449.9412 | 1208144.7855 | 2667461.1507 | 1208140.2513
45 | 2667353.2022 | 1208205.7419 | 2667368.8364 | 1208230.8979
46 | 2667353.2022 | 1208205.7419 | 2667336.9393 | 1208212.1286
47 | 2667419.6085 | 1208228.5491 | 2667383.4512 | 1208240.4045 | 2667377.274 | 1208241.391 | 2667374.1334 | 1208239.421 | 2667368.8364 | 1208230.8979
48 | 2667330.6517 | 1208214.5978 | 2667336.9393 | 1208212.1286
49 | 2667593.9337 | 1208257.2385 | 2667606.4775 | 1208252.7426
50 | 2667593.9337 | 1208257.2385 | 2667587.167 | 1208259.6633
51 | 2667558.5348 | 1208269.9234 | 2667587.167 | 1208259.6633
52 | 2667561.0908 | 1208174.4493 | 2667559.8073 | 1208162.9055 | 2667554.9263 | 1208155.5013 | 2667551.5435 | 1208142.0103 | 2667543.4935 | 1208131.1125
53 | 2667656.9131 | 1208122.1579 | 2667651.3247 | 1208122.1612 | 2667645.6753 | 1208120.8409 | 2667642.2036 | 1208118.5668 | 2667640.5217 | 1208115.3569
54 | 2667681.7263 | 1208268.6068 | 2667685.0413 | 1208269.9452
55 | 2667681.7263 | 1208268.6068 | 2667673.6737 | 1208265.3468 | 2667668.4951 | 1208264.0874 | 2667664.9921 | 1208263.9142 | 2667662.4347 | 1208264.8302 | 2667657.9425 | 1208267.4031 | 2667655.4461 | 1208267.6305 | 2667653.5097 | 1208266.7525 | 2667652.0633 | 1208264.9016 | 2667647.3013 | 1208253.0515 | 2667645.1518 | 1208250.181 | 2667642.1398 | 1208247.6008 | 2667632.2414 | 1208243.5084
56 | 2667910.0646 | 1207871.7261 | 2667889.5497 | 1207874.1464 | 2667871.7833 | 1207877.8911 | 2667863.7389 | 1207880.3394
57 | 2667477.9973 | 1207815.3483 | 2667476.8774 | 1207815.488 | 2667473.1622 | 1207816.2807
58 | 2667465.5808 | 1207817.8982 | 2667473.1622 | 1207816.2807
59 | 2667538.3908 | 1208186.9446 | 2667526.543 | 1208194.5264
60 | 2667526.543 | 1208194.5264 | 2667541.0242 | 1208208.1986 | 2667541.2279 | 1208208.7394
61 | 2667469.9436 | 1208206.7829 | 2667479.2842 | 1208211.1356
62 | 2667263.6319 | 1208028.19 | 2667275.4822 | 1208037.2513
63 | 2667293.9189 | 1208009.7311 | 2667275.4822 | 1208037.2513
64 | 2667275.4822 | 1208037.2513 | 2667290.9807 | 1208048.9379
65 | 2667147.486 | 1208025.2698 | 2667156.2988 | 1208030.6277 | 2667163.8045 | 1208034.5701 | 2667170.2999 | 1208037.0781 | 2667178.6441 | 1208038.8063 | 2667186.587 | 1208039.7074 | 2667194.749 | 1208039.3879 | 2667204.5355 | 1208039.298 | 2667216.966 | 1208040.0495 | 2667227.3362 | 1208042.8124 | 2667235.2608 | 1208045.3365 | 2667240.5329 | 1208048.4422 | 2667247.4112 | 1208053.4005 | 2667258.314 | 1208062.8736 | 2667275.4822 | 1208037.2513
66 | 2667147.486 | 1208025.2698 | 2667140.7413 | 1208017.8894 | 2667122.546 | 1208007.005
67 | 2667147.486 | 1208025.2698 | 2667156.5194 | 1208011.8424
68 | 2667170.8773 | 1207990.5004 | 2667156.5194 | 1208011.8424
69 | 2667561.0908 | 1208174.4493 | 2667553.8996 | 1208177.014 | 2667538.3908 | 1208186.9446
70 | 2667561.0908 | 1208174.4493 | 2667574.2288 | 1208169.7729 | 2667582.4418 | 1208164.2625 | 2667582.4418 | 1208164.2625
71 | 2667919.0293 | 1207870.6684 | 2667910.0646 | 1207871.7261
72 | 2667963.4211 | 1207863.8694 | 2667926.5069 | 1207869.7863 | 2667919.0293 | 1207870.6684
73 | 2667963.4211 | 1207863.8694 | 2667964.6743 | 1207889.3548 | 2667966.8224 | 1207900.3638 | 2667973.0223 | 1207920.2569
74 | 2667175.3238 | 1207983.8909 | 2667170.8773 | 1207990.5004
75 | 2667175.3238 | 1207983.8909 | 2667179.9886 | 1207977.7174
76 | 2667175.3238 | 1207983.8909 | 2667185.3399 | 1207978.2779 | 2667193.974 | 1207974.5172 | 2667196.2587 | 1207973.298
77 | 2667184.7866 | 1207971.3675 | 2667179.9886 | 1207977.7174
78 | 2667269.7511 | 1207928.509 | 2667206.2972 | 1207967.9408 | 2667196.2587 | 1207973.298
79 | 2667184.7866 | 1207971.3675 | 2667191.8827 | 1207961.1838
80 | 2667269.7511 | 1207928.509 | 2667279.8478 | 1207940.8044
81 | 2667269.7511 | 1207928.509 | 2667299.9908 | 1207909.8901
82 | 2667191.7028 | 1207902.0695 | 2667194.5969 | 1207903.0027 | 2667205.2887 | 1207906.9365 | 2667210.6994 | 1207911.9227 | 2667213.6875 | 1207917.3263 | 2667214.0942 | 1207923.7459 | 2667213.4509 | 1207930.2316 | 2667191.8827 | 1207961.1838
83 | 2667281.71 | 1207943.0721 | 2667279.8478 | 1207940.8044
84 | 2667325.8208 | 1207893.9754 | 2667321.3874 | 1207896.716 | 2667299.9908 | 1207909.8901
85 | 2667335.7239 | 1207906.1883 | 2667334.3366 | 1207904.4774
86 | 2667325.8208 | 1207893.9754 | 2667334.3366 | 1207904.4774
87 | 2667351.0328 | 1207925.0677 | 2667335.7239 | 1207906.1883
88 | 2667368.1546 | 1207867.9258 | 2667334.6039 | 1207888.4933 | 2667330.6449 | 1207890.9724 | 2667325.8208 | 1207893.9754
89 | 2667351.0328 | 1207925.0677 | 2667336.3479 | 1207936.9774
90 | 2667351.0328 | 1207925.0677 | 2667372.5134 | 1207951.3712
91 | 2667351.0328 | 1207925.0677 | 2667358.3135 | 1207919.1033
92 | 2667411.9833 | 1207840.159 | 2667368.1546 | 1207867.9258
93 | 2667368.1546 | 1207867.9258 | 2667373.9826 | 1207868.9477 | 2667379.705 | 1207868.0626
94 | 2667334.2596 | 1207938.6711 | 2667336.3479 | 1207936.9774
95 | 2667372.5134 | 1207951.3712 | 2667375.0695 | 1207954.5013 | 2667375.7532 | 1207957.2552 | 2667375.1151 | 1207959.894 | 2667373.3576 | 1207962.0088 | 2667360.7981 | 1207970.978
96 | 2667358.3135 | 1207919.1033 | 2667361.1584 | 1207916.7728
97 | 2667411.9833 | 1207840.159 | 2667421.5124 | 1207849.4167 | 2667425.7169 | 1207853.4778
98 | 2667411.9833 | 1207840.159 | 2667409.9 | 1207838.1343 | 2667414.541 | 1207835.8631
99 | 2667379.705 | 1207868.0626 | 2667383.4275 | 1207867.4868 | 2667389.4741 | 1207869.345 | 2667393.9167 | 1207873.1975 | 2667398.0096 | 1207881.2064
100 | 2667430.4755 | 1207849.5514 | 2667421.8551 | 1207841.9716 | 2667414.541 | 1207835.8631
101 | 2667414.541 | 1207835.8631 | 2667420.0384 | 1207833.1679 | 2667441.3739 | 1207826.4603 | 2667447.4875 | 1207826.4293
102 | 2667447.4875 | 1207826.4293 | 2667459.7051 | 1207819.1518 | 2667465.5808 | 1207817.8982
103 | 2667447.4875 | 1207826.4293 | 2667452.0519 | 1207828.9158 | 2667461.574 | 1207838.6259
104 | 2667334.2596 | 1207938.6711 | 2667314.7867 | 1207954.4641
105 | 2667345.1881 | 1207982.1256 | 2667360.7981 | 1207970.978
106 | 2667374.2864 | 1207906.0183 | 2667361.1584 | 1207916.7728
107 | 2667411.3121 | 1207903.6125 | 2667408.6764 | 1207898.6575 | 2667405.9977 | 1207896.8373 | 2667398.0096 | 1207881.2064
108 | 2667281.71 | 1207943.0721 | 2667284.5045 | 1207946.4751 | 2667285.0904 | 1207949.1278 | 2667284.4425 | 1207951.9667 | 2667282.7813 | 1207954.9943 | 2667282.7813 | 1207954.9943
109 | 2667100.7466 | 1207753.6114 | 2667099.0813 | 1207766.4672 | 2667097.8239 | 1207776.1812 | 2667097.75 | 1207792.2235 | 2667098.6964 | 1207805.4311 | 2667103.0712 | 1207824.1251 | 2667114.1797 | 1207835.6459 | 2667119.2034 | 1207845.9865 | 2667124.3198 | 1207858.2181 | 2667129.9486 | 1207869.5217 | 2667141.0922 | 1207881.9657 | 2667151.9576 | 1207888.0472 | 2667178.3995 | 1207897.7728 | 2667191.7028 | 1207902.0695
110 | 2667466.9191 | 1207844.3347 | 2667466.7701 | 1207843.9246 | 2667461.574 | 1207838.6259
111 | 2667314.7867 | 1207954.4641 | 2667311.3836 | 1207957.2241
112 | 2667282.7813 | 1207954.9943 | 2667278.3453 | 1207959.4945
113 | 2667275.2477 | 1207962.637 | 2667278.3453 | 1207959.4945
114 | 2667275.2477 | 1207962.637 | 2667272.8748 | 1207965.0444 | 2667266.8583 | 1207971.0994
115 | 2667266.8583 | 1207971.0994 | 2667262.1058 | 1207975.8824
116 | 2667262.1058 | 1207975.8824 | 2667259.8853 | 1207978.1171 | 2667259.2418 | 1207978.8975
117 | 2667255.1171 | 1207983.8995 | 2667259.2418 | 1207978.8975
118 | 2667249.7483 | 1207990.4105 | 2667255.1171 | 1207983.8995
119 | 2667100.7466 | 1207753.6114 | 2667086.4972 | 1207766.4702 | 2667074.8658 | 1207771.6872 | 2667072.5435 | 1207772.2737
120 | 2667100.7466 | 1207753.6114 | 2667106.6752 | 1207733.5324 | 2667132.1298 | 1207685.7671
121 | 2667132.1298 | 1207685.7671 | 2667172.6863 | 1207703.5007 | 2667214.6624 | 1207724.119 | 2667222.5778 | 1207734.9258 | 2667232.829 | 1207744.9252 | 2667244.6064 | 1207748.3599 | 2667256.4623 | 1207741.4559 | 2667261.2193 | 1207732.9487 | 2667259.502 | 1207726.1029 | 2667248.7489 | 1207717.4543
122 | 2667132.1298 | 1207685.7671 | 2667143.724 | 1207664.2843 | 2667149.8693 | 1207657.3936
123 | 2667149.8693 | 1207657.3936 | 2667153.9862 | 1207653.7266 | 2667170.465 | 1207638.7472 | 2667204.2736 | 1207597.3801 | 2667223.55 | 1207585.1785 | 2667240.8761 | 1207570.6091 | 2667263.1601 | 1207547.268 | 2667277.5631 | 1207537.7245 | 2667295.0233 | 1207534.8973 | 2667330.8509 | 1207535.7683 | 2667335.8002 | 1207535.0855
124 | 2667341.7431 | 1207534.2655 | 2667335.8002 | 1207535.0855
125 | 2667538.3908 | 1208186.9446 | 2667535.8343 | 1208179.7224
126 | 2667544.951 | 1208218.6272 | 2667544.951 | 1208218.6272 | 2667541.2279 | 1208208.7394
127 | 2667600.4519 | 1208190.8764 | 2667599.7752 | 1208189.2518 | 2667598.5531 | 1208176.319 | 2667598.9286 | 1208170.0193 | 2667596.0405 | 1208165.2282 | 2667591.1544 | 1208166.9961 | 2667587.6492 | 1208167.012 | 2667582.4418 | 1208164.2625
128 | 2667605.1961 | 1208214.7622 | 2667604.5493 | 1208200.7129 | 2667600.4519 | 1208190.8764
129 | 2667605.1961 | 1208214.7622 | 2667623.0844 | 1208207.5381 | 2667621.7453 | 1208204.2654
130 | 2667341.7431 | 1207534.2655 | 2667349.1745 | 1207533.2401 | 2667349.1745 | 1207533.2401
131 | 2667425.5771 | 1207535.4621 | 2667396.8091 | 1207533.6111 | 2667362.332 | 1207534.3559 | 2667349.1745 | 1207533.2401
132 | 2667425.5771 | 1207535.4621 | 2667431.6023 | 1207535.8498 | 2667431.669 | 1207535.8316
133 | 2667512.1168 | 1207495.2958 | 2667506.6054 | 1207501.1093 | 2667496.6891 | 1207507.8902 | 2667464.0747 | 1207525.4546 | 2667450.3582 | 1207530.7474 | 2667431.669 | 1207535.8316
134 | 2667512.1168 | 1207495.2958 | 2667513.203 | 1207494.15
135 | 2667466.9191 | 1207844.3347 | 2667467.6623 | 1207846.3806 | 2667467.8423 | 1207848.6174 | 2667467.3035 | 1207850.5458 | 2667465.3328 | 1207852.3139
136 | 2667465.3328 | 1207852.3139 | 2667453.8717 | 1207862.5963
137 | 2667444.0865 | 1207871.3753 | 2667453.8717 | 1207862.5963
138 | 2667437.4304 | 1207877.3469 | 2667444.0865 | 1207871.3753

## bus_geodata
| x | y | coords
0 | 2667794.6542 | 1207891.8169
1 | 2667795.2967 | 1207891.7634
2 | 2667683.9107 | 1207853.488
3 | 2667826.1352 | 1207889.2623
4 | 2667660.5798 | 1207975.8097
5 | 2667831.0245 | 1207888.8818
6 | 2667659.5898 | 1207979.8031
7 | 2667655.8013 | 1208033.8022
8 | 2667652.7496 | 1208014.304
9 | 2667820.8477 | 1208103.284
10 | 2667638.3722 | 1208064.8571
11 | 2667704.2819 | 1208053.9157
12 | 2667654.0808 | 1208007.1664
13 | 2667655.5763 | 1207997.4674
14 | 2667436.6544 | 1208207.7074
15 | 2667443.0843 | 1208239.2129
16 | 2667393.4049 | 1208191.1533
17 | 2667490.5459 | 1208228.9465
18 | 2667820.1809 | 1208107.7681
19 | 2667835.1783 | 1208199.0862
20 | 2667537.5184 | 1208277.457
21 | 2667529.8851 | 1208281.4731
22 | 2667492.9141 | 1208220.7622
23 | 2667557.8322 | 1208270.1753
24 | 2667388.1938 | 1208181.9889
25 | 2667293.908 | 1208051.1452
26 | 2667438.2825 | 1208171.9594
27 | 2667350.224 | 1208197.1204
28 | 2667380.1448 | 1208198.5145
29 | 2667841.4027 | 1208108.4456
30 | 2667612.9799 | 1208253.1628
31 | 2667612.0951 | 1208250.7291
32 | 2667618.6899 | 1208268.8508
33 | 2667438.7058 | 1208171.7984
34 | 2667449.9412 | 1208144.7855
35 | 2667353.2022 | 1208205.7419
36 | 2667368.8364 | 1208230.8979
37 | 2667336.9393 | 1208212.1286
38 | 2667593.9337 | 1208257.2385
39 | 2667606.4775 | 1208252.7426
40 | 2667587.167 | 1208259.6633
41 | 2667543.4935 | 1208131.1125
42 | 2667640.5217 | 1208115.3569
43 | 2667558.5348 | 1208269.9234
44 | 2667681.7263 | 1208268.6068
45 | 2667685.0413 | 1208269.9452
46 | 2667632.2414 | 1208243.5084
47 | 2667461.1507 | 1208140.2513
48 | 2667863.7389 | 1207880.3394
49 | 2667477.9973 | 1207815.3483
50 | 2667473.1622 | 1207816.2807
51 | 2667443.9658 | 1208243.5867
52 | 2667526.543 | 1208194.5264
53 | 2667479.2842 | 1208211.1356
54 | 2667275.4822 | 1208037.2513
55 | 2667263.6319 | 1208028.19
56 | 2667293.9189 | 1208009.7311
57 | 2667290.9807 | 1208048.9379
58 | 2667147.486 | 1208025.2698
59 | 2667302.3773 | 1208056.6107
60 | 2667122.546 | 1208007.005
61 | 2667156.5194 | 1208011.8424
62 | 2667469.9436 | 1208206.7829
63 | 2667419.6085 | 1208228.5491
64 | 2667330.6517 | 1208214.5978
65 | 2667561.0908 | 1208174.4493
66 | 2667656.9131 | 1208122.1579
67 | 2667919.0293 | 1207870.6684
68 | 2667910.0646 | 1207871.7261
69 | 2667963.4211 | 1207863.8694
70 | 2667973.0223 | 1207920.2569
71 | 2667170.8773 | 1207990.5004
72 | 2667175.3238 | 1207983.8909
73 | 2667179.9886 | 1207977.7174
74 | 2667196.2587 | 1207973.298
75 | 2667184.7866 | 1207971.3675
76 | 2667269.7511 | 1207928.509
77 | 2667191.8828 | 1207961.1838
78 | 2667279.8478 | 1207940.8044
79 | 2667299.9908 | 1207909.8901
80 | 2667334.3366 | 1207904.4774
81 | 2667335.7239 | 1207906.1883
82 | 2667325.8208 | 1207893.9754
83 | 2667351.0328 | 1207925.0677
84 | 2667368.1546 | 1207867.9258
85 | 2667336.3479 | 1207936.9774
86 | 2667372.5134 | 1207951.3712
87 | 2667358.3135 | 1207919.1033
88 | 2667411.9833 | 1207840.159
89 | 2667379.705 | 1207868.0626
90 | 2667425.7169 | 1207853.4778
91 | 2667414.541 | 1207835.863
92 | 2667430.4755 | 1207849.5514
93 | 2667447.4875 | 1207826.4293
94 | 2667334.2596 | 1207938.6711
95 | 2667360.7981 | 1207970.978
96 | 2667361.1584 | 1207916.7728
97 | 2667398.0096 | 1207881.2064
98 | 2667281.71 | 1207943.0721
99 | 2667191.7028 | 1207902.0695
100 | 2667465.5808 | 1207817.8982
101 | 2667461.574 | 1207838.6259
102 | 2667374.2864 | 1207906.0183
103 | 2667314.7867 | 1207954.4641
104 | 2667345.1881 | 1207982.1256
105 | 2667311.3836 | 1207957.2241
106 | 2667282.7813 | 1207954.9943
107 | 2667278.3453 | 1207959.4945
108 | 2667275.2477 | 1207962.637
109 | 2667266.8583 | 1207971.0994
110 | 2667262.1058 | 1207975.8824
111 | 2667259.2418 | 1207978.8975
112 | 2667255.1171 | 1207983.8995
113 | 2667100.7466 | 1207753.6114
114 | 2667249.7483 | 1207990.4105
115 | 2667411.3121 | 1207903.6125
116 | 2667132.1298 | 1207685.7671
117 | 2667248.7489 | 1207717.4543
118 | 2667149.8693 | 1207657.3936
119 | 2667072.5435 | 1207772.2737
120 | 2667335.8002 | 1207535.0855
121 | 2667538.3908 | 1208186.9446
122 | 2667541.2279 | 1208208.7394
123 | 2667582.4418 | 1208164.2625
124 | 2667535.8343 | 1208179.7224
125 | 2667600.4519 | 1208190.8764
126 | 2667544.951 | 1208218.6272
127 | 2667605.1961 | 1208214.7622
128 | 2667621.7453 | 1208204.2654
129 | 2667341.7431 | 1207534.2655
130 | 2667349.1745 | 1207533.2401
131 | 2667425.5771 | 1207535.4621
132 | 2667431.669 | 1207535.8316
133 | 2667512.1168 | 1207495.2958
134 | 2667513.203 | 1207494.15
135 | 2667466.9191 | 1207844.3347
136 | 2667465.3328 | 1207852.3139
137 | 2667453.8717 | 1207862.5963
138 | 2667444.0865 | 1207871.3753
139 | 2667437.4304 | 1207877.3469
140 | 2667452.8723 | 1208155.2028

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97504 | -0.4821 | 0.00085641 | 0.00021464
1 | 0.97504 | -0.48214 | 0.0010323 | 0.00025872
2 | 0.97557 | -0.4718 | 0 | 0
3 | 0.97497 | -0.48357 | 0.00053679 | 0.00013453
4 | 0.97608 | -0.46173 | 0 | 0
5 | 0.97496 | -0.48375 | 0.00049542 | 0.00012416
6 | 0.97609 | -0.46139 | 0.00023024 | 5.7705e-05
7 | 0.97635 | -0.4563 | 0 | 0
8 | 0.97625 | -0.45829 | 0.00028778 | 7.2125e-05
9 | 0.97594 | -0.46434 | 0 | 0
10 | 0.97672 | -0.44908 | 0 | 0
11 | 0.97627 | -0.45794 | 0.0017095 | 0.00042844
12 | 0.97622 | -0.45895 | 0 | 0
13 | 0.97617 | -0.45985 | 0.00036921 | 9.2534e-05
14 | 0.9908 | -0.17507 | 0 | 0
15 | 0.99061 | -0.17867 | 0.0040697 | 0.00102
16 | 0.99347 | -0.12394 | 0 | 0
17 | 0.98791 | -0.23069 | 0.0012906 | 0.00032345
18 | 0.97594 | -0.4645 | 0 | 0
19 | 0.97577 | -0.46784 | 0.0018867 | 0.00047285
20 | 0.98321 | -0.32182 | 0 | 0
21 | 0.98473 | -0.29229 | 0 | 0
22 | 0.98024 | -0.37974 | 0 | 0
23 | 0.98305 | -0.3249 | 0.0008682 | 0.00021759
24 | 0.99423 | -0.10944 | 0 | 0
25 | 0.98795 | -0.22946 | 0 | 0
26 | 0.99753 | -0.046734 | 0 | 0
27 | 0.99413 | -0.11125 | 0.0025105 | 0.00062918
28 | 0.99322 | -0.1288 | 0.0078276 | 0.0019618
29 | 0.97593 | -0.46452 | 0.00046342 | 0.00011615
30 | 0.98269 | -0.33197 | 0 | 0
31 | 0.98269 | -0.33192 | 0 | 0
32 | 0.98267 | -0.33232 | 0.0011662 | 0.00029228
33 | 0.99752 | -0.046887 | 0.019293 | 0.0048353
34 | 1 | 0 | -0.22692 | -0.057725
35 | 0.99296 | -0.13382 | 0 | 0
36 | 0.99282 | -0.13646 | 0.0021633 | 0.00054217
37 | 0.99288 | -0.13539 | 0.0017797 | 0.00044603
38 | 0.9828 | -0.32972 | 0 | 0
39 | 0.98272 | -0.33129 | 0.00073213 | 0.00018349
40 | 0.98285 | -0.32887 | 0.00051301 | 0.00012857
41 | 0.97795 | -0.42475 | 0 | 0
42 | 0.97662 | -0.45102 | 0.0012158 | 0.0003047
43 | 0.98305 | -0.325 | 0 | 0
44 | 0.98243 | -0.33702 | 0 | 0
45 | 0.98242 | -0.33721 | 0.0028987 | 0.00072648
46 | 0.9826 | -0.3337 | 0.0017399 | 0.00043605
47 | 0.9998 | -0.0038794 | 0.018403 | 0.0046123
48 | 0.97491 | -0.48467 | 0.00019436 | 4.8712e-05
49 | 0.9732 | -0.51717 | 0.0025665 | 0.00064321
50 | 0.97321 | -0.51694 | 0.0012834 | 0.00032164
51 | 0.9906 | -0.17885 | 0.0022428 | 0.0005621
52 | 0.97921 | -0.39996 | 0 | 0
53 | 0.97995 | -0.38555 | 0.012224 | 0.0030636
54 | 0.98728 | -0.24247 | 0 | 0
55 | 0.98726 | -0.24278 | 0.001179 | 0.00029548
56 | 0.98721 | -0.2438 | 0.0022432 | 0.00056219
57 | 0.98784 | -0.23154 | 0.00057959 | 0.00014526
58 | 0.983 | -0.32518 | 0 | 0
59 | 0.98787 | -0.23111 | 0.0092086 | 0.0023079
60 | 0.98292 | -0.32665 | 0.0026178 | 0.00065608
61 | 0.98256 | -0.33379 | 0.0019544 | 0.00048981
62 | 0.97988 | -0.38686 | 0.0069587 | 0.001744
63 | 0.99267 | -0.13941 | 0.0028758 | 0.00072074
64 | 0.99286 | -0.13578 | 0.003306 | 0.00082855
65 | 0.97846 | -0.41475 | 0 | 0
66 | 0.9766 | -0.45133 | 0.00086171 | 0.00021597
67 | 0.97485 | -0.48595 | 0.00077144 | 0.00019334
68 | 0.97486 | -0.48579 | 0.00030987 | 7.766e-05
69 | 0.97484 | -0.48612 | 0 | 0
70 | 0.97483 | -0.48633 | 0.00020288 | 5.0846e-05
71 | 0.98187 | -0.3472 | 0.00080439 | 0.0002016
72 | 0.98166 | -0.35132 | 0 | 0
73 | 0.98154 | -0.35354 | 0.0037903 | 0.00094995
74 | 0.98115 | -0.36121 | 0.0025218 | 0.00063201
75 | 0.98145 | -0.35528 | 0 | 0
76 | 0.97845 | -0.41381 | 0 | 0
77 | 0.98131 | -0.358 | 0.001177 | 0.00029499
78 | 0.97815 | -0.41984 | 0.0018772 | 0.00047047
79 | 0.97692 | -0.44394 | 0.0010395 | 0.00026052
80 | 0.97533 | -0.47523 | 0.0014353 | 0.00035971
81 | 0.97528 | -0.47615 | 0.0010176 | 0.00025504
82 | 0.97563 | -0.46917 | 0 | 0
83 | 0.97478 | -0.48596 | 0 | 0
84 | 0.97466 | -0.48828 | 0 | 0
85 | 0.97468 | -0.48798 | 0.0017586 | 0.00044075
86 | 0.97442 | -0.49298 | 0.0024265 | 0.00060813
87 | 0.97474 | -0.48681 | 0.00092349 | 0.00023145
88 | 0.97386 | -0.50404 | 0 | 0
89 | 0.97461 | -0.48923 | 0.0012465 | 0.0003124
90 | 0.97383 | -0.5047 | 0.0018827 | 0.00047186
91 | 0.97375 | -0.50622 | 0 | 0
92 | 0.97372 | -0.50687 | 0.0017004 | 0.00042616
93 | 0.97334 | -0.51446 | 0 | 0
94 | 0.97467 | -0.48818 | 0.00095905 | 0.00024036
95 | 0.9742 | -0.49748 | 0.0013672 | 0.00034266
96 | 0.97472 | -0.48709 | 0.0015248 | 0.00038214
97 | 0.97454 | -0.49069 | 0.001514 | 0.00037946
98 | 0.9781 | -0.42085 | 0.0020587 | 0.00051595
99 | 0.98052 | -0.37357 | 0 | 0
100 | 0.97324 | -0.51639 | 0.0013395 | 0.0003357
101 | 0.9732 | -0.51716 | 0.0014204 | 0.00035598
102 | 0.97468 | -0.48786 | 0.0024893 | 0.00062387
103 | 0.9746 | -0.4896 | 0.0020088 | 0.00050346
104 | 0.97406 | -0.50011 | 0.0074653 | 0.001871
105 | 0.97459 | -0.48968 | 0.0010787 | 0.00027034
106 | 0.97788 | -0.42499 | 0.001803 | 0.00045187
107 | 0.9778 | -0.42672 | 0.0018009 | 0.00045135
108 | 0.97774 | -0.42779 | 0.0018776 | 0.00047058
109 | 0.97762 | -0.43026 | 0.0018841 | 0.00047221
110 | 0.97756 | -0.43143 | 0.0018852 | 0.00047247
111 | 0.97753 | -0.432 | 0.0018324 | 0.00045924
112 | 0.97749 | -0.43269 | 0.001833 | 0.00045938
113 | 0.97853 | -0.41246 | 0 | 0
114 | 0.97746 | -0.43329 | 0.0039357 | 0.00098638
115 | 0.9745 | -0.4915 | 0.0016766 | 0.00042018
116 | 0.97781 | -0.42666 | 0 | 0
117 | 0.97753 | -0.43221 | 0.0017372 | 0.00043537
118 | 0.97754 | -0.43196 | 0 | 0
119 | 0.97852 | -0.41279 | 0.00052757 | 0.00013222
120 | 0.97566 | -0.46903 | 0.00028514 | 7.1462e-05
121 | 0.97893 | -0.40548 | 0 | 0
122 | 0.97915 | -0.40111 | 0.0015484 | 0.00038806
123 | 0.97828 | -0.41827 | 0.0020694 | 0.00051864
124 | 0.97892 | -0.40577 | 0.0020695 | 0.00051866
125 | 0.97805 | -0.42281 | 0.0017236 | 0.00043198
126 | 0.97914 | -0.40141 | 0.0015452 | 0.00038726
127 | 0.97795 | -0.42476 | 0 | 0
128 | 0.97786 | -0.42655 | 0.0043204 | 0.0010828
129 | 0.97561 | -0.46995 | 0.00066659 | 0.00016706
130 | 0.97556 | -0.47101 | 0.0015324 | 0.00038406
131 | 0.97512 | -0.47963 | 0.00019258 | 4.8264e-05
132 | 0.97508 | -0.4803 | 0.00056944 | 0.00014272
133 | 0.97463 | -0.48931 | 0.0035655 | 0.00089359
134 | 0.97462 | -0.48936 | 0.0018211 | 0.00045641
135 | 0.97315 | -0.51808 | 0.0010902 | 0.00027322
136 | 0.97311 | -0.51896 | 0.0013147 | 0.0003295
137 | 0.97305 | -0.52009 | 0.0014453 | 0.00036224
138 | 0.97302 | -0.5207 | 0.0014547 | 0.00036458
139 | 0.97301 | -0.52087 | 0.0010705 | 0.00026829
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0035434 | 0.00088533 | -0.0035434 | -0.00088533 | 7.0675e-09 | -3.5184e-09 | 0.0054066 | 0.0054066 | 0.0054066 | 0.97504 | -0.4821 | 0.97504 | -0.48214 | 1.4853
1 | -0.0043998 | -0.0011 | 0.0044019 | 0.0010998 | 2.1556e-06 | -2.1211e-07 | 0.0067136 | 0.006713 | 0.0067136 | 0.97504 | -0.4821 | 0.97557 | -0.4718 | 1.8444
2 | 0.0025111 | 0.00062662 | -0.0025109 | -0.00062689 | 1.7031e-07 | -2.7687e-07 | 0.0038312 | 0.0038313 | 0.0038313 | 0.97504 | -0.48214 | 0.97497 | -0.48357 | 1.0526
3 | -0.0044019 | -0.0010998 | 0.0044041 | 0.0010995 | 2.1066e-06 | -2.092e-07 | 0.006713 | 0.0067124 | 0.006713 | 0.97557 | -0.4718 | 0.97608 | -0.46173 | 1.8442
4 | 0.0019741 | 0.00049236 | -0.0019741 | -0.00049241 | 1.6685e-08 | -5.0478e-08 | 0.0030121 | 0.0030121 | 0.0030121 | 0.97497 | -0.48357 | 0.97496 | -0.48375 | 0.8275
5 | -0.0044041 | -0.0010995 | 0.0044041 | 0.0010995 | 6.9517e-08 | -6.9357e-09 | 0.0067124 | 0.0067124 | 0.0067124 | 0.97608 | -0.46173 | 0.97609 | -0.46139 | 1.8441
6 | 0.0014787 | 0.00036825 | -0.0014786 | -0.00036863 | 6.4783e-08 | -3.8179e-07 | 0.002256 | 0.0022561 | 0.0022561 | 0.97496 | -0.48375 | 0.97491 | -0.48467 | 0.61982
7 | -0.0046344 | -0.0011572 | 0.0046347 | 0.0011572 | 3.3907e-07 | -9.5441e-09 | 0.0070634 | 0.0070633 | 0.0070634 | 0.97609 | -0.46139 | 0.97617 | -0.45985 | 1.9405
8 | 0.0052926 | 0.001322 | -0.0052921 | -0.0013219 | 5.0051e-07 | 6.3708e-08 | 0.0080646 | 0.0080647 | 0.0080647 | 0.97635 | -0.4563 | 0.97625 | -0.45829 | 2.2156
9 | 0.0023513 | 0.00058591 | -0.0023504 | -0.00058767 | 8.9842e-07 | -1.7582e-06 | 0.0035824 | 0.0035832 | 0.0035832 | 0.97635 | -0.4563 | 0.97594 | -0.46434 | 0.98439
10 | -0.0093535 | -0.0023358 | 0.0093567 | 0.0023373 | 3.2101e-06 | 1.5272e-06 | 0.014252 | 0.014252 | 0.014252 | 0.97635 | -0.4563 | 0.97672 | -0.44908 | 3.9155
11 | 0.0017096 | 0.00042786 | -0.0017095 | -0.00042844 | 1.3381e-07 | -5.7166e-07 | 0.0026053 | 0.0026056 | 0.0026056 | 0.97635 | -0.4563 | 0.97627 | -0.45794 | 0.71582
12 | 0.0050043 | 0.0012498 | -0.0050041 | -0.0012498 | 1.5835e-07 | 1.0561e-08 | 0.0076261 | 0.0076261 | 0.0076261 | 0.97625 | -0.45829 | 0.97622 | -0.45895 | 2.0951
13 | 0.00046343 | 0.00011588 | -0.00046342 | -0.00011615 | 3.9673e-09 | -2.6228e-07 | 0.00070649 | 0.00070659 | 0.00070659 | 0.97594 | -0.46434 | 0.97593 | -0.46452 | 0.19412
14 | 0.001887 | 0.00047178 | -0.001887 | -0.00047183 | 1.407e-08 | -4.765e-08 | 0.0028767 | 0.0028767 | 0.0028767 | 0.97594 | -0.46434 | 0.97594 | -0.4645 | 0.79031
15 | -0.011434 | -0.0028572 | 0.011448 | 0.0028642 | 1.3235e-05 | 7.0124e-06 | 0.017417 | 0.017417 | 0.017417 | 0.97672 | -0.44908 | 0.97795 | -0.42475 | 4.7849
16 | 0.0020777 | 0.00051992 | -0.0020775 | -0.00052044 | 1.928e-07 | -5.1882e-07 | 0.0031651 | 0.0031653 | 0.0031653 | 0.97672 | -0.44908 | 0.97662 | -0.45102 | 0.86959
17 | 0.0050041 | 0.0012498 | -0.0050039 | -0.0012498 | 2.1408e-07 | 1.4289e-08 | 0.0076261 | 0.0076261 | 0.0076261 | 0.97622 | -0.45895 | 0.97617 | -0.45985 | 2.0951
18 | 0.0063136 | 0.0015823 | -0.0063125 | -0.001582 | 1.0842e-06 | 2.798e-07 | 0.009482 | 0.0094821 | 0.0094821 | 0.9908 | -0.17507 | 0.99061 | -0.17867 | 2.605
19 | -0.059979 | -0.015232 | 0.060127 | 0.015326 | 0.00014798 | 9.408e-05 | 0.09015 | 0.09015 | 0.09015 | 0.9908 | -0.17507 | 0.99347 | -0.12394 | 24.7666
20 | 0.053666 | 0.01365 | -0.053522 | -0.013559 | 0.00014341 | 9.103e-05 | 0.080669 | 0.080669 | 0.080669 | 0.9908 | -0.17507 | 0.98791 | -0.23069 | 22.1618
21 | 0.0022428 | 0.00056206 | -0.0022428 | -0.0005621 | 1.9001e-08 | -4.5311e-08 | 0.003369 | 0.003369 | 0.003369 | 0.99061 | -0.17867 | 0.9906 | -0.17885 | 0.92555
22 | 0.01796 | 0.0045024 | -0.017956 | -0.0045 | 4.1609e-06 | 2.4645e-06 | 0.026901 | 0.026902 | 0.026902 | 0.99347 | -0.12394 | 0.99322 | -0.1288 | 7.3905
23 | -0.078088 | -0.019829 | 0.078142 | 0.019864 | 5.4517e-05 | 3.4753e-05 | 0.11705 | 0.11705 | 0.11705 | 0.99347 | -0.12394 | 0.99423 | -0.10944 | 32.157
24 | 0.052232 | 0.013236 | -0.052078 | -0.013138 | 0.00015409 | 9.777e-05 | 0.078725 | 0.078725 | 0.078725 | 0.98791 | -0.23069 | 0.98473 | -0.29229 | 21.6278
25 | 0.001887 | 0.00047183 | -0.0018867 | -0.00047285 | 3.0026e-07 | -1.0164e-06 | 0.0028767 | 0.0028771 | 0.0028771 | 0.97594 | -0.4645 | 0.97577 | -0.46784 | 0.79043
26 | -0.052004 | -0.013091 | 0.052078 | 0.013138 | 7.3523e-05 | 4.6653e-05 | 0.078725 | 0.078725 | 0.078725 | 0.98321 | -0.32182 | 0.98473 | -0.29229 | 21.6278
27 | 0.044082 | 0.011106 | -0.04396 | -0.011029 | 0.00012177 | 7.7011e-05 | 0.066736 | 0.066736 | 0.066736 | 0.98321 | -0.32182 | 0.98024 | -0.37974 | 18.334
28 | 0.0079224 | 0.0019849 | -0.0079213 | -0.0019844 | 1.1633e-06 | 4.7089e-07 | 0.01199 | 0.01199 | 0.01199 | 0.98321 | -0.32182 | 0.98305 | -0.3249 | 3.2939
29 | 0.024771 | 0.0062183 | -0.024748 | -0.0062036 | 2.386e-05 | 1.4704e-05 | 0.037607 | 0.037607 | 0.037607 | 0.98024 | -0.37974 | 0.97921 | -0.39996 | 10.3316
30 | 0.019189 | 0.004811 | -0.019183 | -0.0048078 | 5.3119e-06 | 3.1892e-06 | 0.029129 | 0.029129 | 0.029129 | 0.98024 | -0.37974 | 0.97995 | -0.38555 | 8.0025
31 | 0.0070531 | 0.0017668 | -0.007053 | -0.0017668 | 3.1897e-08 | 1.0952e-08 | 0.010676 | 0.010676 | 0.010676 | 0.98305 | -0.3249 | 0.98305 | -0.325 | 2.9329
32 | 0.10588 | 0.027124 | -0.10527 | -0.02674 | 0.00061193 | 0.00038412 | 0.15867 | 0.15868 | 0.15868 | 0.99423 | -0.10944 | 0.98795 | -0.22946 | 14.5308
33 | -0.18653 | -0.047616 | 0.1871 | 0.047977 | 0.0005671 | 0.00036068 | 0.27948 | 0.27948 | 0.27948 | 0.99423 | -0.10944 | 0.99753 | -0.046734 | 25.5937
34 | 0.0025107 | 0.00062879 | -0.0025105 | -0.00062918 | 2.1642e-07 | -3.9151e-07 | 0.0037575 | 0.0037576 | 0.0037576 | 0.99423 | -0.10944 | 0.99413 | -0.11125 | 1.0323
35 | 0.0092093 | 0.0023082 | -0.0092086 | -0.0023079 | 7.2575e-07 | 3.3568e-07 | 0.013871 | 0.013871 | 0.013871 | 0.98795 | -0.22946 | 0.98787 | -0.23111 | 3.8107
36 | 0.096058 | 0.024431 | -0.096048 | -0.024425 | 9.6097e-06 | 6.0094e-06 | 0.14481 | 0.14481 | 0.14481 | 0.98795 | -0.22946 | 0.98784 | -0.23154 | 13.2606
37 | 0.019293 | 0.0048354 | -0.019293 | -0.0048353 | 1.4066e-07 | 8.411e-08 | 0.02878 | 0.02878 | 0.02878 | 0.99753 | -0.046734 | 0.99752 | -0.046887 | 7.9066
38 | -0.20639 | -0.052812 | 0.20686 | 0.05311 | 0.00046811 | 0.00029804 | 0.30826 | 0.30826 | 0.30826 | 0.99753 | -0.046734 | 1 | 0 | 28.2291
39 | 0.010129 | 0.0025382 | -0.010126 | -0.002537 | 2.4193e-06 | 1.1858e-06 | 0.015174 | 0.015174 | 0.015174 | 0.99322 | -0.1288 | 0.99296 | -0.13382 | 4.1688
40 | -0.0011662 | -0.00029208 | 0.0011662 | 0.00029205 | 3.0274e-09 | -3.0863e-08 | 0.0017659 | 0.0017659 | 0.0017659 | 0.98269 | -0.33197 | 0.98269 | -0.33192 | 0.48513
41 | 0.0011662 | 0.00029208 | -0.0011662 | -0.00029228 | 1.9523e-08 | -1.9901e-07 | 0.0017659 | 0.0017659 | 0.0017659 | 0.98269 | -0.33197 | 0.98267 | -0.33232 | 0.48515
42 | -0.0058057 | -0.001454 | 0.0058058 | 0.0014541 | 1.7293e-07 | 3.507e-08 | 0.0087907 | 0.0087907 | 0.0087907 | 0.98269 | -0.33192 | 0.98272 | -0.33129 | 2.415
43 | 0.0046394 | 0.001162 | -0.004639 | -0.001162 | 3.9505e-07 | -1.7592e-08 | 0.0070249 | 0.007025 | 0.007025 | 0.98269 | -0.33192 | 0.9826 | -0.3337 | 1.9299
44 | 0.018407 | 0.0046144 | -0.018403 | -0.0046123 | 3.4018e-06 | 2.0186e-06 | 0.02739 | 0.02739 | 0.02739 | 1 | 0 | 0.9998 | -0.0038794 | 7.5248
45 | 0.0050401 | 0.0012624 | -0.0050395 | -0.0012624 | 6.3358e-07 | 2.2426e-08 | 0.0075527 | 0.0075528 | 0.0075528 | 0.99296 | -0.13382 | 0.99282 | -0.13646 | 2.075
46 | 0.0050861 | 0.0012745 | -0.0050857 | -0.0012745 | 3.8062e-07 | 1.7611e-08 | 0.0076218 | 0.0076219 | 0.0076219 | 0.99296 | -0.13382 | 0.99288 | -0.13539 | 2.0939
47 | 0.0028762 | 0.00072025 | -0.0028758 | -0.00072074 | 4.0451e-07 | -4.9167e-07 | 0.0043106 | 0.0043108 | 0.0043108 | 0.99282 | -0.13646 | 0.99267 | -0.13941 | 1.1843
48 | 0.003306 | 0.00082851 | -0.003306 | -0.00082855 | 6.2187e-08 | -4.7563e-08 | 0.0049547 | 0.0049547 | 0.0049547 | 0.99288 | -0.13539 | 0.99286 | -0.13578 | 1.3612
49 | 0.0065384 | 0.0016377 | -0.006538 | -0.0016375 | 4.8967e-07 | 1.4455e-07 | 0.0098992 | 0.0098993 | 0.0098993 | 0.9828 | -0.32972 | 0.98272 | -0.33129 | 2.7196
50 | -0.0065384 | -0.0016377 | 0.0065387 | 0.0016378 | 2.6414e-07 | 7.7961e-08 | 0.0098992 | 0.0098992 | 0.0098992 | 0.9828 | -0.32972 | 0.98285 | -0.32887 | 2.7196
51 | -0.0070517 | -0.0017663 | 0.007053 | 0.0017668 | 1.2999e-06 | 4.4642e-07 | 0.010676 | 0.010676 | 0.010676 | 0.98285 | -0.32887 | 0.98305 | -0.325 | 2.9329
52 | -0.011448 | -0.0028642 | 0.011453 | 0.0028671 | 5.4513e-06 | 2.8872e-06 | 0.017417 | 0.017416 | 0.017417 | 0.97795 | -0.42475 | 0.97846 | -0.41475 | 4.7848
53 | 0.00086172 | 0.00021573 | -0.00086171 | -0.00021597 | 1.2388e-08 | -2.3187e-07 | 0.0013129 | 0.001313 | 0.001313 | 0.97662 | -0.45102 | 0.9766 | -0.45133 | 0.3607
54 | 0.0028987 | 0.00072645 | -0.0028987 | -0.00072648 | 2.5777e-08 | -2.8656e-08 | 0.0043905 | 0.0043905 | 0.0043905 | 0.98243 | -0.33702 | 0.98242 | -0.33721 | 1.2062
55 | -0.0028987 | -0.00072645 | 0.0028992 | 0.00072594 | 4.5765e-07 | -5.0897e-07 | 0.0043905 | 0.0043902 | 0.0043905 | 0.98243 | -0.33702 | 0.9826 | -0.3337 | 1.2062
56 | 0.0012843 | 0.00031992 | -0.0012842 | -0.00032046 | 6.8e-08 | -5.4528e-07 | 0.0019595 | 0.0019597 | 0.0019597 | 0.97491 | -0.48467 | 0.97486 | -0.48579 | 0.53838
57 | -0.0025665 | -0.00064321 | 0.0025665 | 0.00064317 | 2.8453e-08 | -4.3017e-08 | 0.0039241 | 0.0039241 | 0.0039241 | 0.9732 | -0.51717 | 0.97321 | -0.51694 | 1.0781
58 | -0.0038498 | -0.00096481 | 0.0038499 | 0.00096478 | 1.0072e-07 | -3.1865e-08 | 0.0058863 | 0.0058863 | 0.0058863 | 0.97321 | -0.51694 | 0.97324 | -0.51639 | 1.6171
59 | 0.021654 | 0.0054286 | -0.021648 | -0.0054251 | 5.7001e-06 | 3.4716e-06 | 0.032906 | 0.032906 | 0.032906 | 0.97921 | -0.39996 | 0.97893 | -0.40548 | 9.0401
60 | 0.0030937 | 0.00077505 | -0.0030936 | -0.0007752 | 1.6985e-07 | -1.4908e-07 | 0.0047011 | 0.0047012 | 0.0047012 | 0.97921 | -0.39996 | 0.97915 | -0.40111 | 1.2915
61 | 0.0069592 | 0.0017442 | -0.0069587 | -0.001744 | 4.3153e-07 | 1.4636e-07 | 0.010567 | 0.010567 | 0.010567 | 0.97995 | -0.38555 | 0.97988 | -0.38686 | 2.9031
62 | 0.001179 | 0.0002953 | -0.001179 | -0.00029548 | 1.7632e-08 | -1.7913e-07 | 0.0017769 | 0.001777 | 0.001777 | 0.98728 | -0.24247 | 0.98726 | -0.24278 | 0.48818
63 | 0.0022433 | 0.00056185 | -0.0022432 | -0.00056219 | 1.419e-07 | -3.3244e-07 | 0.0033809 | 0.0033811 | 0.0033811 | 0.98728 | -0.24247 | 0.98721 | -0.2438 | 0.92887
64 | -0.095418 | -0.024249 | 0.095468 | 0.02428 | 5.0266e-05 | 3.1425e-05 | 0.14393 | 0.14393 | 0.14393 | 0.98728 | -0.24247 | 0.98784 | -0.23154 | 13.1807
65 | 0.091996 | 0.023392 | -0.091631 | -0.023164 | 0.00036498 | 0.0002278 | 0.13878 | 0.13878 | 0.13878 | 0.98728 | -0.24247 | 0.983 | -0.32518 | 12.7086
66 | 0.002618 | 0.00065581 | -0.0026178 | -0.00065608 | 1.8375e-07 | -2.779e-07 | 0.0039629 | 0.003963 | 0.003963 | 0.983 | -0.32518 | 0.98292 | -0.32665 | 1.0887
67 | 0.089013 | 0.022508 | -0.088976 | -0.022485 | 3.6766e-05 | 2.2915e-05 | 0.13481 | 0.13481 | 0.13481 | 0.983 | -0.32518 | 0.98256 | -0.33379 | 12.3457
68 | 0.087022 | 0.021995 | -0.086966 | -0.02196 | 5.59e-05 | 3.4799e-05 | 0.13186 | 0.13186 | 0.13186 | 0.98256 | -0.33379 | 0.98187 | -0.3472 | 12.0747
69 | -0.01957 | -0.0049013 | 0.019579 | 0.0049065 | 8.6334e-06 | 5.1987e-06 | 0.02976 | 0.02976 | 0.02976 | 0.97846 | -0.41475 | 0.97893 | -0.40548 | 8.1759
70 | 0.0081169 | 0.0020342 | -0.0081155 | -0.0020336 | 1.362e-06 | 5.7234e-07 | 0.012344 | 0.012344 | 0.012344 | 0.97846 | -0.41475 | 0.97828 | -0.41827 | 3.3912
71 | -0.00097432 | -0.00024291 | 0.00097433 | 0.0002428 | 7.4823e-09 | -1.0776e-07 | 0.0014867 | 0.0014867 | 0.0014867 | 0.97485 | -0.48595 | 0.97486 | -0.48579 | 0.40845
72 | 0.00020288 | 4.957e-05 | -0.00020288 | -5.0129e-05 | 1.6116e-09 | -5.5895e-07 | 0.00030922 | 0.00030942 | 0.00030942 | 0.97485 | -0.48595 | 0.97484 | -0.48612 | 0.085006
73 | 0.00020288 | 5.0129e-05 | -0.00020288 | -5.0846e-05 | 2.0687e-09 | -7.1642e-07 | 0.00030942 | 0.00030968 | 0.00030968 | 0.97484 | -0.48612 | 0.97483 | -0.48633 | 0.085077
74 | 0.086161 | 0.021759 | -0.086144 | -0.021748 | 1.6993e-05 | 1.0574e-05 | 0.13064 | 0.13064 | 0.13064 | 0.98187 | -0.3472 | 0.98166 | -0.35132 | 11.9631
75 | 0.015928 | 0.0040036 | -0.015927 | -0.0040026 | 1.6921e-06 | 9.8514e-07 | 0.024149 | 0.024149 | 0.024149 | 0.98166 | -0.35132 | 0.98154 | -0.35354 | 6.6342
76 | 0.070216 | 0.017745 | -0.070183 | -0.017724 | 3.3295e-05 | 2.0418e-05 | 0.10649 | 0.10649 | 0.10649 | 0.98166 | -0.35132 | 0.98115 | -0.36121 | 9.7517
77 | 0.012136 | 0.0030527 | -0.012135 | -0.0030521 | 1.0107e-06 | 5.4627e-07 | 0.018402 | 0.018403 | 0.018403 | 0.98154 | -0.35354 | 0.98145 | -0.35528 | 5.0556
78 | 0.067661 | 0.017092 | -0.067491 | -0.016986 | 0.00017013 | 0.00010671 | 0.10266 | 0.10266 | 0.10266 | 0.98115 | -0.36121 | 0.97845 | -0.41381 | 14.1023
79 | 0.012135 | 0.0030521 | -0.012134 | -0.0030513 | 1.5763e-06 | 8.5199e-07 | 0.018403 | 0.018403 | 0.018403 | 0.98145 | -0.35528 | 0.98131 | -0.358 | 5.0557
80 | 0.020802 | 0.0052182 | -0.020796 | -0.0052145 | 5.9717e-06 | 3.6221e-06 | 0.031637 | 0.031637 | 0.031637 | 0.97845 | -0.41381 | 0.97815 | -0.41984 | 8.6916
81 | 0.046689 | 0.011767 | -0.046622 | -0.011725 | 6.7183e-05 | 4.2552e-05 | 0.071027 | 0.071027 | 0.071027 | 0.97845 | -0.41381 | 0.97692 | -0.44394 | 19.513
82 | 0.010957 | 0.0027563 | -0.010948 | -0.0027521 | 8.1441e-06 | 4.2195e-06 | 0.016618 | 0.016618 | 0.016618 | 0.98131 | -0.358 | 0.98052 | -0.37357 | 4.5654
83 | 0.018919 | 0.0047441 | -0.018918 | -0.0047435 | 9.1152e-07 | 5.4654e-07 | 0.028782 | 0.028782 | 0.028782 | 0.97815 | -0.41984 | 0.9781 | -0.42085 | 7.9071
84 | 0.045582 | 0.011464 | -0.045527 | -0.01143 | 5.4866e-05 | 3.4735e-05 | 0.069444 | 0.069444 | 0.069444 | 0.97692 | -0.44394 | 0.97563 | -0.46917 | 19.0781
85 | 0.023038 | 0.005779 | -0.023037 | -0.0057784 | 1.0206e-06 | 6.2569e-07 | 0.035151 | 0.035151 | 0.035151 | 0.97533 | -0.47523 | 0.97528 | -0.47615 | 9.6568
86 | -0.024474 | -0.0061387 | 0.024481 | 0.0061431 | 7.0695e-06 | 4.3557e-06 | 0.03734 | 0.03734 | 0.03734 | 0.97533 | -0.47523 | 0.97563 | -0.46917 | 10.2583
87 | 0.02202 | 0.0055234 | -0.022009 | -0.0055171 | 1.0289e-05 | 6.2819e-06 | 0.033598 | 0.033598 | 0.033598 | 0.97528 | -0.47615 | 0.97478 | -0.48596 | 9.2303
88 | 0.021047 | 0.0052864 | -0.021027 | -0.0052748 | 1.9173e-05 | 1.1652e-05 | 0.032104 | 0.032104 | 0.032104 | 0.97563 | -0.46917 | 0.97466 | -0.48828 | 8.8198
89 | 0.005806 | 0.0014548 | -0.0058054 | -0.0014547 | 5.5694e-07 | 1.2077e-07 | 0.0088628 | 0.0088629 | 0.0088629 | 0.97478 | -0.48596 | 0.97468 | -0.48798 | 2.4349
90 | 0.011266 | 0.002825 | -0.011262 | -0.002823 | 3.7666e-06 | 1.9874e-06 | 0.017198 | 0.017198 | 0.017198 | 0.97478 | -0.48596 | 0.97442 | -0.49298 | 4.7247
91 | 0.0049379 | 0.0012373 | -0.0049377 | -0.0012373 | 2.0053e-07 | 1.1018e-08 | 0.0075377 | 0.0075377 | 0.0075377 | 0.97478 | -0.48596 | 0.97474 | -0.48681 | 2.0708
92 | 0.01659 | 0.0041632 | -0.016577 | -0.0041559 | 1.2458e-05 | 7.3286e-06 | 0.02533 | 0.02533 | 0.02533 | 0.97466 | -0.48828 | 0.97386 | -0.50404 | 6.9587
93 | 0.0044376 | 0.0011116 | -0.0044374 | -0.0011116 | 2.015e-07 | -1.6943e-08 | 0.0067746 | 0.0067747 | 0.0067747 | 0.97466 | -0.48828 | 0.97461 | -0.48923 | 1.8612
94 | 0.0040468 | 0.0010139 | -0.0040468 | -0.0010139 | 3.8484e-08 | -8.8804e-09 | 0.006178 | 0.006178 | 0.006178 | 0.97468 | -0.48798 | 0.97467 | -0.48818 | 1.6973
95 | 0.0088354 | 0.0022149 | -0.0088335 | -0.002214 | 1.8962e-06 | 8.6767e-07 | 0.013492 | 0.013493 | 0.013493 | 0.97442 | -0.49298 | 0.9742 | -0.49748 | 3.7067
96 | 0.0040142 | 0.0010058 | -0.0040141 | -0.0010059 | 5.1787e-08 | -1.2696e-08 | 0.0061279 | 0.0061279 | 0.0061279 | 0.97474 | -0.48681 | 0.97472 | -0.48709 | 1.6835
97 | 0.0018828 | 0.00047166 | -0.0018827 | -0.00047186 | 5.9288e-08 | -1.9975e-07 | 0.0028767 | 0.0028768 | 0.0028768 | 0.97386 | -0.50404 | 0.97383 | -0.5047 | 0.79033
98 | 0.014695 | 0.0036842 | -0.014693 | -0.0036834 | 1.5261e-06 | 8.7625e-07 | 0.022453 | 0.022453 | 0.022453 | 0.97386 | -0.50404 | 0.97375 | -0.50622 | 6.1684
99 | 0.0031909 | 0.00079918 | -0.0031907 | -0.00079935 | 2.222e-07 | -1.689e-07 | 0.0048716 | 0.0048717 | 0.0048717 | 0.97461 | -0.48923 | 0.97454 | -0.49069 | 1.3384
100 | 0.0017004 | 0.00042593 | -0.0017004 | -0.00042616 | 5.3108e-08 | -2.2692e-07 | 0.0025984 | 0.0025985 | 0.0025985 | 0.97375 | -0.50622 | 0.97372 | -0.50687 | 0.71387
101 | 0.012993 | 0.0032574 | -0.012987 | -0.0032546 | 5.1018e-06 | 2.836e-06 | 0.019855 | 0.019855 | 0.019855 | 0.97375 | -0.50622 | 0.97334 | -0.51446 | 5.4546
102 | 0.0051899 | 0.0013005 | -0.0051894 | -0.0013005 | 4.7754e-07 | 5.4224e-08 | 0.0079341 | 0.0079342 | 0.0079342 | 0.97334 | -0.51446 | 0.97324 | -0.51639 | 2.1797
103 | 0.0077976 | 0.0019541 | -0.0077966 | -0.0019536 | 1.0017e-06 | 4.0749e-07 | 0.011921 | 0.011921 | 0.011921 | 0.97334 | -0.51446 | 0.9732 | -0.51716 | 3.275
104 | 0.0030877 | 0.00077357 | -0.0030875 | -0.00077375 | 2.0892e-07 | -1.7874e-07 | 0.0047139 | 0.004714 | 0.004714 | 0.97467 | -0.48818 | 0.9746 | -0.4896 | 1.295
105 | 0.0074663 | 0.0018713 | -0.0074653 | -0.001871 | 9.3553e-07 | 3.5994e-07 | 0.011404 | 0.011404 | 0.011404 | 0.9742 | -0.49748 | 0.97406 | -0.50011 | 3.1331
106 | 0.0024894 | 0.00062372 | -0.0024893 | -0.00062387 | 9.1908e-08 | -1.527e-07 | 0.0038002 | 0.0038003 | 0.0038003 | 0.97472 | -0.48709 | 0.97468 | -0.48786 | 1.044
107 | 0.0016766 | 0.0004199 | -0.0016766 | -0.00042018 | 6.4891e-08 | -2.8745e-07 | 0.0025599 | 0.00256 | 0.00256 | 0.97454 | -0.49069 | 0.9745 | -0.4915 | 0.7033
108 | 0.016859 | 0.0042276 | -0.016856 | -0.0042256 | 3.327e-06 | 1.9601e-06 | 0.02565 | 0.02565 | 0.02565 | 0.9781 | -0.42085 | 0.97788 | -0.42499 | 7.0466
109 | 0.010948 | 0.0027521 | -0.010928 | -0.0027416 | 2.0293e-05 | 1.0521e-05 | 0.016618 | 0.016619 | 0.016619 | 0.98052 | -0.37357 | 0.97853 | -0.41246 | 4.5657
110 | 0.0063762 | 0.0015977 | -0.0063759 | -0.0015976 | 2.8006e-07 | 8.1608e-08 | 0.0097491 | 0.0097491 | 0.0097491 | 0.9732 | -0.51716 | 0.97315 | -0.51808 | 2.6783
111 | 0.0010787 | 0.00027029 | -0.0010787 | -0.00027034 | 4.4568e-09 | -5.1748e-08 | 0.0016469 | 0.0016469 | 0.0016469 | 0.9746 | -0.4896 | 0.97459 | -0.48968 | 0.45246
112 | 0.015053 | 0.0037737 | -0.015052 | -0.003773 | 1.2433e-06 | 7.1647e-07 | 0.022906 | 0.022906 | 0.022906 | 0.97788 | -0.42499 | 0.9778 | -0.42672 | 6.2929
113 | 0.013251 | 0.0033217 | -0.01325 | -0.0033213 | 6.7289e-07 | 3.7531e-07 | 0.020166 | 0.020166 | 0.020166 | 0.9778 | -0.42672 | 0.97774 | -0.42779 | 5.54
114 | 0.011373 | 0.0028507 | -0.011371 | -0.00285 | 1.3387e-06 | 7.0732e-07 | 0.017308 | 0.017308 | 0.017308 | 0.97774 | -0.42779 | 0.97762 | -0.43026 | 4.755
115 | 0.0094873 | 0.0023778 | -0.0094867 | -0.0023776 | 5.2726e-07 | 2.5291e-07 | 0.01444 | 0.01444 | 0.01444 | 0.97762 | -0.43026 | 0.97756 | -0.43143 | 3.9672
116 | 0.0076015 | 0.0019051 | -0.0076013 | -0.001905 | 2.0895e-07 | 8.1554e-08 | 0.011571 | 0.011571 | 0.011571 | 0.97756 | -0.43143 | 0.97753 | -0.432 | 3.1788
117 | 0.005769 | 0.0014458 | -0.0057688 | -0.0014457 | 1.8749e-07 | 3.872e-08 | 0.0087816 | 0.0087816 | 0.0087816 | 0.97753 | -0.432 | 0.97749 | -0.43269 | 2.4125
118 | 0.0039358 | 0.00098635 | -0.0039357 | -0.00098638 | 1.136e-07 | -3.3079e-08 | 0.0059914 | 0.0059914 | 0.0059914 | 0.97749 | -0.43269 | 0.97746 | -0.43329 | 1.646
119 | 0.00052758 | 0.0001318 | -0.00052757 | -0.00013222 | 8.286e-09 | -4.2603e-07 | 0.00080211 | 0.00080227 | 0.00080227 | 0.97853 | -0.41246 | 0.97852 | -0.41279 | 0.2204
120 | 0.010401 | 0.0026098 | -0.010394 | -0.0026062 | 7.0396e-06 | 3.5635e-06 | 0.015817 | 0.015817 | 0.015817 | 0.97853 | -0.41246 | 0.97781 | -0.42666 | 4.3454
121 | 0.0017376 | 0.00043347 | -0.0017372 | -0.00043537 | 4.5874e-07 | -1.9009e-06 | 0.0026436 | 0.0026443 | 0.0026443 | 0.97781 | -0.42666 | 0.97753 | -0.43221 | 0.72647
122 | 0.008656 | 0.0021727 | -0.0086538 | -0.0021718 | 2.1881e-06 | 9.7879e-07 | 0.013174 | 0.013174 | 0.013174 | 0.97781 | -0.42666 | 0.97754 | -0.43196 | 3.6192
123 | 0.0086538 | 0.0021718 | -0.0086385 | -0.0021649 | 1.5278e-05 | 6.8408e-06 | 0.013174 | 0.013175 | 0.013175 | 0.97754 | -0.43196 | 0.97566 | -0.46903 | 3.6195
124 | 0.0083534 | 0.0020934 | -0.008353 | -0.0020933 | 3.6515e-07 | 1.5878e-07 | 0.01274 | 0.01274 | 0.01274 | 0.97566 | -0.46903 | 0.97561 | -0.46995 | 3.5
125 | 0.0020695 | 0.00051859 | -0.0020695 | -0.00051866 | 2.8426e-08 | -7.811e-08 | 0.0031457 | 0.0031458 | 0.0031458 | 0.97893 | -0.40548 | 0.97892 | -0.40577 | 0.86422
126 | 0.0015452 | 0.00038714 | -0.0015452 | -0.00038726 | 2.1847e-08 | -1.1891e-07 | 0.0023482 | 0.0023482 | 0.0023482 | 0.97915 | -0.40111 | 0.97914 | -0.40141 | 0.64512
127 | 0.0060461 | 0.001515 | -0.0060448 | -0.0015147 | 1.3081e-06 | 3.1947e-07 | 0.0091964 | 0.0091966 | 0.0091966 | 0.97828 | -0.41827 | 0.97805 | -0.42281 | 2.5265
128 | 0.0043212 | 0.0010827 | -0.0043208 | -0.0010828 | 4.0066e-07 | -5.3774e-08 | 0.0065742 | 0.0065743 | 0.0065743 | 0.97805 | -0.42281 | 0.97795 | -0.42476 | 1.8061
129 | 0.0043208 | 0.0010828 | -0.0043204 | -0.0010828 | 3.6923e-07 | -4.949e-08 | 0.0065743 | 0.0065744 | 0.0065744 | 0.97795 | -0.42476 | 0.97786 | -0.42655 | 1.8062
130 | 0.0076864 | 0.0019262 | -0.007686 | -0.0019261 | 3.8664e-07 | 1.5378e-07 | 0.011723 | 0.011723 | 0.011723 | 0.97561 | -0.46995 | 0.97556 | -0.47101 | 3.2207
131 | 0.0061536 | 0.001542 | -0.0061511 | -0.0015414 | 2.528e-06 | 6.6296e-07 | 0.009386 | 0.0093864 | 0.0093864 | 0.97556 | -0.47101 | 0.97512 | -0.47963 | 2.5787
132 | 0.0059585 | 0.0014931 | -0.0059583 | -0.001493 | 1.8933e-07 | 4.4993e-08 | 0.0090925 | 0.0090926 | 0.0090926 | 0.97512 | -0.47963 | 0.97508 | -0.4803 | 2.498
133 | 0.0053889 | 0.0013503 | -0.0053866 | -0.00135 | 2.3114e-06 | 3.4299e-07 | 0.0082236 | 0.008224 | 0.008224 | 0.97508 | -0.4803 | 0.97463 | -0.48931 | 2.2593
134 | 0.0018211 | 0.00045639 | -0.0018211 | -0.00045641 | 4.5769e-09 | -1.6746e-08 | 0.0027803 | 0.0027804 | 0.0027804 | 0.97463 | -0.48931 | 0.97462 | -0.48936 | 0.76383
135 | 0.0052858 | 0.0013244 | -0.0052855 | -0.0013243 | 2.2219e-07 | 2.951e-08 | 0.0080821 | 0.0080822 | 0.0080822 | 0.97315 | -0.51808 | 0.97311 | -0.51896 | 2.2204
136 | 0.0039708 | 0.00099482 | -0.0039706 | -0.00099488 | 2.1287e-07 | -5.5037e-08 | 0.0060718 | 0.0060718 | 0.0060718 | 0.97311 | -0.51896 | 0.97305 | -0.52009 | 1.6681
137 | 0.0025252 | 0.00063264 | -0.0025252 | -0.00063276 | 7.3514e-08 | -1.1624e-07 | 0.0038616 | 0.0038616 | 0.0038616 | 0.97305 | -0.52009 | 0.97302 | -0.5207 | 1.0609
138 | 0.0010705 | 0.00026818 | -0.0010705 | -0.00026829 | 8.9868e-09 | -1.0532e-07 | 0.001637 | 0.0016371 | 0.0016371 | 0.97302 | -0.5207 | 0.97301 | -0.52087 | 0.44975

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.22692 | 0.057725

## res_load
| p_mw | q_mvar
0 | 0.00085641 | 0.00021464
1 | 0.0010323 | 0.00025872
2 | 0.00053679 | 0.00013453
3 | 0.00049542 | 0.00012416
4 | 0.00023024 | 5.7705e-05
5 | 0.00028778 | 7.2125e-05
6 | 0.0017095 | 0.00042844
7 | 0.00036921 | 9.2534e-05
8 | 0.0040697 | 0.00102
9 | 0.0012906 | 0.00032345
10 | 0.0018867 | 0.00047285
11 | 0.0008682 | 0.00021759
12 | 0.0025105 | 0.00062918
13 | 0.0078276 | 0.0019618
14 | 0.00046342 | 0.00011615
15 | 0.0011662 | 0.00029228
16 | 0.019293 | 0.0048353
17 | 0.0021633 | 0.00054217
18 | 0.0017797 | 0.00044603
19 | 0.00073213 | 0.00018349
20 | 0.00051301 | 0.00012857
21 | 0.0012158 | 0.0003047
22 | 0.0028987 | 0.00072648
23 | 0.0017399 | 0.00043605
24 | 0.018403 | 0.0046123
25 | 0.00019436 | 4.8712e-05
26 | 0.0025665 | 0.00064321
27 | 0.0012834 | 0.00032164
28 | 0.0022428 | 0.0005621
29 | 0.012224 | 0.0030636
30 | 0.001179 | 0.00029548
31 | 0.0022432 | 0.00056219
32 | 0.00057959 | 0.00014526
33 | 0.0092086 | 0.0023079
34 | 0.0026178 | 0.00065608
35 | 0.0019544 | 0.00048981
36 | 0.0069587 | 0.001744
37 | 0.0028758 | 0.00072074
38 | 0.003306 | 0.00082855
39 | 0.00086171 | 0.00021597
40 | 0.00077144 | 0.00019334
41 | 0.00030987 | 7.766e-05
42 | 0.00020288 | 5.0846e-05
43 | 0.00080439 | 0.0002016
44 | 0.0037903 | 0.00094995
45 | 0.0025218 | 0.00063201
46 | 0.001177 | 0.00029499
47 | 0.0018772 | 0.00047047
48 | 0.0010395 | 0.00026052
49 | 0.0014353 | 0.00035971
50 | 0.0010176 | 0.00025504
51 | 0.0017586 | 0.00044075
52 | 0.0024265 | 0.00060813
53 | 0.00092349 | 0.00023145
54 | 0.0012465 | 0.0003124
55 | 0.0018827 | 0.00047186
56 | 0.0017004 | 0.00042616
57 | 0.00095905 | 0.00024036
58 | 0.0013672 | 0.00034266
59 | 0.0015248 | 0.00038214
60 | 0.001514 | 0.00037946
61 | 0.0020587 | 0.00051595
62 | 0.0013395 | 0.0003357
63 | 0.0014204 | 0.00035598
64 | 0.0024893 | 0.00062387
65 | 0.0020088 | 0.00050346
66 | 0.0074653 | 0.001871
67 | 0.0010787 | 0.00027034
68 | 0.001803 | 0.00045187
69 | 0.0018009 | 0.00045135
70 | 0.0018776 | 0.00047058
71 | 0.0018841 | 0.00047221
72 | 0.0018852 | 0.00047247
73 | 0.0018324 | 0.00045924
74 | 0.001833 | 0.00045938
75 | 0.0039357 | 0.00098638
76 | 0.0016766 | 0.00042018
77 | 0.0017372 | 0.00043537
78 | 0.00052757 | 0.00013222
79 | 0.00028514 | 7.1462e-05
80 | 0.0015484 | 0.00038806
81 | 0.0020694 | 0.00051864
82 | 0.0020695 | 0.00051866
83 | 0.0017236 | 0.00043198
84 | 0.0015452 | 0.00038726
85 | 0.0043204 | 0.0010828
86 | 0.00066659 | 0.00016706
87 | 0.0015324 | 0.00038406
88 | 0.00019258 | 4.8264e-05
89 | 0.00056944 | 0.00014272
90 | 0.0035655 | 0.00089359
91 | 0.0018211 | 0.00045641
92 | 0.0010902 | 0.00027322
93 | 0.0013147 | 0.0003295
94 | 0.0014453 | 0.00036224
95 | 0.0014547 | 0.00036458
96 | 0.0010705 | 0.00026829

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1