## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1059-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1059-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1059-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1059-20_0_3_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1059-20_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1059-20_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1059-20_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1059-20_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1059-20_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1059-20_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1059-20_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1059-20_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1059-20_0_3_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_1059-20_0_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1059-20_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1059-20_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1059-20_0_3_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_1059-20_0_3_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_1059-20_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1059-20_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1059-20_0_3_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1059-20_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1059-20_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1059-20_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1059-20_0_3_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_1059-20_0_3_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_1059-20_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1059-20_0_3_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_1059-20_0_3_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1059-20_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1059-20_0_3_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_1059-20_0_3_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1059-20_0_3_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1059-20_0_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1059-20_0_3_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_1059-20_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1059-20_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1059-20_0_3_node_30 | 0.4 | n |  | TRUE
40 | bus_MV_24_1_node_194 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-20_0_3_load_0 | 0 | 0.013346 | 0.0033449 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-20_0_3_load_1 | 1 | 0.0026683 | 0.00066875 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-20_0_3_load_2 | 2 | 0.0060876 | 0.0015257 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-20_0_3_load_3 | 3 | 0.0034792 | 0.00087198 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-20_0_3_load_4 | 4 | 0.0035502 | 0.00088976 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-20_0_3_load_15 | 5 | 0.019029 | 0.004769 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-20_0_3_load_6 | 6 | 0.010318 | 0.0025859 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-20_0_3_load_5 | 8 | 0.022988 | 0.0057613 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-20_0_3_load_8 | 10 | 0.011308 | 0.002834 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-20_0_3_load_16 | 11 | 0.0063719 | 0.001597 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-20_0_3_load_24 | 14 | 0.010614 | 0.0026601 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1059-20_0_3_load_22 | 15 | 0.012583 | 0.0031536 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1059-20_0_3_load_38 | 18 | 0.014614 | 0.0036627 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1059-20_0_3_load_41 | 19 | 0.018104 | 0.0045373 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1059-20_0_3_load_21 | 21 | 0.015319 | 0.0038393 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1059-20_0_3_load_23 | 25 | 0.010462 | 0.0026219 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1059-20_0_3_load_42 | 26 | 0.014222 | 0.0035645 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1059-20_0_3_load_31 | 31 | 0.01676 | 0.0042004 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1059-20_0_3_load_39 | 32 | 0.017205 | 0.0043121 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1059-20_0_3_load_32 | 33 | 0.02067 | 0.0051805 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1059-20_0_3_load_43 | 34 | 0.014823 | 0.0037149 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1059-20_0_3_load_25 | 36 | 0.014675 | 0.003678 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1059-20_0_3_load_28 | 37 | 0.016453 | 0.0041234 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1059-20_0_3_load_29 | 38 | 0.014222 | 0.0035644 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1059-20_0_3_load_30 | 39 | 0.018187 | 0.004558 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-20_0_3_line_0 |  | 0 | 1 | 0.024457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1059-20_0_3_line_1 |  | 0 | 2 | 0.029582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1059-20_0_3_line_2 |  | 1 | 3 | 0.010152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1059-20_0_3_line_3 |  | 2 | 4 | 0.0027527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1059-20_0_3_line_4 |  | 3 | 5 | 0.013046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1059-20_0_3_line_5 |  | 4 | 6 | 0.015417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1059-20_0_3_line_6 |  | 5 | 7 | 0.015191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1059-20_0_3_line_7 |  | 6 | 8 | 0.032294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1059-20_0_3_line_8 |  | 7 | 11 | 0.053109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1059-20_0_3_line_9 |  | 7 | 12 | 0.040676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1059-20_0_3_line_10 |  | 8 | 9 | 0.015475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1059-20_0_3_line_11 |  | 9 | 10 | 0.10983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1059-20_0_3_line_12 |  | 11 | 21 | 0.050606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1059-20_0_3_line_13 |  | 12 | 19 | 0.0114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1059-20_0_3_line_14 |  | 12 | 20 | 0.1227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1059-20_0_3_line_15 |  | 13 | 14 | 0.007261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1059-20_0_3_line_16 |  | 13 | 15 | 0.015817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1059-20_0_3_line_17 |  | 15 | 25 | 0.032271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1059-20_0_3_line_18 |  | 16 | 17 | 0.040992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1059-20_0_3_line_19 |  | 16 | 18 | 0.057142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1059-20_0_3_line_20 |  | 17 | 22 | 0.018135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1059-20_0_3_line_21 |  | 18 | 24 | 0.034298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1059-20_0_3_line_22 |  | 20 | 23 | 0.011199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1059-20_0_3_line_23 |  | 20 | 24 | 0.01878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1059-20_0_3_line_24 |  | 20 | 25 | 0.037803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1059-20_0_3_line_25 |  | 22 | 33 | 0.025582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1059-20_0_3_line_26 |  | 23 | 26 | 0.008288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1059-20_0_3_line_27 |  | 23 | 27 | 0.03522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1059-20_0_3_line_28 |  | 24 | 28 | 0.02185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1059-20_0_3_line_29 |  | 27 | 34 | 0.006417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1059-20_0_3_line_30 |  | 28 | 35 | 0.024407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1059-20_0_3_line_31 |  | 28 | 36 | 0.018501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1059-20_0_3_line_32 |  | 29 | 30 | 0.024623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1059-20_0_3_line_33 |  | 29 | 31 | 0.018249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1059-20_0_3_line_34 |  | 30 | 32 | 0.015785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1059-20_0_3_line_35 |  | 31 | 35 | 0.0067704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1059-20_0_3_line_36 |  | 35 | 37 | 0.015607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1059-20_0_3_line_37 |  | 37 | 38 | 0.029219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1059-20_0_3_line_38 |  | 38 | 39 | 0.005855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-20_0_3_trafo_30 | 0.63 MVA 20/0.4 kV | 40 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2663629.0815 | 1209281.6773 | 2663627.3933 | 1209281.1833 | 2663605.0733 | 1209277.0556
1 | 2663629.0815 | 1209281.6773 | 2663657.4729 | 1209289.9856
2 | 2663595.0907 | 1209275.2095 | 2663605.0733 | 1209277.0556
3 | 2663657.4729 | 1209289.9856 | 2663660.1148 | 1209290.7587
4 | 2663595.0907 | 1209275.2095 | 2663582.2626 | 1209272.8372
5 | 2663674.9109 | 1209295.0885 | 2663660.1148 | 1209290.7587
6 | 2663574.7615 | 1209284.569 | 2663576.4894 | 1209279.362 | 2663577.8715 | 1209275.2076 | 2663581.0766 | 1209272.6179 | 2663582.2626 | 1209272.8372
7 | 2663704.0575 | 1209286.8302 | 2663698.3995 | 1209291.9137 | 2663690.9316 | 1209295.7697 | 2663684.1247 | 1209296.7977 | 2663678.2186 | 1209296.0565 | 2663674.9109 | 1209295.0885
8 | 2663574.7615 | 1209284.569 | 2663624.9007 | 1209302.0809
9 | 2663544.9988 | 1209271.2329 | 2663548.5028 | 1209271.2702 | 2663554.5078 | 1209273.4355 | 2663555.537 | 1209281.0066 | 2663557.334 | 1209285.7175 | 2663563.9504 | 1209286.1549 | 2663565.7684 | 1209284.6066 | 2663568.3974 | 1209284.0009 | 2663574.7615 | 1209284.569
10 | 2663715.569 | 1209276.4875 | 2663704.0575 | 1209286.8302
11 | 2663715.569 | 1209276.4875 | 2663704.1948 | 1209266.0153 | 2663695.2958 | 1209258.6603 | 2663691.0638 | 1209257.0364 | 2663669.0415 | 1209250.6532 | 2663654.0628 | 1209245.9906 | 2663637.0565 | 1209241.8401 | 2663615.4721 | 1209235.7286
12 | 2663668.9005 | 1209325.661 | 2663666.009 | 1209321.8308 | 2663649.0246 | 1209311.3767 | 2663635.735 | 1209305.865 | 2663624.9007 | 1209302.0809
13 | 2663539.4692 | 1209261.5459 | 2663544.4689 | 1209268.1699 | 2663544.9988 | 1209271.2329
14 | 2663436.6172 | 1209309.6036 | 2663438.7603 | 1209313.2285 | 2663459.4899 | 1209301.0748 | 2663484.9544 | 1209287.5818 | 2663500.4319 | 1209279.6638 | 2663508.4495 | 1209276.2915 | 2663515.9496 | 1209274.4035 | 2663527.2765 | 1209271.5111 | 2663527.8259 | 1209274.163 | 2663544.9988 | 1209271.2329
15 | 2663477.3509 | 1209258.461 | 2663484.6332 | 1209258.4718
16 | 2663477.3509 | 1209258.461 | 2663461.5387 | 1209258.8492
17 | 2663445.9776 | 1209276.7376 | 2663445.5446 | 1209262.1362 | 2663446.0495 | 1209260.4072 | 2663447.307 | 1209259.3866 | 2663459.6573 | 1209258.8954 | 2663461.5387 | 1209258.8492
18 | 2663353.3237 | 1209366.4425 | 2663352.6932 | 1209365.6798 | 2663350.5169 | 1209363.0328 | 2663341.9283 | 1209368.6562 | 2663354.6123 | 1209382.5326 | 2663359.6768 | 1209388.0786
19 | 2663353.3237 | 1209366.4425 | 2663356.0729 | 1209363.103 | 2663402.262 | 1209337.4871
20 | 2663371.9248 | 1209401.4834 | 2663359.6768 | 1209388.0786
21 | 2663432.256 | 1209320.853 | 2663402.262 | 1209337.4871
22 | 2663429.4589 | 1209310.0945 | 2663429.7051 | 1209313.3991 | 2663436.6172 | 1209309.6036
23 | 2663436.6172 | 1209309.6036 | 2663438.7603 | 1209313.2285 | 2663429.3411 | 1209318.3204 | 2663432.256 | 1209320.853
24 | 2663436.6172 | 1209309.6036 | 2663444.3985 | 1209304.8612 | 2663446.3706 | 1209301.6913 | 2663446.1601 | 1209282.8887 | 2663445.9776 | 1209276.7376
25 | 2663371.9248 | 1209401.4834 | 2663383.73 | 1209378.7877
26 | 2663424.9845 | 1209304.0988 | 2663425.2254 | 1209307.1811 | 2663426.6314 | 1209308.6413 | 2663429.4589 | 1209310.0945
27 | 2663426.8906 | 1209274.968 | 2663427.5121 | 1209283.7133 | 2663427.8896 | 1209288.9649 | 2663429.4589 | 1209310.0945
28 | 2663451.4454 | 1209331.2855 | 2663436.2839 | 1209323.7975 | 2663432.256 | 1209320.853
29 | 2663426.8906 | 1209274.968 | 2663421.9399 | 1209270.8685
30 | 2663451.4454 | 1209331.2855 | 2663473.3823 | 1209342.1141
31 | 2663451.4454 | 1209331.2855 | 2663442.9326 | 1209347.7119
32 | 2663484.4675 | 1209378.3429 | 2663485.5279 | 1209372.2727 | 2663488.2625 | 1209365.3087 | 2663491.4897 | 1209359.9175 | 2663493.8967 | 1209355.8851
33 | 2663493.8967 | 1209355.8851 | 2663485.0828 | 1209347.6642 | 2663480.5939 | 1209345.1816 | 2663479.6125 | 1209344.7641
34 | 2663484.4675 | 1209378.3429 | 2663479.0112 | 1209378.9075 | 2663473.3217 | 1209379.9587 | 2663471.3894 | 1209381.528 | 2663470.1526 | 1209383.1314
35 | 2663473.3823 | 1209342.1141 | 2663479.6125 | 1209344.7641
36 | 2663473.3823 | 1209342.1141 | 2663476.2352 | 1209338.3199 | 2663482.363 | 1209329.3535
37 | 2663482.363 | 1209329.3535 | 2663485.0458 | 1209325.428 | 2663486.9179 | 1209324.514 | 2663492.8395 | 1209327.3676 | 2663495.0801 | 1209326.8356 | 2663501.5692 | 1209314.9923
38 | 2663504.3827 | 1209309.8575 | 2663501.5692 | 1209314.9923

## bus_geodata
| x | y | coords
0 | 2663629.0815 | 1209281.6773
1 | 2663605.0733 | 1209277.0556
2 | 2663657.4729 | 1209289.9856
3 | 2663595.0907 | 1209275.2095
4 | 2663660.1148 | 1209290.7587
5 | 2663582.2626 | 1209272.8372
6 | 2663674.9109 | 1209295.0885
7 | 2663574.7615 | 1209284.569
8 | 2663704.0575 | 1209286.8302
9 | 2663715.569 | 1209276.4875
10 | 2663615.4721 | 1209235.7286
11 | 2663624.9007 | 1209302.0809
12 | 2663544.9988 | 1209271.2329
13 | 2663477.3509 | 1209258.461
14 | 2663484.6332 | 1209258.4718
15 | 2663461.5387 | 1209258.8492
16 | 2663353.3237 | 1209366.4425
17 | 2663359.6768 | 1209388.0786
18 | 2663402.262 | 1209337.4871
19 | 2663539.4692 | 1209261.546
20 | 2663436.6172 | 1209309.6036
21 | 2663668.9005 | 1209325.661
22 | 2663371.9248 | 1209401.4834
23 | 2663429.4589 | 1209310.0945
24 | 2663432.256 | 1209320.853
25 | 2663445.9776 | 1209276.7376
26 | 2663424.9845 | 1209304.0988
27 | 2663426.8906 | 1209274.968
28 | 2663451.4454 | 1209331.2855
29 | 2663493.8967 | 1209355.8851
30 | 2663484.4675 | 1209378.3429
31 | 2663479.6125 | 1209344.7641
32 | 2663470.1526 | 1209383.1314
33 | 2663383.73 | 1209378.7877
34 | 2663421.9399 | 1209270.8685
35 | 2663473.3823 | 1209342.1141
36 | 2663442.9326 | 1209347.7119
37 | 2663482.363 | 1209329.3535
38 | 2663501.5692 | 1209314.9923
39 | 2663504.3827 | 1209309.8575
40 | 2663473.3823 | 1209342.1141

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97717 | -0.43971 | 0.013346 | 0.0033449
1 | 0.97871 | -0.40957 | 0.0026683 | 0.00066875
2 | 0.97567 | -0.46905 | 0.0060876 | 0.0015257
3 | 0.97937 | -0.3966 | 0.0034792 | 0.00087198
4 | 0.97555 | -0.47148 | 0.0035502 | 0.00088976
5 | 0.98027 | -0.37913 | 0.019029 | 0.004769
6 | 0.97491 | -0.48408 | 0.010318 | 0.0025859
7 | 0.98158 | -0.3536 | 0 | 0
8 | 0.97388 | -0.50442 | 0.022988 | 0.0057613
9 | 0.97372 | -0.50763 | 0 | 0
10 | 0.97256 | -0.53049 | 0.011308 | 0.002834
11 | 0.98051 | -0.37446 | 0.0063719 | 0.001597
12 | 0.9859 | -0.26973 | 0 | 0
13 | 0.98892 | -0.21192 | 0 | 0
14 | 0.98885 | -0.2133 | 0.010614 | 0.0026601
15 | 0.98908 | -0.20893 | 0.012583 | 0.0031536
16 | 0.98987 | -0.19376 | 0 | 0
17 | 0.98909 | -0.20885 | 0 | 0
18 | 0.99095 | -0.17277 | 0.014614 | 0.0036627
19 | 0.98571 | -0.27343 | 0.018104 | 0.0045373
20 | 0.99093 | -0.17299 | 0 | 0
21 | 0.97979 | -0.38853 | 0.015319 | 0.0038393
22 | 0.98875 | -0.21553 | 0 | 0
23 | 0.99063 | -0.17877 | 0 | 0
24 | 0.99206 | -0.15131 | 0 | 0
25 | 0.98976 | -0.1956 | 0.010462 | 0.0026219
26 | 0.99053 | -0.18086 | 0.014222 | 0.0035645
27 | 0.99015 | -0.18804 | 0 | 0
28 | 0.99361 | -0.12162 | 0 | 0
29 | 0.99496 | -0.096026 | 0 | 0
30 | 0.99457 | -0.10349 | 0 | 0
31 | 0.99524 | -0.090499 | 0.01676 | 0.0042004
32 | 0.99432 | -0.10827 | 0.017205 | 0.0043121
33 | 0.98826 | -0.22496 | 0.02067 | 0.0051805
34 | 0.99007 | -0.18973 | 0.014823 | 0.0037149
35 | 0.99545 | -0.086453 | 0 | 0
36 | 0.99336 | -0.12641 | 0.014675 | 0.003678
37 | 0.99679 | -0.060934 | 0.016453 | 0.0041234
38 | 0.99944 | -0.010548 | 0.014222 | 0.0035644
39 | 1 | 0 | -0.31549 | -0.080184
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.067754 | -0.017039 | 0.067852 | 0.017101 | 9.7671e-05 | 6.2202e-05 | 0.1032 | 0.1032 | 0.1032 | 0.97717 | -0.43971 | 0.97871 | -0.40957 | 28.3504
1 | 0.054408 | 0.013694 | -0.054331 | -0.013646 | 7.6186e-05 | 4.8389e-05 | 0.082872 | 0.082872 | 0.082872 | 0.97717 | -0.43971 | 0.97567 | -0.46905 | 22.7671
2 | -0.07052 | -0.01777 | 0.070564 | 0.017798 | 4.3792e-05 | 2.7899e-05 | 0.10725 | 0.10725 | 0.10725 | 0.97871 | -0.40957 | 0.97937 | -0.3966 | 29.4649
3 | 0.048244 | 0.01212 | -0.048238 | -0.012116 | 5.5899e-06 | 3.5431e-06 | 0.073588 | 0.073588 | 0.073588 | 0.97567 | -0.46905 | 0.97555 | -0.47148 | 20.2164
4 | -0.074043 | -0.01867 | 0.074105 | 0.018709 | 6.1958e-05 | 3.9489e-05 | 0.11254 | 0.11254 | 0.11254 | 0.97937 | -0.3966 | 0.98027 | -0.37913 | 30.9172
5 | 0.044688 | 0.011227 | -0.044661 | -0.01121 | 2.6868e-05 | 1.7003e-05 | 0.068173 | 0.068173 | 0.068173 | 0.97555 | -0.47148 | 0.97491 | -0.48408 | 18.7288
6 | -0.093134 | -0.023478 | 0.093248 | 0.023551 | 0.00011394 | 7.2728e-05 | 0.14142 | 0.14142 | 0.14142 | 0.98027 | -0.37913 | 0.98158 | -0.3536 | 38.8526
7 | 0.034343 | 0.0086237 | -0.03431 | -0.0086028 | 3.3282e-05 | 2.0899e-05 | 0.052424 | 0.052424 | 0.052424 | 0.97491 | -0.48408 | 0.97388 | -0.50442 | 14.4023
8 | 0.021723 | 0.0054553 | -0.021701 | -0.0054421 | 2.1602e-05 | 1.3155e-05 | 0.032934 | 0.032935 | 0.032935 | 0.98158 | -0.3536 | 0.98051 | -0.37446 | 9.048
9 | -0.11497 | -0.029006 | 0.11543 | 0.029303 | 0.00046372 | 0.00029626 | 0.17436 | 0.17436 | 0.17436 | 0.98158 | -0.3536 | 0.9859 | -0.26973 | 47.9004
10 | 0.011322 | 0.0028415 | -0.01132 | -0.0028405 | 1.737e-06 | 9.1913e-07 | 0.0173 | 0.017301 | 0.017301 | 0.97388 | -0.50442 | 0.97372 | -0.50763 | 4.7529
11 | 0.01132 | 0.0028405 | -0.011308 | -0.002834 | 1.2327e-05 | 6.525e-06 | 0.017301 | 0.017301 | 0.017301 | 0.97372 | -0.50763 | 0.97256 | -0.53049 | 4.753
12 | 0.015329 | 0.0038452 | -0.015319 | -0.0038393 | 1.0271e-05 | 5.9359e-06 | 0.023265 | 0.023265 | 0.023265 | 0.98051 | -0.37446 | 0.97979 | -0.38853 | 6.3914
13 | 0.018107 | 0.0045392 | -0.018104 | -0.0045373 | 3.193e-06 | 1.8982e-06 | 0.02733 | 0.02733 | 0.02733 | 0.9859 | -0.26973 | 0.98571 | -0.27343 | 7.5082
14 | -0.13354 | -0.033842 | 0.13417 | 0.034236 | 0.00062387 | 0.00039456 | 0.20169 | 0.20169 | 0.20169 | 0.9859 | -0.26973 | 0.99093 | -0.17299 | 18.4695
15 | 0.010614 | 0.0026604 | -0.010614 | -0.0026601 | 6.9458e-07 | 3.5137e-07 | 0.015972 | 0.015972 | 0.015972 | 0.98892 | -0.21192 | 0.98885 | -0.2133 | 4.3878
16 | -0.010614 | -0.0026604 | 0.010616 | 0.0026612 | 1.513e-06 | 7.6537e-07 | 0.015972 | 0.015971 | 0.015972 | 0.98892 | -0.21192 | 0.98908 | -0.20893 | 4.3878
17 | -0.023199 | -0.0058148 | 0.023214 | 0.0058238 | 1.4741e-05 | 9.0201e-06 | 0.034902 | 0.034902 | 0.034902 | 0.98908 | -0.20893 | 0.98976 | -0.1956 | 9.5885
18 | 0.020701 | 0.0051991 | -0.020686 | -0.0051901 | 1.489e-05 | 9.003e-06 | 0.031123 | 0.031123 | 0.031123 | 0.98987 | -0.19376 | 0.98909 | -0.20885 | 8.5502
19 | -0.020701 | -0.0051991 | 0.020722 | 0.0052116 | 2.0756e-05 | 1.2548e-05 | 0.031123 | 0.031122 | 0.031123 | 0.98987 | -0.19376 | 0.99095 | -0.17277 | 8.5502
20 | 0.020686 | 0.0051901 | -0.02068 | -0.0051861 | 6.5873e-06 | 3.9832e-06 | 0.031123 | 0.031123 | 0.031123 | 0.98909 | -0.20885 | 0.98875 | -0.21553 | 8.5502
21 | -0.035336 | -0.0088743 | 0.035372 | 0.008897 | 3.622e-05 | 2.2738e-05 | 0.053067 | 0.053067 | 0.053067 | 0.99095 | -0.17277 | 0.99206 | -0.15131 | 14.5789
22 | 0.029062 | 0.0072896 | -0.029054 | -0.0072847 | 7.9995e-06 | 4.9755e-06 | 0.043643 | 0.043643 | 0.043643 | 0.99093 | -0.17299 | 0.99063 | -0.17877 | 11.9899
23 | -0.19694 | -0.049995 | 0.19714 | 0.050125 | 0.00020562 | 0.00013087 | 0.29596 | 0.29596 | 0.29596 | 0.99093 | -0.17299 | 0.99206 | -0.15131 | 27.1024
24 | 0.033712 | 0.0084685 | -0.033675 | -0.0084458 | 3.6339e-05 | 2.2771e-05 | 0.05063 | 0.05063 | 0.05063 | 0.99093 | -0.17299 | 0.98976 | -0.1956 | 13.9093
25 | 0.02068 | 0.0051861 | -0.02067 | -0.0051805 | 9.2925e-06 | 5.6193e-06 | 0.031123 | 0.031123 | 0.031123 | 0.98875 | -0.21553 | 0.98826 | -0.22496 | 8.5503
26 | 0.014224 | 0.0035653 | -0.014222 | -0.0035645 | 1.4188e-06 | 8.0133e-07 | 0.021366 | 0.021366 | 0.021366 | 0.99063 | -0.17877 | 0.99053 | -0.18086 | 5.8697
27 | 0.014831 | 0.0037194 | -0.014824 | -0.0037156 | 6.5549e-06 | 3.7419e-06 | 0.022278 | 0.022278 | 0.022278 | 0.99063 | -0.17877 | 0.99015 | -0.18804 | 6.1203
28 | -0.23252 | -0.059022 | 0.23285 | 0.059234 | 0.00033272 | 0.00021209 | 0.34902 | 0.34902 | 0.34902 | 0.99206 | -0.15131 | 0.99361 | -0.12162 | 31.9619
29 | 0.014824 | 0.0037156 | -0.014823 | -0.0037149 | 1.1943e-06 | 6.8181e-07 | 0.022278 | 0.022278 | 0.022278 | 0.99015 | -0.18804 | 0.99007 | -0.18973 | 6.1203
30 | -0.24753 | -0.062914 | 0.24795 | 0.063182 | 0.00041994 | 0.00026781 | 0.37101 | 0.37101 | 0.37101 | 0.99361 | -0.12162 | 0.99545 | -0.086453 | 33.975
31 | 0.014679 | 0.0036799 | -0.014675 | -0.003678 | 3.3528e-06 | 1.9062e-06 | 0.021983 | 0.021983 | 0.021983 | 0.99361 | -0.12162 | 0.99336 | -0.12641 | 6.0393
32 | 0.017215 | 0.004318 | -0.017209 | -0.0043144 | 6.1216e-06 | 3.5982e-06 | 0.025748 | 0.025748 | 0.025748 | 0.99496 | -0.096026 | 0.99457 | -0.10349 | 7.0736
33 | -0.017215 | -0.004318 | 0.01722 | 0.0043207 | 4.5368e-06 | 2.6665e-06 | 0.025748 | 0.025748 | 0.025748 | 0.99496 | -0.096026 | 0.99524 | -0.090499 | 7.0736
34 | 0.017209 | 0.0043144 | -0.017205 | -0.0043121 | 3.9245e-06 | 2.3068e-06 | 0.025748 | 0.025748 | 0.025748 | 0.99457 | -0.10349 | 0.99432 | -0.10827 | 7.0737
35 | -0.03398 | -0.0085211 | 0.033986 | 0.0085252 | 6.5535e-06 | 4.1062e-06 | 0.050806 | 0.050806 | 0.050806 | 0.99524 | -0.090499 | 0.99545 | -0.086453 | 13.9577
36 | -0.28194 | -0.071707 | 0.28228 | 0.071929 | 0.00034712 | 0.00022155 | 0.42181 | 0.42181 | 0.42181 | 0.99545 | -0.086453 | 0.99679 | -0.060934 | 38.6275
37 | -0.29873 | -0.076052 | 0.29946 | 0.076517 | 0.00072772 | 0.0004646 | 0.44637 | 0.44637 | 0.44637 | 0.99679 | -0.060934 | 0.99944 | -0.010548 | 40.8766
38 | -0.31368 | -0.080081 | 0.31384 | 0.080183 | 0.00015999 | 0.00010216 | 0.46755 | 0.46755 | 0.46755 | 0.99944 | -0.010548 | 1 | 0 | 42.8156

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33368 | 0.084742

## res_load
| p_mw | q_mvar
0 | 0.013346 | 0.0033449
1 | 0.0026683 | 0.00066875
2 | 0.0060876 | 0.0015257
3 | 0.0034792 | 0.00087198
4 | 0.0035502 | 0.00088976
5 | 0.019029 | 0.004769
6 | 0.010318 | 0.0025859
7 | 0.022988 | 0.0057613
8 | 0.011308 | 0.002834
9 | 0.0063719 | 0.001597
10 | 0.010614 | 0.0026601
11 | 0.012583 | 0.0031536
12 | 0.014614 | 0.0036627
13 | 0.018104 | 0.0045373
14 | 0.015319 | 0.0038393
15 | 0.010462 | 0.0026219
16 | 0.014222 | 0.0035645
17 | 0.01676 | 0.0042004
18 | 0.017205 | 0.0043121
19 | 0.02067 | 0.0051805
20 | 0.014823 | 0.0037149
21 | 0.014675 | 0.003678
22 | 0.016453 | 0.0041234
23 | 0.014222 | 0.0035644
24 | 0.018187 | 0.004558

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1