## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-33_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-33_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1059-33_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1059-33_0_3_node_47 | 0.4 | n |  | TRUE
4 | bus_LV_1059-33_0_3_node_48 | 0.4 | n |  | TRUE
5 | bus_LV_1059-33_0_3_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_1059-33_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1059-33_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1059-33_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1059-33_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1059-33_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1059-33_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1059-33_0_3_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1059-33_0_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1059-33_0_3_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_1059-33_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1059-33_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1059-33_0_3_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_1059-33_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1059-33_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1059-33_0_3_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_1059-33_0_3_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1059-33_0_3_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_1059-33_0_3_node_46 | 0.4 | n |  | TRUE
24 | bus_LV_1059-33_0_3_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1059-33_0_3_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_1059-33_0_3_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_1059-33_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1059-33_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1059-33_0_3_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_1059-33_0_3_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1059-33_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1059-33_0_3_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_1059-33_0_3_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_1059-33_0_3_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_1059-33_0_3_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_1059-33_0_3_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1059-33_0_3_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1059-33_0_3_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1059-33_0_3_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1059-33_0_3_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_1059-33_0_3_node_52 | 0.4 | n |  | TRUE
42 | bus_LV_1059-33_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1059-33_0_3_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_1059-33_0_3_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_1059-33_0_3_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1059-33_0_3_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1059-33_0_3_node_41 | 0.4 | n |  | TRUE
48 | bus_MV_24_1_node_180 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-33_0_3_load_0 | 0 | 0.013488 | 0.0033805 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-33_0_3_load_1 | 1 | 0.0064797 | 0.001624 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-33_0_3_load_2 | 2 | 0.0064758 | 0.001623 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-33_0_3_load_47 | 3 | 0.02676 | 0.0067066 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-33_0_3_load_48 | 4 | 0.013038 | 0.0032676 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-33_0_3_load_3 | 6 | 0.013083 | 0.0032789 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-33_0_3_load_4 | 7 | 0.011464 | 0.0028733 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-33_0_3_load_30 | 12 | 0.015702 | 0.0039352 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-33_0_3_load_29 | 13 | 0.0082411 | 0.0020654 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-33_0_3_load_51 | 14 | 0.012036 | 0.0030164 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-33_0_3_load_45 | 17 | 0.048116 | 0.012059 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1059-33_0_3_load_10 | 19 | 0.025849 | 0.0064783 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1059-33_0_3_load_50 | 20 | 0.01147 | 0.0028746 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1059-33_0_3_load_46 | 23 | 0.0073854 | 0.001851 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1059-33_0_3_load_42 | 24 | 0.0091822 | 0.0023013 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1059-33_0_3_load_28 | 28 | 0.0071781 | 0.001799 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1059-33_0_3_load_18 | 30 | 0.003502 | 0.00087767 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1059-33_0_3_load_44 | 32 | 0.0088343 | 0.0022141 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1059-33_0_3_load_40 | 34 | 0.0076917 | 0.0019277 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1059-33_0_3_load_17 | 35 | 0.0091386 | 0.0022904 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1059-33_0_3_load_26 | 39 | 0.0069293 | 0.0017366 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1059-33_0_3_load_49 | 40 | 0.0065162 | 0.0016331 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1059-33_0_3_load_52 | 41 | 0.0065133 | 0.0016324 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1059-33_0_3_load_43 | 42 | 0.0032162 | 0.00080606 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1059-33_0_3_load_25 | 43 | 0.0057941 | 0.0014521 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1059-33_0_3_load_38 | 44 | 0.0039406 | 0.00098761 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1059-33_0_3_load_37 | 45 | 0.0023077 | 0.00057837 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1059-33_0_3_load_27 | 46 | 0.0071826 | 0.0018001 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1059-33_0_3_load_41 | 47 | 0.011832 | 0.0029653 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-33_0_3_line_0 |  | 0 | 1 | 0.010122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1059-33_0_3_line_1 |  | 1 | 2 | 0.017506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1059-33_0_3_line_2 |  | 2 | 3 | 0.01195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1059-33_0_3_line_3 |  | 3 | 4 | 0.017334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1059-33_0_3_line_4 |  | 3 | 5 | 0.029547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1059-33_0_3_line_5 |  | 5 | 26 | 0.003227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1059-33_0_3_line_6 |  | 6 | 7 | 0.053132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1059-33_0_3_line_7 |  | 7 | 8 | 0.033516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1059-33_0_3_line_8 |  | 8 | 9 | 0.031442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1059-33_0_3_line_9 |  | 8 | 10 | 0.008826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1059-33_0_3_line_10 |  | 9 | 14 | 0.025069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1059-33_0_3_line_11 |  | 9 | 15 | 0.006877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1059-33_0_3_line_12 |  | 10 | 19 | 0.021764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1059-33_0_3_line_13 |  | 11 | 12 | 0.027967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1059-33_0_3_line_14 |  | 11 | 13 | 0.011945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1059-33_0_3_line_15 |  | 12 | 15 | 0.010762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1059-33_0_3_line_16 |  | 14 | 20 | 0.015883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1059-33_0_3_line_17 |  | 16 | 17 | 0.042537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1059-33_0_3_line_18 |  | 16 | 18 | 0.002976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1059-33_0_3_line_19 |  | 18 | 21 | 0.010691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1059-33_0_3_line_20 |  | 18 | 19 | 0.013955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1059-33_0_3_line_21 |  | 21 | 22 | 0.0059814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1059-33_0_3_line_22 |  | 21 | 23 | 0.023505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1059-33_0_3_line_23 |  | 22 | 24 | 0.021255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1059-33_0_3_line_24 |  | 22 | 25 | 0.037121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1059-33_0_3_line_25 |  | 25 | 33 | 0.072555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1059-33_0_3_line_26 |  | 25 | 34 | 0.022707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1059-33_0_3_line_27 |  | 25 | 31 | 0.017341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1059-33_0_3_line_28 |  | 26 | 27 | 0.030246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1059-33_0_3_line_29 |  | 26 | 28 | 0.012214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1059-33_0_3_line_30 |  | 27 | 29 | 0.005292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1059-33_0_3_line_31 |  | 27 | 30 | 0.043104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1059-33_0_3_line_32 |  | 28 | 46 | 0.021736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1059-33_0_3_line_33 |  | 29 | 32 | 0.023111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1059-33_0_3_line_34 |  | 29 | 42 | 0.02042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1059-33_0_3_line_35 |  | 30 | 35 | 0.031161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1059-33_0_3_line_36 |  | 31 | 32 | 0.016714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1059-33_0_3_line_37 |  | 33 | 45 | 0.05664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1059-33_0_3_line_38 |  | 34 | 47 | 0.020018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1059-33_0_3_line_39 |  | 36 | 37 | 0.031737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1059-33_0_3_line_40 |  | 36 | 38 | 0.03426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1059-33_0_3_line_41 |  | 36 | 39 | 0.0032431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1059-33_0_3_line_42 |  | 37 | 41 | 0.013001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1059-33_0_3_line_43 |  | 38 | 40 | 0.0070248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1059-33_0_3_line_44 |  | 39 | 43 | 0.018443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1059-33_0_3_line_45 |  | 43 | 46 | 0.033383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1059-33_0_3_line_46 |  | 44 | 45 | 0.028349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-33_0_3_trafo_48 | 0.63 MVA 20/0.4 kV | 48 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2664845.5241 | 1209774.3589 | 2664851.9147 | 1209782.2086
1 | 2664851.9147 | 1209782.2086 | 2664854.3001 | 1209785.1386 | 2664863.4702 | 1209795.3546
2 | 2664871.453 | 1209804.2478 | 2664863.4702 | 1209795.3546
3 | 2664883.855 | 1209816.39 | 2664879.4981 | 1209812.3402 | 2664871.453 | 1209804.2478
4 | 2664871.453 | 1209804.2478 | 2664893.2424 | 1209784.2279
5 | 2664895.6225 | 1209782.0414 | 2664893.2424 | 1209784.2279
6 | 2664810.9074 | 1209829.3833 | 2664835.7047 | 1209854.6791 | 2664848.6848 | 1209866.7258
7 | 2664875.1169 | 1209883.903 | 2664873.2384 | 1209882.604 | 2664861.3471 | 1209871.0455 | 2664854.937 | 1209871.9764 | 2664851.1836 | 1209869.0449 | 2664848.6848 | 1209866.7258
8 | 2664853.0676 | 1209882.4291 | 2664859.0566 | 1209886.6635 | 2664864.6709 | 1209890.4157 | 2664866.6365 | 1209891.3932 | 2664870.657 | 1209893.5271 | 2664874.751 | 1209884.6995 | 2664875.1169 | 1209883.903
9 | 2664883.5988 | 1209883.2726 | 2664882.7421 | 1209883.7636 | 2664880.0028 | 1209884.7344 | 2664875.1169 | 1209883.903
10 | 2664853.0676 | 1209882.4291 | 2664840.7849 | 1209870.5106 | 2664835.2983 | 1209864.7522
11 | 2664848.0904 | 1209887.1891 | 2664853.0676 | 1209882.4291
12 | 2664883.5988 | 1209883.2726 | 2664887.4996 | 1209881.0358 | 2664892.2309 | 1209875.8174 | 2664898.3462 | 1209867.6241
13 | 2664820.1712 | 1209913.8799 | 2664827.4505 | 1209907.0993 | 2664831.1366 | 1209902.2363 | 2664840.2377 | 1209894.5442
14 | 2664820.1712 | 1209913.8799 | 2664811.4468 | 1209905.7215
15 | 2664848.0904 | 1209887.1891 | 2664841.6693 | 1209893.3342 | 2664840.2377 | 1209894.5442
16 | 2664824.3423 | 1209853.253 | 2664835.2983 | 1209864.7522
17 | 2664909.1839 | 1209858.0798 | 2664947.5037 | 1209876.5448
18 | 2664906.6934 | 1209856.4406 | 2664907.3424 | 1209856.8701 | 2664909.1839 | 1209858.0798
19 | 2664906.6934 | 1209856.4406 | 2664913.0879 | 1209847.8604
20 | 2664906.6934 | 1209856.4406 | 2664898.3462 | 1209867.6241
21 | 2664913.0879 | 1209847.8604 | 2664914.8697 | 1209845.4783 | 2664915.2998 | 1209845.761 | 2664917.3828 | 1209847.1289
22 | 2664913.0879 | 1209847.8604 | 2664895.3408 | 1209832.4479
23 | 2664917.3828 | 1209847.1289 | 2664919.896 | 1209848.7795 | 2664936.2394 | 1209856.8976
24 | 2664917.3828 | 1209847.1289 | 2664927.5873 | 1209833.4871 | 2664930.6574 | 1209827.9616 | 2664932.0608 | 1209823.3295 | 2664940.4327 | 1209820.241
25 | 2664955.1859 | 1209768.6143 | 2664970.2582 | 1209804.2557 | 2664963.6428 | 1209807.2856 | 2664940.4327 | 1209820.241
26 | 2664940.4327 | 1209820.241 | 2664954.7117 | 1209837.8959
27 | 2664929.3164 | 1209808.0125 | 2664932.6821 | 1209811.6403 | 2664935.6735 | 1209814.0521 | 2664938.9569 | 1209815.4664 | 2664939.0669 | 1209815.8345 | 2664940.4327 | 1209820.241
28 | 2664895.6225 | 1209782.0414 | 2664903.6204 | 1209790.9782 | 2664909.7379 | 1209784.1072 | 2664910.6463 | 1209780.9596 | 2664912.2421 | 1209775.4069
29 | 2664895.6225 | 1209782.0414 | 2664887.4729 | 1209772.9434
30 | 2664917.107 | 1209773.2918 | 2664912.2421 | 1209775.4069
31 | 2664912.2421 | 1209775.4069 | 2664913.9483 | 1209769.4885 | 2664912.7634 | 1209759.6363 | 2664906.901 | 1209747.9431 | 2664897.6156 | 1209737.5441
32 | 2664887.4729 | 1209772.9434 | 2664872.9703 | 1209756.7529
33 | 2664917.107 | 1209773.2918 | 2664920.1522 | 1209781.2298 | 2664923.4774 | 1209787.8923 | 2664927.1751 | 1209788.9554 | 2664928.2807 | 1209792.081
34 | 2664917.107 | 1209773.2918 | 2664935.8335 | 1209765.1502
35 | 2664876.8615 | 1209714.3007 | 2664897.6156 | 1209737.5441
36 | 2664929.3164 | 1209808.0125 | 2664931.3046 | 1209800.6297 | 2664928.2807 | 1209792.081
37 | 2664955.1859 | 1209768.6143 | 2664933.986 | 1209716.0911
38 | 2664954.7117 | 1209837.8959 | 2664959.1752 | 1209843.4146 | 2664964.3441 | 1209855.2559 | 2664964.3441 | 1209855.2559
39 | 2664836.2267 | 1209715.7332 | 2664834.001 | 1209717.6991 | 2664853.1274 | 1209739.1866
40 | 2664817.0805 | 1209739.4286 | 2664814.7528 | 1209736.7906 | 2664814.6748 | 1209734.8775 | 2664834.001 | 1209717.6991 | 2664836.2267 | 1209715.7332
41 | 2664836.2267 | 1209715.7332 | 2664838.3905 | 1209718.1488
42 | 2664853.1274 | 1209739.1866 | 2664843.4703 | 1209747.9204
43 | 2664817.0805 | 1209739.4286 | 2664821.7292 | 1209744.6953
44 | 2664850.6963 | 1209731.8867 | 2664838.3905 | 1209718.1488
45 | 2664872.9703 | 1209756.7529 | 2664850.6963 | 1209731.8867
46 | 2664933.986 | 1209716.0911 | 2664923.3752 | 1209689.8026

## bus_geodata
| x | y | coords
0 | 2664845.5241 | 1209774.3589
1 | 2664851.9147 | 1209782.2086
2 | 2664863.4702 | 1209795.3546
3 | 2664871.453 | 1209804.2478
4 | 2664883.855 | 1209816.39
5 | 2664893.2424 | 1209784.2279
6 | 2664810.9074 | 1209829.3833
7 | 2664848.6848 | 1209866.7258
8 | 2664875.1169 | 1209883.903
9 | 2664853.0676 | 1209882.4291
10 | 2664883.5988 | 1209883.2726
11 | 2664820.1712 | 1209913.8799
12 | 2664840.2377 | 1209894.5442
13 | 2664811.4468 | 1209905.7215
14 | 2664835.2983 | 1209864.7522
15 | 2664848.0904 | 1209887.1891
16 | 2664909.1839 | 1209858.0798
17 | 2664947.5037 | 1209876.5448
18 | 2664906.6934 | 1209856.4406
19 | 2664898.3462 | 1209867.6241
20 | 2664824.3423 | 1209853.253
21 | 2664913.0879 | 1209847.8604
22 | 2664917.3828 | 1209847.1289
23 | 2664895.3408 | 1209832.4479
24 | 2664936.2394 | 1209856.8976
25 | 2664940.4327 | 1209820.241
26 | 2664895.6225 | 1209782.0414
27 | 2664912.2421 | 1209775.4069
28 | 2664887.4729 | 1209772.9434
29 | 2664917.107 | 1209773.2918
30 | 2664897.6156 | 1209737.5441
31 | 2664929.3164 | 1209808.0125
32 | 2664928.2807 | 1209792.081
33 | 2664955.1859 | 1209768.6143
34 | 2664954.7117 | 1209837.8959
35 | 2664876.8615 | 1209714.3007
36 | 2664836.2267 | 1209715.7332
37 | 2664853.1274 | 1209739.1866
38 | 2664817.0805 | 1209739.4286
39 | 2664838.3905 | 1209718.1488
40 | 2664821.7292 | 1209744.6953
41 | 2664843.4703 | 1209747.9204
42 | 2664935.8335 | 1209765.1502
43 | 2664850.6963 | 1209731.8867
44 | 2664923.3752 | 1209689.8026
45 | 2664933.986 | 1209716.0911
46 | 2664872.9703 | 1209756.7529
47 | 2664964.3441 | 1209855.2559
48 | 2664871.453 | 1209804.2478

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99765 | -0.044939 | 0.013488 | 0.0033805
1 | 0.99777 | -0.042548 | 0.0064797 | 0.001624
2 | 0.99809 | -0.03643 | 0.0064758 | 0.001623
3 | 0.99838 | -0.030902 | 0.02676 | 0.0067066
4 | 1 | 0 | -0.31104 | -0.078722
5 | 0.99608 | -0.0746 | 0 | 0
6 | 0.98262 | -0.33483 | 0.013083 | 0.0032789
7 | 0.98326 | -0.32229 | 0.011464 | 0.0028733
8 | 0.98402 | -0.30746 | 0 | 0
9 | 0.98264 | -0.33436 | 0 | 0
10 | 0.98461 | -0.29603 | 0 | 0
11 | 0.98204 | -0.34615 | 0 | 0
12 | 0.98225 | -0.34199 | 0.015702 | 0.0039352
13 | 0.98195 | -0.34793 | 0.0082411 | 0.0020654
14 | 0.9821 | -0.345 | 0.012036 | 0.0030164
15 | 0.98249 | -0.33733 | 0 | 0
16 | 0.98718 | -0.24601 | 0 | 0
17 | 0.9853 | -0.28269 | 0.048116 | 0.012059
18 | 0.98731 | -0.24345 | 0 | 0
19 | 0.98605 | -0.2679 | 0.025849 | 0.0064783
20 | 0.98193 | -0.34829 | 0.01147 | 0.0028746
21 | 0.98803 | -0.22951 | 0 | 0
22 | 0.98831 | -0.22405 | 0 | 0
23 | 0.98787 | -0.23261 | 0.0073854 | 0.001851
24 | 0.98813 | -0.22754 | 0.0091822 | 0.0023013
25 | 0.99017 | -0.18823 | 0 | 0
26 | 0.99583 | -0.079384 | 0 | 0
27 | 0.99386 | -0.11721 | 0 | 0
28 | 0.99539 | -0.088001 | 0.0071781 | 0.001799
29 | 0.99353 | -0.12345 | 0 | 0
30 | 0.99336 | -0.12683 | 0.003502 | 0.00087767
31 | 0.99117 | -0.1689 | 0 | 0
32 | 0.99213 | -0.1503 | 0.0088343 | 0.0022141
33 | 0.98975 | -0.1963 | 0 | 0
34 | 0.98976 | -0.19612 | 0.0076917 | 0.0019277
35 | 0.9931 | -0.13186 | 0.0091386 | 0.0022904
36 | 0.99358 | -0.12301 | 0 | 0
37 | 0.99339 | -0.12666 | 0 | 0
38 | 0.99337 | -0.12695 | 0 | 0
39 | 0.99361 | -0.12226 | 0.0069293 | 0.0017366
40 | 0.99333 | -0.12776 | 0.0065162 | 0.0016331
41 | 0.99331 | -0.12815 | 0.0065133 | 0.0016324
42 | 0.99347 | -0.12461 | 0.0032162 | 0.00080606
43 | 0.99395 | -0.11576 | 0.0057941 | 0.0014521
44 | 0.98932 | -0.20459 | 0.0039406 | 0.00098761
45 | 0.98943 | -0.2026 | 0.0023077 | 0.00057837
46 | 0.99473 | -0.1006 | 0.0071826 | 0.0018001
47 | 0.98954 | -0.20033 | 0.011832 | 0.0029653
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013488 | -0.0033805 | 0.01349 | 0.0033813 | 1.5363e-06 | 8.5104e-07 | 0.020118 | 0.020118 | 0.020118 | 0.99765 | -0.044939 | 0.99777 | -0.042548 | 5.5269
1 | -0.019969 | -0.0050053 | 0.019975 | 0.0050088 | 5.8225e-06 | 3.4977e-06 | 0.029781 | 0.029781 | 0.029781 | 0.99777 | -0.042548 | 0.99809 | -0.03643 | 8.1817
2 | -0.026451 | -0.0066318 | 0.026458 | 0.0066361 | 6.9695e-06 | 4.3042e-06 | 0.039436 | 0.039436 | 0.039436 | 0.99809 | -0.03643 | 0.99838 | -0.030902 | 10.834
3 | -0.30893 | -0.078428 | 0.30939 | 0.078722 | 0.00046007 | 0.00029376 | 0.46079 | 0.46079 | 0.46079 | 0.99838 | -0.030902 | 1 | 0 | 42.1973
4 | 0.25571 | 0.065085 | -0.25517 | -0.064743 | 0.00053747 | 0.00034283 | 0.38148 | 0.38148 | 0.38148 | 0.99838 | -0.030902 | 0.99608 | -0.0746 | 34.9337
5 | 0.25517 | 0.064743 | -0.25512 | -0.064705 | 5.8701e-05 | 3.7443e-05 | 0.38148 | 0.38148 | 0.38148 | 0.99608 | -0.0746 | 0.99583 | -0.079384 | 34.9337
6 | -0.013083 | -0.0032789 | 0.013091 | 0.0032833 | 7.8207e-06 | 4.3318e-06 | 0.019812 | 0.019812 | 0.019812 | 0.98262 | -0.33483 | 0.98326 | -0.32229 | 5.4429
7 | -0.024555 | -0.0061565 | 0.024573 | 0.0061672 | 1.7357e-05 | 1.0683e-05 | 0.037162 | 0.037162 | 0.037162 | 0.98326 | -0.32229 | 0.98402 | -0.30746 | 10.2092
8 | 0.047534 | 0.011945 | -0.047473 | -0.011906 | 6.0938e-05 | 3.8602e-05 | 0.071891 | 0.071891 | 0.071891 | 0.98402 | -0.30746 | 0.98264 | -0.33436 | 19.7504
9 | -0.072107 | -0.018112 | 0.072146 | 0.018137 | 3.9361e-05 | 2.5079e-05 | 0.10905 | 0.10905 | 0.10905 | 0.98402 | -0.30746 | 0.98461 | -0.29603 | 29.9595
10 | 0.023519 | 0.0058993 | -0.023507 | -0.0058919 | 1.1925e-05 | 7.3148e-06 | 0.035617 | 0.035617 | 0.035617 | 0.98264 | -0.33436 | 0.9821 | -0.345 | 9.7848
11 | 0.023954 | 0.006007 | -0.023951 | -0.0060049 | 3.3934e-06 | 2.0847e-06 | 0.036275 | 0.036275 | 0.036275 | 0.98264 | -0.33436 | 0.98249 | -0.33733 | 9.9656
12 | -0.072146 | -0.018137 | 0.072243 | 0.018199 | 9.7062e-05 | 6.1843e-05 | 0.10905 | 0.10905 | 0.10905 | 0.98461 | -0.29603 | 0.98605 | -0.2679 | 29.9595
13 | -0.0082418 | -0.0020657 | 0.0082435 | 0.0020664 | 1.6356e-06 | 6.9286e-07 | 0.012488 | 0.012488 | 0.012488 | 0.98204 | -0.34615 | 0.98225 | -0.34199 | 3.4309
14 | 0.0082418 | 0.0020657 | -0.0082411 | -0.0020654 | 6.9858e-07 | 2.9598e-07 | 0.012488 | 0.012488 | 0.012488 | 0.98204 | -0.34615 | 0.98195 | -0.34793 | 3.4309
15 | -0.023945 | -0.0060016 | 0.023951 | 0.0060049 | 5.3106e-06 | 3.2625e-06 | 0.036275 | 0.036275 | 0.036275 | 0.98225 | -0.34199 | 0.98249 | -0.33733 | 9.9656
16 | 0.011471 | 0.0028755 | -0.01147 | -0.0028746 | 1.7993e-06 | 9.5064e-07 | 0.017381 | 0.017381 | 0.017381 | 0.9821 | -0.345 | 0.98193 | -0.34829 | 4.775
17 | 0.0482 | 0.012112 | -0.048116 | -0.012059 | 8.4227e-05 | 5.3362e-05 | 0.072665 | 0.072665 | 0.072665 | 0.98718 | -0.24601 | 0.9853 | -0.28269 | 19.963
18 | -0.0482 | -0.012112 | 0.048206 | 0.012116 | 5.8927e-06 | 3.7333e-06 | 0.072665 | 0.072665 | 0.072665 | 0.98718 | -0.24601 | 0.98731 | -0.24345 | 19.963
19 | -0.14641 | -0.036867 | 0.14651 | 0.036929 | 9.7661e-05 | 6.223e-05 | 0.22073 | 0.22073 | 0.22073 | 0.98731 | -0.24345 | 0.98803 | -0.22951 | 30.3194
20 | 0.098207 | 0.024751 | -0.098092 | -0.024677 | 0.00011472 | 7.3243e-05 | 0.14806 | 0.14806 | 0.14806 | 0.98731 | -0.24345 | 0.98605 | -0.2679 | 40.6758
21 | -0.1539 | -0.03878 | 0.15394 | 0.038806 | 4.0191e-05 | 2.5492e-05 | 0.23185 | 0.23185 | 0.23185 | 0.98803 | -0.22951 | 0.98831 | -0.22405 | 21.2316
22 | 0.0073865 | 0.0018514 | -0.0073854 | -0.001851 | 1.0908e-06 | 3.9714e-07 | 0.011124 | 0.011125 | 0.011125 | 0.98803 | -0.22951 | 0.98787 | -0.23261 | 3.0562
23 | 0.0091837 | 0.002302 | -0.0091822 | -0.0023013 | 1.524e-06 | 7.0301e-07 | 0.013827 | 0.013827 | 0.013827 | 0.98831 | -0.22405 | 0.98813 | -0.22754 | 3.7987
24 | -0.16312 | -0.041108 | 0.1634 | 0.041285 | 0.00028006 | 0.00017781 | 0.24568 | 0.24568 | 0.24568 | 0.98831 | -0.22405 | 0.99017 | -0.18823 | 22.4979
25 | 0.006253 | 0.0015669 | -0.0062506 | -0.0015663 | 2.4026e-06 | 6.0481e-07 | 0.0093969 | 0.0093972 | 0.0093972 | 0.99017 | -0.18823 | 0.98975 | -0.1963 | 2.5817
26 | 0.019533 | 0.0048987 | -0.019526 | -0.0048943 | 7.3378e-06 | 4.4042e-06 | 0.029356 | 0.029356 | 0.029356 | 0.99017 | -0.18823 | 0.98976 | -0.19612 | 8.0647
27 | -0.18919 | -0.047751 | 0.18936 | 0.047863 | 0.00017536 | 0.00011156 | 0.28443 | 0.28443 | 0.28443 | 0.99017 | -0.18823 | 0.99117 | -0.1689 | 26.0466
28 | 0.21494 | 0.054613 | -0.21455 | -0.054364 | 0.00039063 | 0.00024882 | 0.32143 | 0.32143 | 0.32143 | 0.99583 | -0.079384 | 0.99386 | -0.11721 | 29.4352
29 | 0.040178 | 0.010093 | -0.040162 | -0.010082 | 1.6514e-05 | 1.041e-05 | 0.060044 | 0.060044 | 0.060044 | 0.99583 | -0.079384 | 0.99539 | -0.088001 | 16.4956
30 | 0.2019 | 0.051192 | -0.20184 | -0.051153 | 6.0529e-05 | 3.8533e-05 | 0.30249 | 0.30249 | 0.30249 | 0.99386 | -0.11721 | 0.99353 | -0.12345 | 27.701
31 | 0.012649 | 0.0031722 | -0.012643 | -0.003169 | 5.7975e-06 | 3.1521e-06 | 0.018938 | 0.018939 | 0.018939 | 0.99386 | -0.11721 | 0.99336 | -0.12683 | 5.2029
32 | 0.032984 | 0.0082831 | -0.032964 | -0.0082707 | 1.9822e-05 | 1.2404e-05 | 0.049313 | 0.049314 | 0.049314 | 0.99539 | -0.088001 | 0.99473 | -0.1006 | 13.5477
33 | 0.19862 | 0.050347 | -0.19837 | -0.050184 | 0.00025599 | 0.00016294 | 0.29768 | 0.29768 | 0.29768 | 0.99353 | -0.12345 | 0.99213 | -0.1503 | 27.2599
34 | 0.0032164 | 0.00080591 | -0.0032162 | -0.00080606 | 1.7769e-07 | -1.507e-07 | 0.0048171 | 0.0048172 | 0.0048172 | 0.99353 | -0.12345 | 0.99347 | -0.12461 | 1.3234
35 | 0.0091408 | 0.0022914 | -0.0091386 | -0.0022904 | 2.1909e-06 | 9.989e-07 | 0.013693 | 0.013693 | 0.013693 | 0.99336 | -0.12683 | 0.9931 | -0.13186 | 3.7618
36 | -0.18936 | -0.047863 | 0.18953 | 0.04797 | 0.00016901 | 0.00010752 | 0.28443 | 0.28443 | 0.28443 | 0.99117 | -0.1689 | 0.99213 | -0.1503 | 26.0465
37 | 0.0062506 | 0.0015663 | -0.0062487 | -0.0015659 | 1.8757e-06 | 4.7277e-07 | 0.0093972 | 0.0093975 | 0.0093975 | 0.98975 | -0.1963 | 0.98943 | -0.2026 | 2.5817
38 | 0.011834 | 0.0029666 | -0.011832 | -0.0029653 | 2.3763e-06 | 1.2636e-06 | 0.017792 | 0.017792 | 0.017792 | 0.98976 | -0.19612 | 0.98954 | -0.20033 | 4.8879
39 | 0.0065149 | 0.0016328 | -0.0065138 | -0.0016325 | 1.133e-06 | 3.1417e-07 | 0.009757 | 0.0097571 | 0.0097571 | 0.99358 | -0.12301 | 0.99339 | -0.12666 | 2.6805
40 | 0.0065177 | 0.0016335 | -0.0065165 | -0.0016332 | 1.2241e-06 | 3.3982e-07 | 0.0097611 | 0.0097613 | 0.0097613 | 0.99358 | -0.12301 | 0.99337 | -0.12695 | 2.6817
41 | -0.013033 | -0.0032664 | 0.013033 | 0.0032666 | 4.6331e-07 | 2.5451e-07 | 0.019518 | 0.019518 | 0.019518 | 0.99358 | -0.12301 | 0.99361 | -0.12226 | 5.3621
42 | 0.0065138 | 0.0016325 | -0.0065133 | -0.0016324 | 4.6415e-07 | 1.2875e-07 | 0.0097571 | 0.0097572 | 0.0097572 | 0.99339 | -0.12666 | 0.99331 | -0.12815 | 2.6805
43 | 0.0065165 | 0.0016332 | -0.0065162 | -0.0016331 | 2.51e-07 | 6.9704e-08 | 0.0097613 | 0.0097613 | 0.0097613 | 0.99337 | -0.12695 | 0.99333 | -0.12776 | 2.6817
44 | -0.019962 | -0.0050033 | 0.019969 | 0.005007 | 6.1813e-06 | 3.717e-06 | 0.029895 | 0.029895 | 0.029895 | 0.99361 | -0.12226 | 0.99395 | -0.11576 | 8.213
45 | -0.025763 | -0.0064591 | 0.025781 | 0.0064706 | 1.8623e-05 | 1.1486e-05 | 0.038569 | 0.038569 | 0.038569 | 0.99395 | -0.11576 | 0.99473 | -0.1006 | 10.596
46 | -0.0039406 | -0.00098761 | 0.003941 | 0.00098749 | 3.7345e-07 | -1.2505e-07 | 0.005927 | 0.0059269 | 0.005927 | 0.98932 | -0.20459 | 0.98943 | -0.2026 | 1.6283

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32408 | 0.08199

## res_load
| p_mw | q_mvar
0 | 0.013488 | 0.0033805
1 | 0.0064797 | 0.001624
2 | 0.0064758 | 0.001623
3 | 0.02676 | 0.0067066
4 | 0.013038 | 0.0032676
5 | 0.013083 | 0.0032789
6 | 0.011464 | 0.0028733
7 | 0.015702 | 0.0039352
8 | 0.0082411 | 0.0020654
9 | 0.012036 | 0.0030164
10 | 0.048116 | 0.012059
11 | 0.025849 | 0.0064783
12 | 0.01147 | 0.0028746
13 | 0.0073854 | 0.001851
14 | 0.0091822 | 0.0023013
15 | 0.0071781 | 0.001799
16 | 0.003502 | 0.00087767
17 | 0.0088343 | 0.0022141
18 | 0.0076917 | 0.0019277
19 | 0.0091386 | 0.0022904
20 | 0.0069293 | 0.0017366
21 | 0.0065162 | 0.0016331
22 | 0.0065133 | 0.0016324
23 | 0.0032162 | 0.00080606
24 | 0.0057941 | 0.0014521
25 | 0.0039406 | 0.00098761
26 | 0.0023077 | 0.00057837
27 | 0.0071826 | 0.0018001
28 | 0.011832 | 0.0029653

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1