## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-43_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-43_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1059-43_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1059-43_0_4_node_45 | 0.4 | n |  | TRUE
4 | bus_LV_1059-43_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1059-43_0_4_node_94 | 0.4 | n |  | TRUE
6 | bus_LV_1059-43_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1059-43_0_4_node_83 | 0.4 | n |  | TRUE
8 | bus_LV_1059-43_0_4_node_81 | 0.4 | n |  | TRUE
9 | bus_LV_1059-43_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1059-43_0_4_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1059-43_0_4_node_38 | 0.4 | n |  | TRUE
12 | bus_LV_1059-43_0_4_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_1059-43_0_4_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_1059-43_0_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_1059-43_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1059-43_0_4_node_36 | 0.4 | n |  | TRUE
17 | bus_LV_1059-43_0_4_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_1059-43_0_4_node_96 | 0.4 | n |  | TRUE
19 | bus_LV_1059-43_0_4_node_65 | 0.4 | n |  | TRUE
20 | bus_LV_1059-43_0_4_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_1059-43_0_4_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_1059-43_0_4_node_110 | 0.4 | n |  | TRUE
23 | bus_LV_1059-43_0_4_node_76 | 0.4 | n |  | TRUE
24 | bus_LV_1059-43_0_4_node_70 | 0.4 | n |  | TRUE
25 | bus_LV_1059-43_0_4_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_1059-43_0_4_node_61 | 0.4 | n |  | TRUE
27 | bus_LV_1059-43_0_4_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_1059-43_0_4_node_62 | 0.4 | n |  | TRUE
29 | bus_LV_1059-43_0_4_node_60 | 0.4 | n |  | TRUE
30 | bus_LV_1059-43_0_4_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_1059-43_0_4_node_75 | 0.4 | n |  | TRUE
32 | bus_LV_1059-43_0_4_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_1059-43_0_4_node_71 | 0.4 | n |  | TRUE
34 | bus_LV_1059-43_0_4_node_82 | 0.4 | n |  | TRUE
35 | bus_LV_1059-43_0_4_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_1059-43_0_4_node_67 | 0.4 | n |  | TRUE
37 | bus_LV_1059-43_0_4_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_1059-43_0_4_node_88 | 0.4 | n |  | TRUE
39 | bus_LV_1059-43_0_4_node_89 | 0.4 | n |  | TRUE
40 | bus_LV_1059-43_0_4_node_86 | 0.4 | n |  | TRUE
41 | bus_LV_1059-43_0_4_node_77 | 0.4 | n |  | TRUE
42 | bus_LV_1059-43_0_4_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_1059-43_0_4_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_1059-43_0_4_node_78 | 0.4 | n |  | TRUE
45 | bus_LV_1059-43_0_4_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_1059-43_0_4_node_87 | 0.4 | n |  | TRUE
47 | bus_LV_1059-43_0_4_node_79 | 0.4 | n |  | TRUE
48 | bus_LV_1059-43_0_4_node_80 | 0.4 | n |  | TRUE
49 | bus_LV_1059-43_0_4_node_74 | 0.4 | n |  | TRUE
50 | bus_LV_1059-43_0_4_node_85 | 0.4 | n |  | TRUE
51 | bus_LV_1059-43_0_4_node_95 | 0.4 | n |  | TRUE
52 | bus_MV_23_0_node_159 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-43_0_4_load_0 | 0 | 0.0076409 | 0.001915 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-43_0_4_load_94 | 5 | 0.011529 | 0.0028895 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-43_0_4_load_81 | 8 | 0.00050212 | 0.00012584 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-43_0_4_load_49 | 12 | 0.072943 | 0.018281 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-43_0_4_load_90 | 17 | 0.018051 | 0.0045241 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-43_0_4_load_96 | 18 | 0.014077 | 0.0035281 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-43_0_4_load_110 | 22 | 0.026137 | 0.0065505 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-43_0_4_load_70 | 24 | 0.0096612 | 0.0024213 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-43_0_4_load_61 | 26 | 0.0015036 | 0.00037684 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-43_0_4_load_62 | 28 | 0.015966 | 0.0040014 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-43_0_4_load_60 | 29 | 0.036896 | 0.009247 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1059-43_0_4_load_72 | 30 | 0.00031444 | 7.8805e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1059-43_0_4_load_71 | 33 | 0.0049614 | 0.0012434 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1059-43_0_4_load_69 | 35 | 0.01115 | 0.0027944 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1059-43_0_4_load_67 | 36 | 0.0023421 | 0.00058699 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1059-43_0_4_load_63 | 37 | 0.0044482 | 0.0011148 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1059-43_0_4_load_88 | 38 | 0.00015257 | 3.8239e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1059-43_0_4_load_89 | 39 | 0.00038519 | 9.6539e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1059-43_0_4_load_86 | 40 | 0.021414 | 0.0053669 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1059-43_0_4_load_77 | 41 | 0.013114 | 0.0032866 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1059-43_0_4_load_73 | 42 | 0.0029293 | 0.00073415 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1059-43_0_4_load_64 | 43 | 0.0023232 | 0.00058226 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1059-43_0_4_load_87 | 46 | 0.0046171 | 0.0011571 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1059-43_0_4_load_79 | 47 | 0.0045835 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1059-43_0_4_load_80 | 48 | 0.0025839 | 0.0006476 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1059-43_0_4_load_74 | 49 | 0.024971 | 0.0062584 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1059-43_0_4_load_85 | 50 | 0.019855 | 0.004976 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1059-43_0_4_load_95 | 51 | 0.0014979 | 0.00037541 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-43_0_4_line_0 |  | 0 | 1 | 0.052277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1059-43_0_4_line_1 |  | 1 | 2 | 0.032069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1059-43_0_4_line_2 |  | 1 | 3 | 0.058404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1059-43_0_4_line_3 |  | 2 | 4 | 0.020435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_1059-43_0_4_line_4 |  | 2 | 5 | 0.0096133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1059-43_0_4_line_5 |  | 3 | 30 | 0.0025358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1059-43_0_4_line_6 |  | 3 | 31 | 0.043177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1059-43_0_4_line_7 |  | 4 | 6 | 0.098273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1059-43_0_4_line_8 |  | 6 | 7 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1059-43_0_4_line_9 |  | 6 | 8 | 0.065919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1059-43_0_4_line_10 |  | 7 | 28 | 0.057634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1059-43_0_4_line_11 |  | 8 | 34 | 0.069534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1059-43_0_4_line_12 |  | 9 | 10 | 0.014293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1059-43_0_4_line_13 |  | 9 | 11 | 0.05012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1059-43_0_4_line_14 |  | 9 | 12 | 0.034498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1059-43_0_4_line_15 |  | 10 | 13 | 0.013866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1059-43_0_4_line_16 |  | 11 | 19 | 0.011073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1059-43_0_4_line_17 |  | 12 | 14 | 0.020242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1059-43_0_4_line_18 |  | 13 | 17 | 0.022469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1059-43_0_4_line_19 |  | 14 | 15 | 0.065301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1059-43_0_4_line_20 |  | 15 | 16 | 0.071513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1059-43_0_4_line_21 |  | 16 | 18 | 0.021974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1059-43_0_4_line_22 |  | 19 | 36 | 0.068565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1059-43_0_4_line_23 |  | 19 | 37 | 0.041638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1059-43_0_4_line_24 |  | 20 | 21 | 0.15495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1059-43_0_4_line_25 |  | 20 | 22 | 0.043705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1059-43_0_4_line_26 |  | 21 | 23 | 0.006914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1059-43_0_4_line_27 |  | 21 | 24 | 0.022692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1059-43_0_4_line_28 |  | 23 | 40 | 0.012991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1059-43_0_4_line_29 |  | 24 | 35 | 0.041252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1059-43_0_4_line_30 |  | 25 | 26 | 0.038777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1059-43_0_4_line_31 |  | 26 | 29 | 0.0085733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1059-43_0_4_line_32 |  | 27 | 28 | 0.012373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1059-43_0_4_line_33 |  | 27 | 29 | 0.047979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1059-43_0_4_line_34 |  | 30 | 32 | 0.023695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1059-43_0_4_line_35 |  | 31 | 41 | 0.0024676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1059-43_0_4_line_36 |  | 31 | 42 | 0.019204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1059-43_0_4_line_37 |  | 32 | 33 | 0.037212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1059-43_0_4_line_38 |  | 34 | 45 | 0.00545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1059-43_0_4_line_39 |  | 36 | 44 | 0.044557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1059-43_0_4_line_40 |  | 37 | 43 | 0.02782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1059-43_0_4_line_41 |  | 38 | 39 | 0.029781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1059-43_0_4_line_42 |  | 39 | 45 | 0.070193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1059-43_0_4_line_43 |  | 40 | 50 | 0.026863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_1059-43_0_4_line_44 |  | 41 | 50 | 0.021988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_1059-43_0_4_line_45 |  | 42 | 49 | 0.049835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1059-43_0_4_line_46 |  | 44 | 47 | 0.016618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1059-43_0_4_line_47 |  | 44 | 48 | 0.021157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1059-43_0_4_line_48 |  | 45 | 46 | 0.024983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1059-43_0_4_line_49 |  | 46 | 47 | 0.031577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1059-43_0_4_line_50 |  | 48 | 51 | 0.024984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-43_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 52 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2665279.9536 | 1209080.3697 | 2665275.5357 | 1209084.6462 | 2665273.7686 | 1209086.3502 | 2665269.536 | 1209084.8141 | 2665266.3751 | 1209085.3687 | 2665260.4205 | 1209089.7508 | 2665257.1654 | 1209094.7516 | 2665249.9906 | 1209105.7465 | 2665244.9364 | 1209113.7577
1 | 2665279.9536 | 1209080.3697 | 2665283.4677 | 1209076.717 | 2665284.6517 | 1209075.4959 | 2665282.5733 | 1209073.005 | 2665280.2625 | 1209069.5109 | 2665279.5365 | 1209067.0792 | 2665279.0856 | 1209062.4381 | 2665279.3189 | 1209059.172 | 2665280.6287 | 1209054.1055 | 2665281.4111 | 1209052.0795
2 | 2665279.9536 | 1209080.3697 | 2665285.2563 | 1209084.8526 | 2665303.4374 | 1209099.6828 | 2665313.457 | 1209108.6868 | 2665324.2594 | 1209118.3998
3 | 2665269.5266 | 1209039.8087 | 2665267.3998 | 1209042.4315 | 2665268.3719 | 1209043.2092 | 2665274.1443 | 1209047.8419 | 2665278.4953 | 1209050.3799 | 2665281.4111 | 1209052.0795
4 | 2665281.4111 | 1209052.0795 | 2665283.7185 | 1209046.1566 | 2665285.3695 | 1209043.3492
5 | 2665324.2594 | 1209118.3998 | 2665326.1434 | 1209120.0971
6 | 2665353.3071 | 1209086.3871 | 2665327.2295 | 1209115.1303 | 2665326.6986 | 1209115.7137 | 2665324.2594 | 1209118.3998
7 | 2665187.3938 | 1208986.3342 | 2665196.7734 | 1208989.2384 | 2665230.3992 | 1209011.9974 | 2665256.4679 | 1209030.6381 | 2665264.6155 | 1209035.6636 | 2665269.5266 | 1209039.8087
8 | 2665196.149 | 1208971.2428 | 2665189.0993 | 1208981.2163 | 2665187.3938 | 1208986.3342
9 | 2665187.3938 | 1208986.3342 | 2665169.4025 | 1208983.9919 | 2665153.6046 | 1208982.6742 | 2665122.8416 | 1208974.1473
10 | 2665196.149 | 1208971.2428 | 2665212.1938 | 1208948.582 | 2665213.7727 | 1208946.0088 | 2665227.7812 | 1208923.104
11 | 2665056.2126 | 1208954.2948 | 2665069.9079 | 1208958.113 | 2665106.2124 | 1208969.538 | 2665122.8416 | 1208974.1473
12 | 2665253.2107 | 1208817.5724 | 2665255.016 | 1208813.0783 | 2665251.4827 | 1208810.8272 | 2665253.8516 | 1208806.9285 | 2665254.2155 | 1208806.3321
13 | 2665207.1382 | 1208827.564 | 2665216.599 | 1208822.3642 | 2665223.8747 | 1208818.1633 | 2665229.4533 | 1208815.5115 | 2665235.0131 | 1208813.8935 | 2665239.3658 | 1208813.5075 | 2665243.8769 | 1208813.9348 | 2665246.8565 | 1208814.6678 | 2665248.6492 | 1208815.4991 | 2665253.2107 | 1208817.5724
14 | 2665253.2107 | 1208817.5724 | 2665250.8191 | 1208823.5388 | 2665270.0078 | 1208844.0256
15 | 2665243.5987 | 1208807.3945 | 2665247.0205 | 1208808.7104 | 2665251.4827 | 1208810.8272 | 2665253.8516 | 1208806.9285 | 2665254.2155 | 1208806.3321
16 | 2665196.675 | 1208831.2742 | 2665207.1382 | 1208827.564
17 | 2665283.8452 | 1208858.7992 | 2665270.0078 | 1208844.0256
18 | 2665243.5987 | 1208807.3945 | 2665244.9948 | 1208802.7736 | 2665247.0522 | 1208796.0809 | 2665249.8953 | 1208791.2312 | 2665253.3178 | 1208787.5608
19 | 2665283.8452 | 1208858.7992 | 2665286.867 | 1208861.9341 | 2665295.9499 | 1208847.5024 | 2665297.7525 | 1208844.6426 | 2665299.7409 | 1208841.4846 | 2665324.0801 | 1208856.3489 | 2665328.2256 | 1208849.201
20 | 2665328.2256 | 1208849.201 | 2665335.1212 | 1208851.9448 | 2665337.0881 | 1208855.6019 | 2665339.1857 | 1208857.7373 | 2665348.1622 | 1208862.0604 | 2665357.5926 | 1208865.8882 | 2665357.2885 | 1208866.5853 | 2665354.8254 | 1208872.1395 | 2665351.9566 | 1208878.6342 | 2665351.5668 | 1208879.5194 | 2665354.9562 | 1208882.4027 | 2665356.9279 | 1208885.6263 | 2665357.8675 | 1208889.3722 | 2665357.6641 | 1208892.672 | 2665355.6048 | 1208898.8421
21 | 2665355.6048 | 1208898.8421 | 2665350.9181 | 1208908.2076 | 2665345.2706 | 1208918.2266
22 | 2665196.675 | 1208831.2742 | 2665196.9669 | 1208833.0896 | 2665196.5955 | 1208837.1547 | 2665191.8794 | 1208842.9734 | 2665150.9443 | 1208879.9372
23 | 2665196.675 | 1208831.2742 | 2665189.4555 | 1208833.8191 | 2665186.0786 | 1208834.6494 | 2665179.2682 | 1208835.9314 | 2665172.1433 | 1208836.0759 | 2665155.6944 | 1208836.0764
24 | 2665395.7584 | 1209030.7068 | 2665399.3967 | 1209029.6015 | 2665415.9219 | 1209003.3888 | 2665431.6815 | 1208978.3796 | 2665441.7606 | 1208962.5582 | 2665447.3175 | 1208966.0434 | 2665502.6451 | 1209000.6936
25 | 2665471.1133 | 1209031.0441 | 2665502.6451 | 1209000.6936
26 | 2665395.7584 | 1209030.7068 | 2665390.4191 | 1209035.1177
27 | 2665395.7584 | 1209030.7068 | 2665392.8835 | 1209023.8934 | 2665401.0376 | 1209010.9509
28 | 2665390.4191 | 1209035.1177 | 2665382.5192 | 1209039.4116 | 2665380.4073 | 1209042.8076
29 | 2665423.0271 | 1208976.0481 | 2665401.0376 | 1209010.9509
30 | 2665304.0882 | 1208970.7778 | 2665304.9055 | 1208961.3921 | 2665304.2203 | 1208958.7052 | 2665293.3428 | 1208951.6597 | 2665281.8308 | 1208944.3747
31 | 2665281.8308 | 1208944.3747 | 2665274.5862 | 1208939.7902
32 | 2665234.7963 | 1208912.985 | 2665232.5975 | 1208915.229 | 2665227.7812 | 1208923.104
33 | 2665234.7963 | 1208912.985 | 2665249.5715 | 1208923.0192 | 2665270.3159 | 1208937.0879 | 2665274.5862 | 1208939.7902
34 | 2665343.7483 | 1209135.9572 | 2665326.1434 | 1209120.0971
35 | 2665353.3071 | 1209086.3871 | 2665354.6102 | 1209084.2916
36 | 2665353.3071 | 1209086.3871 | 2665369.2875 | 1209097.0362
37 | 2665343.7483 | 1209135.9572 | 2665347.1154 | 1209145.0329 | 2665346.0186 | 1209154.2487 | 2665338.4046 | 1209170.8359
38 | 2665055.7625 | 1208948.8643 | 2665056.2126 | 1208954.2948
39 | 2665116.6572 | 1208908.2812 | 2665123.5647 | 1208903.6649 | 2665133.6029 | 1208895.7028 | 2665146.0652 | 1208884.343 | 2665150.9443 | 1208879.9372
40 | 2665155.6944 | 1208836.0764 | 2665152.8489 | 1208836.0765 | 2665127.8811 | 1208835.4793
41 | 2665139.1292 | 1208895.7194 | 2665136.0221 | 1208898.3308 | 2665120.1773 | 1208910.3431 | 2665115.4154 | 1208913.7221
42 | 2665055.7625 | 1208948.8643 | 2665071.9591 | 1208944.994 | 2665092.7876 | 1208929.7785 | 2665115.4154 | 1208913.7221
43 | 2665366.2216 | 1209065.6195 | 2665380.4073 | 1209042.8076
44 | 2665366.2216 | 1209065.6195 | 2665354.6102 | 1209084.2916
45 | 2665369.2875 | 1209097.0362 | 2665382.4151 | 1209105.7843 | 2665401.1244 | 1209077.3232
46 | 2665116.6572 | 1208908.2812 | 2665103.6308 | 1208917 | 2665102.8454 | 1208917.5229
47 | 2665116.6572 | 1208908.2812 | 2665104.5743 | 1208890.9141
48 | 2665055.7625 | 1208948.8643 | 2665076.5593 | 1208935.0206
49 | 2665102.8454 | 1208917.5229 | 2665076.5593 | 1208935.0206
50 | 2665104.5743 | 1208890.9141 | 2665095.7373 | 1208878.2125 | 2665090.1558 | 1208870.5123

## bus_geodata
| x | y | coords
0 | 2665244.9364 | 1209113.7577
1 | 2665279.9536 | 1209080.3697
2 | 2665281.4111 | 1209052.0795
3 | 2665324.2594 | 1209118.3998
4 | 2665269.5266 | 1209039.8087
5 | 2665285.3695 | 1209043.3492
6 | 2665187.3938 | 1208986.3342
7 | 2665196.149 | 1208971.2428
8 | 2665122.8416 | 1208974.1473
9 | 2665253.2107 | 1208817.5724
10 | 2665254.2155 | 1208806.3321
11 | 2665207.1382 | 1208827.564
12 | 2665270.0078 | 1208844.0256
13 | 2665243.5987 | 1208807.3945
14 | 2665283.8452 | 1208858.7992
15 | 2665328.2256 | 1208849.201
16 | 2665355.6048 | 1208898.8421
17 | 2665253.3178 | 1208787.5608
18 | 2665345.2706 | 1208918.2265
19 | 2665196.675 | 1208831.2742
20 | 2665502.6451 | 1209000.6936
21 | 2665395.7584 | 1209030.7068
22 | 2665471.1133 | 1209031.0441
23 | 2665390.4191 | 1209035.1177
24 | 2665401.0376 | 1209010.9509
25 | 2665304.0882 | 1208970.7778
26 | 2665281.8308 | 1208944.3747
27 | 2665234.7963 | 1208912.985
28 | 2665227.7812 | 1208923.104
29 | 2665274.5862 | 1208939.7902
30 | 2665326.1434 | 1209120.0971
31 | 2665353.3071 | 1209086.3871
32 | 2665343.7483 | 1209135.9572
33 | 2665338.4046 | 1209170.8359
34 | 2665056.2126 | 1208954.2948
35 | 2665423.0271 | 1208976.0481
36 | 2665150.9443 | 1208879.9372
37 | 2665155.6944 | 1208836.0764
38 | 2665139.1292 | 1208895.7194
39 | 2665115.4154 | 1208913.7221
40 | 2665380.4073 | 1209042.8076
41 | 2665354.6102 | 1209084.2916
42 | 2665369.2875 | 1209097.0362
43 | 2665127.8811 | 1208835.4793
44 | 2665116.6572 | 1208908.2812
45 | 2665055.7625 | 1208948.8643
46 | 2665076.5593 | 1208935.0206
47 | 2665102.8454 | 1208917.5229
48 | 2665104.5743 | 1208890.9141
49 | 2665401.1244 | 1209077.3232
50 | 2665366.2216 | 1209065.6195
51 | 2665090.1558 | 1208870.5123
52 | 2665234.7963 | 1208912.985

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98152 | -0.35327 | 0.0076409 | 0.001915
1 | 0.98188 | -0.34604 | 0 | 0
2 | 0.98294 | -0.32546 | 0 | 0
3 | 0.98006 | -0.38162 | 0 | 0
4 | 0.98367 | -0.3113 | 0 | 0
5 | 0.98284 | -0.32745 | 0.011529 | 0.0028895
6 | 0.98718 | -0.24351 | 0 | 0
7 | 0.98833 | -0.22133 | 0 | 0
8 | 0.98521 | -0.28148 | 0.00050212 | 0.00012584
9 | 0.97516 | -0.47691 | 0 | 0
10 | 0.97504 | -0.47928 | 0 | 0
11 | 0.97762 | -0.42877 | 0 | 0
12 | 0.97236 | -0.5321 | 0.072943 | 0.018281
13 | 0.97481 | -0.48387 | 0 | 0
14 | 0.9721 | -0.53735 | 0 | 0
15 | 0.97124 | -0.55433 | 0 | 0
16 | 0.9703 | -0.57295 | 0 | 0
17 | 0.97443 | -0.49131 | 0.018051 | 0.0045241
18 | 0.97001 | -0.57868 | 0.014077 | 0.0035281
19 | 0.97789 | -0.42346 | 0 | 0
20 | 0.9723 | -0.534 | 0 | 0
21 | 0.97608 | -0.45961 | 0 | 0
22 | 0.97123 | -0.55508 | 0.026137 | 0.0065505
23 | 0.97638 | -0.45367 | 0 | 0
24 | 0.97564 | -0.46825 | 0.0096612 | 0.0024213
25 | 1 | 0 | -0.34494 | -0.088605
26 | 0.99697 | -0.057062 | 0.0015036 | 0.00037684
27 | 0.99298 | -0.1327 | 0 | 0
28 | 0.99212 | -0.14902 | 0.015966 | 0.0040014
29 | 0.9963 | -0.069668 | 0.036896 | 0.009247
30 | 0.98005 | -0.38186 | 0.00031444 | 7.8805e-05
31 | 0.97876 | -0.40697 | 0 | 0
32 | 0.97994 | -0.384 | 0 | 0
33 | 0.97977 | -0.38735 | 0.0049614 | 0.0012434
34 | 0.98313 | -0.32154 | 0 | 0
35 | 0.97521 | -0.47668 | 0.01115 | 0.0027944
36 | 0.97968 | -0.38858 | 0.0023421 | 0.00058699
37 | 0.97763 | -0.42861 | 0.0044482 | 0.0011148
38 | 0.98293 | -0.32545 | 0.00015257 | 3.8239e-05
39 | 0.98293 | -0.32537 | 0.00038519 | 9.6539e-05
40 | 0.97695 | -0.44253 | 0.021414 | 0.0053669
41 | 0.97871 | -0.40811 | 0.013114 | 0.0032866
42 | 0.97827 | -0.41672 | 0.0029293 | 0.00073415
43 | 0.97757 | -0.42978 | 0.0023232 | 0.00058226
44 | 0.98087 | -0.3655 | 0 | 0
45 | 0.98297 | -0.32468 | 0 | 0
46 | 0.98223 | -0.33906 | 0.0046171 | 0.0011571
47 | 0.98132 | -0.3566 | 0.0045835 | 0.0011487
48 | 0.98079 | -0.36707 | 0.0025839 | 0.0006476
49 | 0.97711 | -0.43941 | 0.024971 | 0.0062584
50 | 0.9778 | -0.42577 | 0.019855 | 0.004976
51 | 0.98075 | -0.36775 | 0.0014979 | 0.00037541
52 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0076409 | -0.001915 | 0.0076435 | 0.001916 | 2.6305e-06 | 1.0225e-06 | 0.011584 | 0.011584 | 0.011584 | 0.98152 | -0.35327 | 0.98188 | -0.34604 | 3.1824
1 | -0.14288 | -0.036085 | 0.14303 | 0.036174 | 0.0001411 | 8.8678e-05 | 0.21664 | 0.21664 | 0.21664 | 0.98188 | -0.34604 | 0.98294 | -0.32546 | 14.8789
2 | 0.13524 | 0.034169 | -0.13501 | -0.034025 | 0.00023022 | 0.00014439 | 0.20505 | 0.20505 | 0.20505 | 0.98188 | -0.34604 | 0.98006 | -0.38162 | 14.0834
3 | -0.15456 | -0.039064 | 0.15466 | 0.03913 | 0.00010498 | 6.6153e-05 | 0.23409 | 0.23409 | 0.23409 | 0.98294 | -0.32546 | 0.98367 | -0.3113 | 16.0777
4 | 0.011531 | 0.0028901 | -0.011529 | -0.0028895 | 1.0984e-06 | 5.8115e-07 | 0.017455 | 0.017455 | 0.017455 | 0.98294 | -0.32546 | 0.98284 | -0.32745 | 4.7955
5 | 0.0052772 | 0.0013223 | -0.0052771 | -0.0013223 | 6.1045e-08 | 7.1147e-09 | 0.0080122 | 0.0080122 | 0.0080122 | 0.98006 | -0.38162 | 0.98005 | -0.38186 | 2.2012
6 | 0.12973 | 0.032703 | -0.12958 | -0.032604 | 0.00015716 | 9.8409e-05 | 0.19704 | 0.19704 | 0.19704 | 0.98006 | -0.38162 | 0.97876 | -0.40697 | 13.5331
7 | -0.15466 | -0.03913 | 0.15517 | 0.039448 | 0.00050486 | 0.0003181 | 0.23409 | 0.23409 | 0.23409 | 0.98367 | -0.3113 | 0.98718 | -0.24351 | 16.0777
8 | -0.28529 | -0.072662 | 0.28559 | 0.072857 | 0.00030567 | 0.00019473 | 0.43044 | 0.43044 | 0.43044 | 0.98718 | -0.24351 | 0.98833 | -0.22133 | 29.5632
9 | 0.13012 | 0.033214 | -0.12988 | -0.033065 | 0.00023826 | 0.00014912 | 0.19635 | 0.19635 | 0.19635 | 0.98718 | -0.24351 | 0.98521 | -0.28148 | 13.4857
10 | -0.28559 | -0.072857 | 0.28659 | 0.073495 | 0.0010011 | 0.00063773 | 0.43044 | 0.43044 | 0.43044 | 0.98833 | -0.22133 | 0.99212 | -0.14902 | 29.5631
11 | 0.12938 | 0.032939 | -0.12913 | -0.032783 | 0.00024939 | 0.00015607 | 0.19559 | 0.19559 | 0.19559 | 0.98521 | -0.28148 | 0.98313 | -0.32154 | 13.4337
12 | 0.018064 | 0.0045312 | -0.018062 | -0.0045302 | 2.0363e-06 | 9.4665e-07 | 0.027565 | 0.027565 | 0.027565 | 0.97516 | -0.47691 | 0.97504 | -0.47928 | 3.7864
13 | -0.10534 | -0.026505 | 0.10559 | 0.026659 | 0.00024294 | 0.00015423 | 0.16078 | 0.16078 | 0.16078 | 0.97516 | -0.47691 | 0.97762 | -0.42877 | 22.0857
14 | 0.087281 | 0.021974 | -0.087052 | -0.021827 | 0.00022959 | 0.00014651 | 0.13322 | 0.13322 | 0.13322 | 0.97516 | -0.47691 | 0.97236 | -0.5321 | 36.5987
15 | 0.018062 | 0.0045302 | -0.018058 | -0.0045279 | 3.9508e-06 | 2.3556e-06 | 0.027565 | 0.027565 | 0.027565 | 0.97504 | -0.47928 | 0.97481 | -0.48387 | 7.5728
16 | -0.10559 | -0.026659 | 0.10561 | 0.026676 | 2.6836e-05 | 1.662e-05 | 0.16078 | 0.16078 | 0.16078 | 0.97762 | -0.42877 | 0.97789 | -0.42346 | 11.0428
17 | 0.014109 | 0.0035459 | -0.014105 | -0.0035439 | 3.5396e-06 | 2.0143e-06 | 0.021594 | 0.021594 | 0.021594 | 0.97236 | -0.5321 | 0.9721 | -0.53735 | 5.9325
18 | 0.018058 | 0.0045279 | -0.018051 | -0.0045241 | 6.4023e-06 | 3.8175e-06 | 0.027565 | 0.027565 | 0.027565 | 0.97481 | -0.48387 | 0.97443 | -0.49131 | 7.5729
19 | 0.014105 | 0.0035439 | -0.014094 | -0.0035374 | 1.1419e-05 | 6.4993e-06 | 0.021594 | 0.021594 | 0.021594 | 0.9721 | -0.53735 | 0.97124 | -0.55433 | 5.9326
20 | 0.014094 | 0.0035374 | -0.014081 | -0.0035303 | 1.2506e-05 | 7.1195e-06 | 0.021594 | 0.021595 | 0.021595 | 0.97124 | -0.55433 | 0.9703 | -0.57295 | 5.9326
21 | 0.014081 | 0.0035303 | -0.014077 | -0.0035281 | 3.8427e-06 | 2.188e-06 | 0.021595 | 0.021595 | 0.021595 | 0.9703 | -0.57295 | 0.97001 | -0.57868 | 5.9327
22 | -0.11239 | -0.028373 | 0.11258 | 0.02849 | 0.00018816 | 0.00011697 | 0.17109 | 0.17109 | 0.17109 | 0.97789 | -0.42346 | 0.97968 | -0.38858 | 11.7507
23 | 0.0067732 | 0.0016974 | -0.0067716 | -0.0016968 | 1.6586e-06 | 5.3928e-07 | 0.010306 | 0.010307 | 0.010307 | 0.97789 | -0.42346 | 0.97763 | -0.42861 | 2.8315
24 | -0.026163 | -0.0065668 | 0.026256 | 0.0066245 | 9.3173e-05 | 5.7702e-05 | 0.040044 | 0.040043 | 0.040044 | 0.9723 | -0.534 | 0.97608 | -0.45961 | 11.0011
25 | 0.026163 | 0.0065668 | -0.026137 | -0.0065505 | 2.6281e-05 | 1.6278e-05 | 0.040044 | 0.040044 | 0.040044 | 0.9723 | -0.534 | 0.97123 | -0.55508 | 11.0011
26 | -0.04708 | -0.011848 | 0.047094 | 0.011856 | 1.3363e-05 | 8.4657e-06 | 0.071791 | 0.071791 | 0.071791 | 0.97608 | -0.45961 | 0.97638 | -0.45367 | 19.7227
27 | 0.020824 | 0.0052233 | -0.020815 | -0.0052181 | 8.5767e-06 | 5.2056e-06 | 0.031747 | 0.031747 | 0.031747 | 0.97608 | -0.45961 | 0.97564 | -0.46825 | 8.7218
28 | -0.047094 | -0.011856 | 0.047119 | 0.011872 | 2.5107e-05 | 1.5906e-05 | 0.071791 | 0.071791 | 0.071791 | 0.97638 | -0.45367 | 0.97695 | -0.44253 | 19.7227
29 | 0.011154 | 0.0027967 | -0.01115 | -0.0027944 | 4.4773e-06 | 2.3506e-06 | 0.017012 | 0.017013 | 0.017013 | 0.97564 | -0.46825 | 0.97521 | -0.47668 | 4.6738
30 | 0.34329 | 0.088605 | -0.34233 | -0.087998 | 0.00095199 | 0.00060725 | 0.51173 | 0.51173 | 0.51173 | 1 | 0 | 0.99697 | -0.057062 | 35.1464
31 | 0.34083 | 0.087621 | -0.34062 | -0.087488 | 0.00020864 | 0.00013308 | 0.50949 | 0.50949 | 0.50949 | 0.99697 | -0.057062 | 0.9963 | -0.069668 | 34.9923
32 | 0.3028 | 0.077649 | -0.30256 | -0.077496 | 0.00023949 | 0.00015263 | 0.45438 | 0.45438 | 0.45438 | 0.99298 | -0.1327 | 0.99212 | -0.14902 | 31.2077
33 | -0.3028 | -0.077649 | 0.30373 | 0.078241 | 0.00092868 | 0.00059187 | 0.45438 | 0.45438 | 0.45438 | 0.99298 | -0.1327 | 0.9963 | -0.069668 | 31.2077
34 | 0.0049627 | 0.0012435 | -0.0049622 | -0.0012435 | 5.0448e-07 | 2.4314e-08 | 0.0075348 | 0.0075349 | 0.0075349 | 0.98005 | -0.38186 | 0.97994 | -0.384 | 2.07
35 | 0.10164 | 0.025587 | -0.10163 | -0.025583 | 5.5263e-06 | 3.4128e-06 | 0.15456 | 0.15456 | 0.15456 | 0.97876 | -0.40697 | 0.97871 | -0.40811 | 10.6153
36 | 0.027941 | 0.0070173 | -0.027928 | -0.0070092 | 1.2997e-05 | 8.0771e-06 | 0.042484 | 0.042484 | 0.042484 | 0.97876 | -0.40697 | 0.97827 | -0.41672 | 11.6713
37 | 0.0049622 | 0.0012435 | -0.0049614 | -0.0012434 | 7.9228e-07 | 3.8336e-08 | 0.0075349 | 0.0075351 | 0.0075351 | 0.97994 | -0.384 | 0.97977 | -0.38735 | 2.0701
38 | 0.12913 | 0.032783 | -0.12911 | -0.032771 | 1.9547e-05 | 1.2234e-05 | 0.19559 | 0.19559 | 0.19559 | 0.98313 | -0.32154 | 0.98297 | -0.32468 | 13.4337
39 | -0.11492 | -0.029077 | 0.11505 | 0.029156 | 0.00012741 | 7.9296e-05 | 0.17465 | 0.17465 | 0.17465 | 0.97968 | -0.38858 | 0.98087 | -0.3655 | 11.9949
40 | 0.0023234 | 0.00058199 | -0.0023232 | -0.00058226 | 1.3046e-07 | -2.6532e-07 | 0.0035362 | 0.0035363 | 0.0035363 | 0.97763 | -0.42861 | 0.97757 | -0.42978 | 0.97152
41 | -0.00015257 | -3.8239e-05 | 0.00015257 | 3.7861e-05 | 5.9546e-10 | -3.771e-07 | 0.00023097 | 0.00023084 | 0.00023097 | 0.98293 | -0.32545 | 0.98293 | -0.32537 | 0.063455
42 | -0.00053777 | -0.0001344 | 0.00053779 | 0.00013352 | 1.7433e-08 | -8.7859e-07 | 0.00081397 | 0.00081365 | 0.00081397 | 0.98293 | -0.32537 | 0.98297 | -0.32468 | 0.22362
43 | -0.068533 | -0.017239 | 0.068588 | 0.017273 | 5.4905e-05 | 3.4466e-05 | 0.10441 | 0.10441 | 0.10441 | 0.97695 | -0.44253 | 0.9778 | -0.42577 | 14.3416
44 | 0.088517 | 0.022297 | -0.088442 | -0.022249 | 7.4716e-05 | 4.7266e-05 | 0.13462 | 0.13462 | 0.13462 | 0.97871 | -0.40811 | 0.9778 | -0.42577 | 18.4919
45 | 0.024998 | 0.0062751 | -0.024971 | -0.0062584 | 2.7026e-05 | 1.6671e-05 | 0.038028 | 0.038028 | 0.038028 | 0.97827 | -0.41672 | 0.97711 | -0.43941 | 10.4473
46 | -0.11913 | -0.030179 | 0.11918 | 0.030211 | 5.095e-05 | 3.1768e-05 | 0.18084 | 0.18084 | 0.18084 | 0.98087 | -0.3655 | 0.98132 | -0.3566 | 12.4202
47 | 0.0040822 | 0.0010226 | -0.0040819 | -0.0010227 | 3.0426e-07 | -7.2293e-08 | 0.0061927 | 0.0061928 | 0.0061928 | 0.98087 | -0.3655 | 0.98079 | -0.36707 | 1.7013
48 | 0.12857 | 0.032637 | -0.12848 | -0.032582 | 8.8861e-05 | 5.5606e-05 | 0.19478 | 0.19478 | 0.19478 | 0.98297 | -0.32468 | 0.98223 | -0.33906 | 13.3779
49 | 0.12387 | 0.031425 | -0.12376 | -0.031359 | 0.0001044 | 6.5216e-05 | 0.18779 | 0.18779 | 0.18779 | 0.98223 | -0.33906 | 0.98132 | -0.3566 | 12.8975
50 | 0.0014979 | 0.00037512 | -0.0014979 | -0.00037541 | 4.8386e-08 | -2.8431e-07 | 0.0022725 | 0.0022726 | 0.0022726 | 0.98079 | -0.36707 | 0.98075 | -0.36775 | 0.62435

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34494 | 0.088605

## res_load
| p_mw | q_mvar
0 | 0.0076409 | 0.001915
1 | 0.011529 | 0.0028895
2 | 0.00050212 | 0.00012584
3 | 0.072943 | 0.018281
4 | 0.018051 | 0.0045241
5 | 0.014077 | 0.0035281
6 | 0.026137 | 0.0065505
7 | 0.0096612 | 0.0024213
8 | 0.0015036 | 0.00037684
9 | 0.015966 | 0.0040014
10 | 0.036896 | 0.009247
11 | 0.00031444 | 7.8805e-05
12 | 0.0049614 | 0.0012434
13 | 0.01115 | 0.0027944
14 | 0.0023421 | 0.00058699
15 | 0.0044482 | 0.0011148
16 | 0.00015257 | 3.8239e-05
17 | 0.00038519 | 9.6539e-05
18 | 0.021414 | 0.0053669
19 | 0.013114 | 0.0032866
20 | 0.0029293 | 0.00073415
21 | 0.0023232 | 0.00058226
22 | 0.0046171 | 0.0011571
23 | 0.0045835 | 0.0011487
24 | 0.0025839 | 0.0006476
25 | 0.024971 | 0.0062584
26 | 0.019855 | 0.004976
27 | 0.0014979 | 0.00037541

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1