## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-44_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-44_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1059-44_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1059-44_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1059-44_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1059-44_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1059-44_0_4_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_1059-44_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1059-44_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1059-44_0_4_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1059-44_0_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_1059-44_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1059-44_0_4_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_1059-44_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_1059-44_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1059-44_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1059-44_0_4_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1059-44_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1059-44_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1059-44_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1059-44_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1059-44_0_4_node_6 | 0.4 | n |  | TRUE
22 | bus_LV_1059-44_0_4_node_7 | 0.4 | n |  | TRUE
23 | bus_LV_1059-44_0_4_node_8 | 0.4 | n |  | TRUE
24 | bus_LV_1059-44_0_4_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1059-44_0_4_node_9 | 0.4 | n |  | TRUE
26 | bus_LV_1059-44_0_4_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_1059-44_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1059-44_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1059-44_0_4_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1059-44_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1059-44_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1059-44_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_MV_216_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-44_0_4_load_0 | 0 | 0.033029 | 0.0082778 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-44_0_4_load_18 | 5 | 0.0060897 | 0.0015262 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-44_0_4_load_32 | 6 | 0.074347 | 0.018633 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-44_0_4_load_13 | 7 | 0.00536 | 0.0013433 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-44_0_4_load_28 | 9 | 0.0053673 | 0.0013452 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-44_0_4_load_15 | 10 | 0.0044456 | 0.0011142 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-44_0_4_load_26 | 13 | 0.0072727 | 0.0018227 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-44_0_4_load_16 | 14 | 0.0056052 | 0.0014048 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-44_0_4_load_12 | 17 | 0.0059517 | 0.0014916 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-44_0_4_load_11 | 19 | 0.0024198 | 0.00060646 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-44_0_4_load_14 | 20 | 0.0035575 | 0.00089159 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1059-44_0_4_load_6 | 21 | 0.027826 | 0.0069738 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1059-44_0_4_load_7 | 22 | 0.0070566 | 0.0017685 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1059-44_0_4_load_31 | 24 | 0.08054 | 0.020185 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1059-44_0_4_load_9 | 25 | 0.0025253 | 0.00063289 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1059-44_0_4_load_10 | 26 | 0.0029852 | 0.00074816 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1059-44_0_4_load_25 | 27 | 0.0071394 | 0.0017893 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1059-44_0_4_load_22 | 28 | 0.0066486 | 0.0016663 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1059-44_0_4_load_33 | 29 | 0.017174 | 0.0043042 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1059-44_0_4_load_29 | 31 | 0.015823 | 0.0039655 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1059-44_0_4_load_24 | 32 | 0.03008 | 0.0075387 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-44_0_4_line_0 |  | 0 | 1 | 0.023394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1059-44_0_4_line_1 |  | 1 | 2 | 0.002948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1059-44_0_4_line_2 |  | 1 | 3 | 0.028804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1059-44_0_4_line_3 |  | 2 | 4 | 0.074449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_1059-44_0_4_line_4 |  | 2 | 5 | 0.023566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1059-44_0_4_line_5 |  | 3 | 6 | 0.064107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1059-44_0_4_line_6 |  | 4 | 7 | 0.031904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1059-44_0_4_line_7 |  | 6 | 18 | 0.027412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1059-44_0_4_line_8 |  | 7 | 19 | 0.028259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1059-44_0_4_line_9 |  | 8 | 9 | 0.002253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1059-44_0_4_line_10 |  | 8 | 10 | 0.027078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1059-44_0_4_line_11 |  | 10 | 20 | 0.023792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1059-44_0_4_line_12 |  | 11 | 12 | 0.029299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1059-44_0_4_line_13 |  | 11 | 13 | 0.01647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1059-44_0_4_line_14 |  | 11 | 14 | 0.011677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1059-44_0_4_line_15 |  | 12 | 27 | 0.016241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1059-44_0_4_line_16 |  | 12 | 28 | 0.00059499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1059-44_0_4_line_17 |  | 13 | 15 | 0.013747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1059-44_0_4_line_18 |  | 14 | 20 | 0.024806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1059-44_0_4_line_19 |  | 15 | 16 | 0.18911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1059-44_0_4_line_20 |  | 15 | 17 | 0.015963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1059-44_0_4_line_21 |  | 16 | 29 | 0.08685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1059-44_0_4_line_22 |  | 17 | 26 | 0.031054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1059-44_0_4_line_23 |  | 18 | 24 | 0.010022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1059-44_0_4_line_24 |  | 18 | 23 | 0.039144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1059-44_0_4_line_25 |  | 19 | 25 | 0.022586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1059-44_0_4_line_26 |  | 21 | 22 | 0.015901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1059-44_0_4_line_27 |  | 22 | 23 | 0.012004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1059-44_0_4_line_28 |  | 24 | 30 | 0.023386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1059-44_0_4_line_29 |  | 25 | 26 | 0.019046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1059-44_0_4_line_30 |  | 28 | 32 | 0.028302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1059-44_0_4_line_31 |  | 30 | 31 | 0.012032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-44_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 33 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2665329.5766 | 1209957.2824 | 2665312.6833 | 1209973.4652
1 | 2665329.5766 | 1209957.2824 | 2665327.9542 | 1209954.8187
2 | 2665329.5766 | 1209957.2824 | 2665338.0441 | 1209966.2806 | 2665346.6019 | 1209974.6683 | 2665349.7904 | 1209977.794
3 | 2665284.926 | 1209902.0378 | 2665286.8362 | 1209901.1248 | 2665291.8484 | 1209898.7448 | 2665296.3233 | 1209907.955 | 2665314.1163 | 1209933.6987 | 2665327.9542 | 1209954.8187
4 | 2665327.9542 | 1209954.8187 | 2665310.8893 | 1209971.0706
5 | 2665349.7904 | 1209977.794 | 2665334.7174 | 1209988.2687 | 2665333.6128 | 1209989.1906 | 2665313.6306 | 1210005.8265 | 2665325.2347 | 1210019.9929
6 | 2665284.926 | 1209902.0378 | 2665284.8439 | 1209904.6718 | 2665283.0941 | 1209909.678 | 2665274.6462 | 1209932.1052
7 | 2665342.6048 | 1210041.1986 | 2665325.2347 | 1210019.9929
8 | 2665264.6847 | 1209958.5505 | 2665274.6462 | 1209932.1052
9 | 2665282.8038 | 1209932.7334 | 2665284.9157 | 1209933.5347
10 | 2665282.8038 | 1209932.7334 | 2665280.0866 | 1209940.0192 | 2665273.2411 | 1209958.0661
11 | 2665273.2411 | 1209958.0661 | 2665264.8031 | 1209980.3114
12 | 2665251.8641 | 1210014.4229 | 2665273.1974 | 1210024.3289 | 2665277.6018 | 1210028.1683
13 | 2665251.8641 | 1210014.4229 | 2665246.0237 | 1210029.8227
14 | 2665251.8641 | 1210014.4229 | 2665256.0055 | 1210003.5049
15 | 2665277.6018 | 1210028.1683 | 2665269.648 | 1210036.8199 | 2665271.7784 | 1210040.7901
16 | 2665278.0503 | 1210028.5593 | 2665277.6018 | 1210028.1683
17 | 2665239.4209 | 1210038.824 | 2665242.2063 | 1210039.8885 | 2665246.0237 | 1210029.8227
18 | 2665256.0055 | 1210003.5049 | 2665264.8031 | 1209980.3114
19 | 2665229.0289 | 1210139.083 | 2665234.9894 | 1210136.1463 | 2665236.3573 | 1210135.472 | 2665235.0167 | 1210133.6562 | 2665234.8663 | 1210132.8096 | 2665234.5362 | 1210131.0271 | 2665235.4553 | 1210129.6919 | 2665245.6828 | 1210118.8304 | 2665247.7456 | 1210117.163 | 2665250.0642 | 1210116.4324 | 2665253.6401 | 1210116.1046 | 2665259.324 | 1210117.6121 | 2665261.8133 | 1210119.3404 | 2665262.9125 | 1210119.6081 | 2665268.4692 | 1210120.9364 | 2665271.7874 | 1210121.9288 | 2665274.1207 | 1210122.6325 | 2665277.3101 | 1210123.5902 | 2665278.6831 | 1210120.3588 | 2665279.6036 | 1210118.2009 | 2665281.2622 | 1210115.2728 | 2665283.7706 | 1210113.1656 | 2665286.6231 | 1210111.5736 | 2665289.7279 | 1210110.5403 | 2665292.6587 | 1210110.1165 | 2665295.622 | 1210110.2045 | 2665298.5265 | 1210110.8033 | 2665291.9478 | 1210100.7697 | 2665283.4687 | 1210093.528 | 2665278.389 | 1210079.8641 | 2665238.0005 | 1210046.3798 | 2665239.4209 | 1210038.824
20 | 2665239.4209 | 1210038.824 | 2665235.0764 | 1210037.1533 | 2665239.0625 | 1210026.5711
21 | 2665229.0289 | 1210139.083 | 2665223.1621 | 1210141.7872 | 2665222.2912 | 1210142.189 | 2665212.7505 | 1210160.4515 | 2665206.6853 | 1210161.1413 | 2665189.8756 | 1210198.4472 | 2665201.4551 | 1210200.7385
22 | 2665239.0625 | 1210026.5711 | 2665250.0092 | 1209997.5102
23 | 2665342.6048 | 1210041.1986 | 2665350.6309 | 1210047.1997
24 | 2665342.6048 | 1210041.1986 | 2665340.0138 | 1210044.5946 | 2665318.8685 | 1210072.369
25 | 2665264.6847 | 1209958.5505 | 2665256.7229 | 1209979.687
26 | 2665319.8218 | 1210053.0246 | 2665309.3798 | 1210065.0163 | 2665309.3798 | 1210065.0163
27 | 2665318.8685 | 1210072.369 | 2665309.3798 | 1210065.0163
28 | 2665369.3605 | 1210061.2039 | 2665350.6309 | 1210047.1997
29 | 2665256.7229 | 1209979.687 | 2665250.0092 | 1209997.5102
30 | 2665300.4428 | 1210034.3441 | 2665300.6323 | 1210035.7804 | 2665292.8288 | 1210038.3299 | 2665290.0819 | 1210035.8317 | 2665286.8473 | 1210036.2299 | 2665278.0503 | 1210028.5593
31 | 2665369.3605 | 1210061.2039 | 2665368.5127 | 1210065.7418 | 2665367.1511 | 1210073.0311

## bus_geodata
| x | y | coords
0 | 2665312.6833 | 1209973.4652
1 | 2665329.5766 | 1209957.2824
2 | 2665327.9542 | 1209954.8187
3 | 2665349.7904 | 1209977.794
4 | 2665284.926 | 1209902.0378
5 | 2665310.8893 | 1209971.0706
6 | 2665325.2347 | 1210019.9929
7 | 2665274.6462 | 1209932.1052
8 | 2665282.8038 | 1209932.7334
9 | 2665284.9157 | 1209933.5347
10 | 2665273.2411 | 1209958.0661
11 | 2665251.8641 | 1210014.4229
12 | 2665277.6018 | 1210028.1683
13 | 2665246.0237 | 1210029.8227
14 | 2665256.0055 | 1210003.5049
15 | 2665239.4209 | 1210038.824
16 | 2665229.0289 | 1210139.083
17 | 2665239.0625 | 1210026.5711
18 | 2665342.6048 | 1210041.1986
19 | 2665264.6847 | 1209958.5505
20 | 2665264.8031 | 1209980.3114
21 | 2665319.8218 | 1210053.0246
22 | 2665309.3798 | 1210065.0163
23 | 2665318.8685 | 1210072.369
24 | 2665350.6309 | 1210047.1997
25 | 2665256.7229 | 1209979.687
26 | 2665250.0092 | 1209997.5102
27 | 2665271.7784 | 1210040.7901
28 | 2665278.0503 | 1210028.5593
29 | 2665201.4551 | 1210200.7385
30 | 2665369.3605 | 1210061.2039
31 | 2665367.1511 | 1210073.0311
32 | 2665300.4428 | 1210034.3441
33 | 2665277.6018 | 1210028.1683

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97986 | -0.38502 | 0.033029 | 0.0082778
1 | 0.98057 | -0.371 | 0 | 0
2 | 0.98074 | -0.36782 | 0 | 0
3 | 0.97919 | -0.39788 | 0 | 0
4 | 0.98498 | -0.28563 | 0 | 0
5 | 0.98061 | -0.37042 | 0.0060897 | 0.0015262
6 | 0.97612 | -0.45797 | 0.074347 | 0.018633
7 | 0.9868 | -0.25063 | 0.00536 | 0.0013433
8 | 0.99491 | -0.096419 | 0 | 0
9 | 0.99489 | -0.096632 | 0.0053673 | 0.0013452
10 | 0.99504 | -0.09386 | 0.0044456 | 0.0011142
11 | 0.99576 | -0.080019 | 0 | 0
12 | 0.99785 | -0.040517 | 0 | 0
13 | 0.99465 | -0.10092 | 0.0072727 | 0.0018227
14 | 0.99555 | -0.083916 | 0.0056052 | 0.0014048
15 | 0.99375 | -0.11796 | 0 | 0
16 | 0.99078 | -0.17547 | 0 | 0
17 | 0.99277 | -0.13657 | 0.0059517 | 0.0014916
18 | 0.97277 | -0.524 | 0 | 0
19 | 0.98845 | -0.21905 | 0.0024198 | 0.00060646
20 | 0.99525 | -0.089751 | 0.0035575 | 0.00089159
21 | 0.97069 | -0.56511 | 0.027826 | 0.0069738
22 | 0.9711 | -0.55692 | 0.0070566 | 0.0017685
23 | 0.97149 | -0.54919 | 0 | 0
24 | 0.97186 | -0.54181 | 0.08054 | 0.020185
25 | 0.98977 | -0.19365 | 0.0025253 | 0.00063289
26 | 0.9909 | -0.17207 | 0.0029852 | 0.00074816
27 | 0.99774 | -0.042547 | 0.0071394 | 0.0017893
28 | 0.99789 | -0.039698 | 0.0066486 | 0.0016663
29 | 0.98941 | -0.20199 | 0.017174 | 0.0043042
30 | 0.97152 | -0.54864 | 0 | 0
31 | 0.97134 | -0.55216 | 0.015823 | 0.0039655
32 | 1 | 0 | -0.32922 | -0.084565
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.033029 | -0.0082778 | 0.033051 | 0.0082917 | 2.207e-05 | 1.383e-05 | 0.050158 | 0.050158 | 0.050158 | 0.97986 | -0.38502 | 0.98057 | -0.371 | 13.7796
1 | -0.24007 | -0.060727 | 0.24011 | 0.060751 | 3.6722e-05 | 2.3353e-05 | 0.36451 | 0.36451 | 0.36451 | 0.98057 | -0.371 | 0.98074 | -0.36782 | 25.0351
2 | 0.20702 | 0.052436 | -0.20676 | -0.052266 | 0.00026685 | 0.00016933 | 0.31435 | 0.31435 | 0.31435 | 0.98057 | -0.371 | 0.97919 | -0.39788 | 21.5903
3 | -0.2462 | -0.062277 | 0.24718 | 0.062897 | 0.00097498 | 0.00062022 | 0.37375 | 0.37375 | 0.37375 | 0.98074 | -0.36782 | 0.98498 | -0.28563 | 25.6698
4 | 0.0060905 | 0.0015264 | -0.0060897 | -0.0015262 | 7.5462e-07 | 1.8563e-07 | 0.0092408 | 0.0092409 | 0.0092409 | 0.98074 | -0.36782 | 0.98061 | -0.37042 | 2.5387
5 | 0.20676 | 0.052266 | -0.20616 | -0.05189 | 0.00059391 | 0.00037688 | 0.31435 | 0.31436 | 0.31436 | 0.97919 | -0.39788 | 0.97612 | -0.45797 | 21.5904
6 | -0.24718 | -0.062897 | 0.24759 | 0.063163 | 0.00041781 | 0.00026577 | 0.37375 | 0.37375 | 0.37375 | 0.98498 | -0.28563 | 0.9868 | -0.25063 | 25.6697
7 | 0.13182 | 0.033257 | -0.1314 | -0.032991 | 0.00041538 | 0.0002655 | 0.20102 | 0.20102 | 0.20102 | 0.97612 | -0.45797 | 0.97277 | -0.524 | 55.2255
8 | -0.25295 | -0.064507 | 0.25334 | 0.064752 | 0.00038626 | 0.00024576 | 0.38183 | 0.38183 | 0.38183 | 0.9868 | -0.25063 | 0.98845 | -0.21905 | 26.2248
9 | 0.0053673 | 0.0013452 | -0.0053673 | -0.0013452 | 5.4445e-08 | 5.5877e-09 | 0.0080275 | 0.0080276 | 0.0080276 | 0.99491 | -0.096419 | 0.99489 | -0.096632 | 2.2054
10 | -0.0053673 | -0.0013452 | 0.005368 | 0.0013452 | 6.5433e-07 | 6.7098e-08 | 0.0080275 | 0.0080274 | 0.0080275 | 0.99491 | -0.096419 | 0.99504 | -0.09386 | 2.2054
11 | -0.0098135 | -0.0024594 | 0.0098155 | 0.0024603 | 1.9215e-06 | 9.2066e-07 | 0.014675 | 0.014675 | 0.014675 | 0.99504 | -0.09386 | 0.99525 | -0.089751 | 4.0317
12 | -0.31254 | -0.080315 | 0.31314 | 0.080698 | 0.00060097 | 0.00038309 | 0.46775 | 0.46775 | 0.46775 | 0.99576 | -0.080019 | 0.99785 | -0.040517 | 32.1257
13 | 0.29355 | 0.075554 | -0.29325 | -0.075364 | 0.00029809 | 0.00018992 | 0.43938 | 0.43938 | 0.43938 | 0.99576 | -0.080019 | 0.99465 | -0.10092 | 30.1772
14 | 0.018985 | 0.0047609 | -0.018982 | -0.0047588 | 3.5249e-06 | 2.1041e-06 | 0.028372 | 0.028372 | 0.028372 | 0.99576 | -0.080019 | 0.99555 | -0.083916 | 7.7945
15 | 0.0071401 | 0.0017895 | -0.0071394 | -0.0017893 | 6.9047e-07 | 2.2977e-07 | 0.010648 | 0.010648 | 0.010648 | 0.99785 | -0.040517 | 0.99774 | -0.042547 | 2.9252
16 | -0.32028 | -0.082487 | 0.32029 | 0.082495 | 1.2766e-05 | 8.1392e-06 | 0.4784 | 0.4784 | 0.4784 | 0.99785 | -0.040517 | 0.99789 | -0.039698 | 32.857
17 | 0.28598 | 0.073541 | -0.28574 | -0.07339 | 0.00023664 | 0.00015074 | 0.4285 | 0.4285 | 0.4285 | 0.99465 | -0.10092 | 0.99375 | -0.11796 | 29.4299
18 | 0.013377 | 0.003354 | -0.013373 | -0.0033519 | 3.7187e-06 | 2.0575e-06 | 0.019994 | 0.019994 | 0.019994 | 0.99555 | -0.083916 | 0.99525 | -0.089751 | 5.4929
19 | 0.017243 | 0.0043448 | -0.017196 | -0.0043169 | 4.7305e-05 | 2.7832e-05 | 0.025827 | 0.025828 | 0.025828 | 0.99375 | -0.11796 | 0.99078 | -0.17547 | 7.0956
20 | 0.2685 | 0.069046 | -0.26826 | -0.068891 | 0.00024265 | 0.00015447 | 0.40267 | 0.40267 | 0.40267 | 0.99375 | -0.11796 | 0.99277 | -0.13657 | 27.6561
21 | 0.017196 | 0.0043169 | -0.017174 | -0.0043042 | 2.1727e-05 | 1.2788e-05 | 0.025828 | 0.025828 | 0.025828 | 0.99078 | -0.17547 | 0.98941 | -0.20199 | 7.0957
22 | 0.26231 | 0.067399 | -0.26186 | -0.067112 | 0.00045138 | 0.00028728 | 0.39375 | 0.39375 | 0.39375 | 0.99277 | -0.13657 | 0.9909 | -0.17207 | 27.0435
23 | 0.096452 | 0.024208 | -0.09637 | -0.024155 | 8.182e-05 | 5.2241e-05 | 0.14755 | 0.14755 | 0.14755 | 0.97277 | -0.524 | 0.97186 | -0.54181 | 40.5365
24 | 0.034948 | 0.0087835 | -0.034906 | -0.0087572 | 4.1965e-05 | 2.6372e-05 | 0.053468 | 0.053468 | 0.053468 | 0.97277 | -0.524 | 0.97149 | -0.54919 | 14.6891
25 | -0.25576 | -0.065359 | 0.25607 | 0.065559 | 0.00031464 | 0.00020021 | 0.38547 | 0.38547 | 0.38547 | 0.98845 | -0.21905 | 0.98977 | -0.19365 | 26.4749
26 | -0.027826 | -0.0069738 | 0.027837 | 0.0069805 | 1.0849e-05 | 6.7469e-06 | 0.042656 | 0.042655 | 0.042656 | 0.97069 | -0.56511 | 0.9711 | -0.55692 | 11.7185
27 | -0.034893 | -0.0087491 | 0.034906 | 0.0087572 | 1.2869e-05 | 8.0877e-06 | 0.053468 | 0.053468 | 0.053468 | 0.9711 | -0.55692 | 0.97149 | -0.54919 | 14.6891
28 | 0.01583 | 0.0039701 | -0.015825 | -0.0039671 | 5.1524e-06 | 3.0079e-06 | 0.024239 | 0.024239 | 0.024239 | 0.97186 | -0.54181 | 0.97152 | -0.54864 | 6.659
29 | -0.2586 | -0.066192 | 0.25887 | 0.066364 | 0.00027057 | 0.00017218 | 0.38927 | 0.38927 | 0.38927 | 0.98977 | -0.19365 | 0.9909 | -0.17207 | 26.7356
30 | -0.32694 | -0.084162 | 0.32757 | 0.084565 | 0.00063267 | 0.00040343 | 0.48831 | 0.48831 | 0.48831 | 0.99789 | -0.039698 | 1 | 0 | 33.5379
31 | 0.015825 | 0.0039671 | -0.015823 | -0.0039655 | 2.6509e-06 | 1.5476e-06 | 0.024239 | 0.024239 | 0.024239 | 0.97152 | -0.54864 | 0.97134 | -0.55216 | 6.659

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3593 | 0.092104

## res_load
| p_mw | q_mvar
0 | 0.033029 | 0.0082778
1 | 0.0060897 | 0.0015262
2 | 0.074347 | 0.018633
3 | 0.00536 | 0.0013433
4 | 0.0053673 | 0.0013452
5 | 0.0044456 | 0.0011142
6 | 0.0072727 | 0.0018227
7 | 0.0056052 | 0.0014048
8 | 0.0059517 | 0.0014916
9 | 0.0024198 | 0.00060646
10 | 0.0035575 | 0.00089159
11 | 0.027826 | 0.0069738
12 | 0.0070566 | 0.0017685
13 | 0.08054 | 0.020185
14 | 0.0025253 | 0.00063289
15 | 0.0029852 | 0.00074816
16 | 0.0071394 | 0.0017893
17 | 0.0066486 | 0.0016663
18 | 0.017174 | 0.0043042
19 | 0.015823 | 0.0039655
20 | 0.03008 | 0.0075387

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1