## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-51_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-51_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1059-51_0_4_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_1059-51_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1059-51_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1059-51_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1059-51_0_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1059-51_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1059-51_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1059-51_0_4_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_1059-51_0_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1059-51_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1059-51_0_4_node_98 | 0.4 | n |  | TRUE
13 | bus_LV_1059-51_0_4_node_104 | 0.4 | n |  | TRUE
14 | bus_LV_1059-51_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1059-51_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1059-51_0_4_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_1059-51_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1059-51_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1059-51_0_4_node_110 | 0.4 | n |  | TRUE
20 | bus_LV_1059-51_0_4_node_74 | 0.4 | n |  | TRUE
21 | bus_LV_1059-51_0_4_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_1059-51_0_4_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_1059-51_0_4_node_124 | 0.4 | n |  | TRUE
24 | bus_LV_1059-51_0_4_node_125 | 0.4 | n |  | TRUE
25 | bus_LV_1059-51_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1059-51_0_4_node_52 | 0.4 | n |  | TRUE
27 | bus_LV_1059-51_0_4_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_1059-51_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1059-51_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1059-51_0_4_node_97 | 0.4 | n |  | TRUE
31 | bus_LV_1059-51_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1059-51_0_4_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_1059-51_0_4_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_1059-51_0_4_node_65 | 0.4 | n |  | TRUE
35 | bus_LV_1059-51_0_4_node_77 | 0.4 | n |  | TRUE
36 | bus_LV_1059-51_0_4_node_107 | 0.4 | n |  | TRUE
37 | bus_LV_1059-51_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1059-51_0_4_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1059-51_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1059-51_0_4_node_96 | 0.4 | n |  | TRUE
41 | bus_LV_1059-51_0_4_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_1059-51_0_4_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_1059-51_0_4_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_1059-51_0_4_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_1059-51_0_4_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_1059-51_0_4_node_71 | 0.4 | n |  | TRUE
47 | bus_LV_1059-51_0_4_node_91 | 0.4 | n |  | TRUE
48 | bus_LV_1059-51_0_4_node_93 | 0.4 | n |  | TRUE
49 | bus_LV_1059-51_0_4_node_69 | 0.4 | n |  | TRUE
50 | bus_LV_1059-51_0_4_node_92 | 0.4 | n |  | TRUE
51 | bus_LV_1059-51_0_4_node_94 | 0.4 | n |  | TRUE
52 | bus_LV_1059-51_0_4_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_1059-51_0_4_node_99 | 0.4 | n |  | TRUE
54 | bus_LV_1059-51_0_4_node_105 | 0.4 | n |  | TRUE
55 | bus_LV_1059-51_0_4_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_1059-51_0_4_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_1059-51_0_4_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_1059-51_0_4_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_1059-51_0_4_node_87 | 0.4 | n |  | TRUE
60 | bus_LV_1059-51_0_4_node_86 | 0.4 | n |  | TRUE
61 | bus_LV_1059-51_0_4_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_1059-51_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_1059-51_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_1059-51_0_4_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_1059-51_0_4_node_90 | 0.4 | n |  | TRUE
66 | bus_LV_1059-51_0_4_node_88 | 0.4 | n |  | TRUE
67 | bus_LV_1059-51_0_4_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_1059-51_0_4_node_108 | 0.4 | n |  | TRUE
69 | bus_LV_1059-51_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_1059-51_0_4_node_89 | 0.4 | n |  | TRUE
71 | bus_LV_1059-51_0_4_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_1059-51_0_4_node_42 | 0.4 | n |  | TRUE
73 | bus_LV_1059-51_0_4_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_1059-51_0_4_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_1059-51_0_4_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_1059-51_0_4_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_1059-51_0_4_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_1059-51_0_4_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_1059-51_0_4_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_1059-51_0_4_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_1059-51_0_4_node_117 | 0.4 | n |  | TRUE
82 | bus_LV_1059-51_0_4_node_116 | 0.4 | n |  | TRUE
83 | bus_LV_1059-51_0_4_node_118 | 0.4 | n |  | TRUE
84 | bus_LV_1059-51_0_4_node_115 | 0.4 | n |  | TRUE
85 | bus_LV_1059-51_0_4_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_1059-51_0_4_node_56 | 0.4 | n |  | TRUE
87 | bus_LV_1059-51_0_4_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_1059-51_0_4_node_58 | 0.4 | n |  | TRUE
89 | bus_LV_1059-51_0_4_node_59 | 0.4 | n |  | TRUE
90 | bus_LV_1059-51_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_1059-51_0_4_node_106 | 0.4 | n |  | TRUE
92 | bus_LV_1059-51_0_4_node_62 | 0.4 | n |  | TRUE
93 | bus_LV_1059-51_0_4_node_114 | 0.4 | n |  | TRUE
94 | bus_LV_1059-51_0_4_node_75 | 0.4 | n |  | TRUE
95 | bus_LV_1059-51_0_4_node_103 | 0.4 | n |  | TRUE
96 | bus_LV_1059-51_0_4_node_70 | 0.4 | n |  | TRUE
97 | bus_LV_1059-51_0_4_node_72 | 0.4 | n |  | TRUE
98 | bus_LV_1059-51_0_4_node_73 | 0.4 | n |  | TRUE
99 | bus_LV_1059-51_0_4_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_1059-51_0_4_node_113 | 0.4 | n |  | TRUE
101 | bus_LV_1059-51_0_4_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_1059-51_0_4_node_78 | 0.4 | n |  | TRUE
103 | bus_LV_1059-51_0_4_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_1059-51_0_4_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_1059-51_0_4_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_1059-51_0_4_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_1059-51_0_4_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_1059-51_0_4_node_82 | 0.4 | n |  | TRUE
109 | bus_LV_1059-51_0_4_node_83 | 0.4 | n |  | TRUE
110 | bus_LV_1059-51_0_4_node_84 | 0.4 | n |  | TRUE
111 | bus_LV_1059-51_0_4_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_1059-51_0_4_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_1059-51_0_4_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_1059-51_0_4_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1059-51_0_4_node_123 | 0.4 | n |  | TRUE
116 | bus_LV_1059-51_0_4_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_1059-51_0_4_node_121 | 0.4 | n |  | TRUE
118 | bus_LV_1059-51_0_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_1059-51_0_4_node_120 | 0.4 | n |  | TRUE
120 | bus_MV_24_1_node_104 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-51_0_4_load_0 | 0 | 0.010669 | 0.002674 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-51_0_4_load_21 | 6 | 0.002827 | 0.00070852 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-51_0_4_load_39 | 9 | 0.012402 | 0.0031082 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-51_0_4_load_25 | 10 | 0.011078 | 0.0027764 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-51_0_4_load_98 | 12 | 0.0085929 | 0.0021536 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-51_0_4_load_104 | 13 | 0.0035806 | 0.00089739 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-51_0_4_load_26 | 16 | 0.022805 | 0.0057154 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-51_0_4_load_110 | 19 | 0.010658 | 0.0026712 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-51_0_4_load_74 | 20 | 0.01662 | 0.0041654 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-51_0_4_load_48 | 21 | 0.015583 | 0.0039056 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-51_0_4_load_29 | 22 | 0.0062084 | 0.001556 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1059-51_0_4_load_124 | 23 | 0.0095129 | 0.0023842 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1059-51_0_4_load_125 | 24 | 0.020935 | 0.0052467 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1059-51_0_4_load_35 | 27 | 0.013147 | 0.0032949 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1059-51_0_4_load_24 | 28 | 0.0093332 | 0.0023391 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1059-51_0_4_load_18 | 29 | 0.0016078 | 0.00040296 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1059-51_0_4_load_27 | 31 | 0.012924 | 0.0032391 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1059-51_0_4_load_77 | 35 | 0.002055 | 0.00051503 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1059-51_0_4_load_107 | 36 | 0.0020535 | 0.00051465 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1059-51_0_4_load_34 | 39 | 0.012883 | 0.0032287 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1059-51_0_4_load_96 | 40 | 0.014142 | 0.0035444 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1059-51_0_4_load_17 | 41 | 0.0033672 | 0.00084389 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1059-51_0_4_load_22 | 44 | 0.0011041 | 0.00027672 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1059-51_0_4_load_23 | 45 | 0.0016045 | 0.00040211 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1059-51_0_4_load_71 | 46 | 0.0015439 | 0.00038694 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1059-51_0_4_load_91 | 47 | 0.0010692 | 0.00026797 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1059-51_0_4_load_93 | 48 | 0.0012785 | 0.00032041 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1059-51_0_4_load_69 | 49 | 0.0020822 | 0.00052185 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1059-51_0_4_load_92 | 50 | 0.0010783 | 0.00027024 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1059-51_0_4_load_94 | 51 | 0.00097147 | 0.00024347 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1059-51_0_4_load_99 | 53 | 0.011985 | 0.0030036 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1059-51_0_4_load_105 | 54 | 0.01219 | 0.0030552 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1059-51_0_4_load_30 | 55 | 0.00465 | 0.0011654 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1059-51_0_4_load_31 | 56 | 0.0030095 | 0.00075425 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1059-51_0_4_load_32 | 57 | 0.005127 | 0.001285 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1059-51_0_4_load_33 | 58 | 0.0016363 | 0.00041009 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1059-51_0_4_load_87 | 59 | 0.0063565 | 0.0015931 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1059-51_0_4_load_86 | 60 | 0.0055723 | 0.0013966 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1059-51_0_4_load_37 | 62 | 0.013373 | 0.0033515 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1059-51_0_4_load_50 | 63 | 0.013586 | 0.0034051 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1059-51_0_4_load_90 | 65 | 0.0042991 | 0.0010775 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1059-51_0_4_load_88 | 66 | 0.0031533 | 0.00079028 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1059-51_0_4_load_108 | 68 | 0.0018949 | 0.0004749 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1059-51_0_4_load_41 | 69 | 0.0031996 | 0.0008019 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1059-51_0_4_load_89 | 70 | 0.0070551 | 0.0017682 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1059-51_0_4_load_40 | 71 | 0.0061576 | 0.0015432 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1059-51_0_4_load_42 | 72 | 0.0064457 | 0.0016155 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1059-51_0_4_load_44 | 73 | 0.0018959 | 0.00047515 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1059-51_0_4_load_45 | 74 | 0.008484 | 0.0021263 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1059-51_0_4_load_46 | 75 | 0.0018918 | 0.00047412 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1059-51_0_4_load_47 | 76 | 0.0035918 | 0.0009002 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1059-51_0_4_load_67 | 77 | 0.0030323 | 0.00075998 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1059-51_0_4_load_66 | 78 | 0.0018713 | 0.000469 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1059-51_0_4_load_53 | 79 | 0.013653 | 0.0034217 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1059-51_0_4_load_117 | 81 | 0.0018747 | 0.00046984 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1059-51_0_4_load_116 | 82 | 0.0018046 | 0.00045228 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1059-51_0_4_load_118 | 83 | 0.0018747 | 0.00046984 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1059-51_0_4_load_115 | 84 | 0.0018026 | 0.00045178 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1059-51_0_4_load_55 | 85 | 0.001802 | 0.00045163 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1059-51_0_4_load_56 | 86 | 0.0027381 | 0.00068624 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1059-51_0_4_load_57 | 87 | 0.0030179 | 0.00075636 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1059-51_0_4_load_58 | 88 | 0.0036969 | 0.00092652 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1059-51_0_4_load_59 | 89 | 0.0018046 | 0.00045228 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1059-51_0_4_load_68 | 90 | 0.0018755 | 0.00047004 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1059-51_0_4_load_106 | 91 | 0.0018026 | 0.00045178 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1059-51_0_4_load_114 | 93 | 0.001802 | 0.00045163 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1059-51_0_4_load_75 | 94 | 0.0017758 | 0.00044505 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1059-51_0_4_load_103 | 95 | 0.002117 | 0.00053058 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1059-51_0_4_load_70 | 96 | 0.010584 | 0.0026525 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1059-51_0_4_load_72 | 97 | 0.0013349 | 0.00033456 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1059-51_0_4_load_73 | 98 | 0.0014042 | 0.00035194 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1059-51_0_4_load_112 | 99 | 0.0014517 | 0.00036384 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1059-51_0_4_load_113 | 100 | 0.0031996 | 0.0008019 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1059-51_0_4_load_76 | 101 | 0.0035851 | 0.00089851 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1059-51_0_4_load_78 | 102 | 0.0012464 | 0.00031238 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1059-51_0_4_load_79 | 103 | 0.0016219 | 0.0004065 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1059-51_0_4_load_80 | 104 | 0.0020771 | 0.00052057 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1059-51_0_4_load_81 | 105 | 0.00057967 | 0.00014528 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1059-51_0_4_load_82 | 108 | 0.0028176 | 0.00070615 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1059-51_0_4_load_83 | 109 | 0.014739 | 0.003694 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1059-51_0_4_load_84 | 110 | 0.014002 | 0.0035092 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1059-51_0_4_load_85 | 111 | 0.0018698 | 0.00046861 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1059-51_0_4_load_100 | 112 | 0.0025481 | 0.00063861 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1059-51_0_4_load_95 | 113 | 0.0018494 | 0.0004635 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1059-51_0_4_load_109 | 114 | 0.0018941 | 0.0004747 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1059-51_0_4_load_123 | 115 | 0.00026358 | 6.606e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1059-51_0_4_load_122 | 116 | 0.0018941 | 0.0004747 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1059-51_0_4_load_121 | 117 | 0.0018931 | 0.00047445 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1059-51_0_4_load_119 | 118 | 0.0018747 | 0.00046984 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1059-51_0_4_load_120 | 119 | 0.0018743 | 0.00046975 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-51_0_4_line_0 |  | 0 | 1 | 0.053875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1059-51_0_4_line_1 |  | 1 | 2 | 0.021608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1059-51_0_4_line_2 |  | 2 | 11 | 0.002606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1059-51_0_4_line_3 |  | 2 | 9 | 0.037261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1059-51_0_4_line_4 |  | 3 | 4 | 0.050857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1059-51_0_4_line_5 |  | 3 | 5 | 0.038242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1059-51_0_4_line_6 |  | 3 | 6 | 0.018093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1059-51_0_4_line_7 |  | 4 | 10 | 0.020272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1059-51_0_4_line_8 |  | 4 | 7 | 0.016996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1059-51_0_4_line_9 |  | 5 | 13 | 0.009324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1059-51_0_4_line_10 |  | 6 | 29 | 0.0079406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1059-51_0_4_line_11 |  | 7 | 8 | 0.017011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1059-51_0_4_line_12 |  | 7 | 9 | 0.013932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1059-51_0_4_line_13 |  | 8 | 12 | 0.01087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1059-51_0_4_line_14 |  | 10 | 28 | 0.048699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1059-51_0_4_line_15 |  | 11 | 22 | 0.014252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1059-51_0_4_line_16 |  | 12 | 30 | 0.04937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1059-51_0_4_line_17 |  | 13 | 26 | 0.0066543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1059-51_0_4_line_18 |  | 14 | 15 | 0.033613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1059-51_0_4_line_19 |  | 14 | 16 | 0.017729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1059-51_0_4_line_20 |  | 15 | 23 | 0.007523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1059-51_0_4_line_21 |  | 15 | 24 | 0.03865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1059-51_0_4_line_22 |  | 16 | 31 | 0.013139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1059-51_0_4_line_23 |  | 17 | 18 | 0.021885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1059-51_0_4_line_24 |  | 17 | 19 | 0.021055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1059-51_0_4_line_25 |  | 18 | 20 | 0.025354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1059-51_0_4_line_26 |  | 18 | 21 | 0.041313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1059-51_0_4_line_27 |  | 20 | 32 | 0.071006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1059-51_0_4_line_28 |  | 21 | 37 | 0.0445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1059-51_0_4_line_29 |  | 25 | 26 | 0.008293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1059-51_0_4_line_30 |  | 25 | 27 | 0.030404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1059-51_0_4_line_31 |  | 26 | 38 | 0.02096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1059-51_0_4_line_32 |  | 27 | 39 | 0.036143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1059-51_0_4_line_33 |  | 29 | 43 | 0.015966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1059-51_0_4_line_34 |  | 29 | 41 | 0.011866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1059-51_0_4_line_35 |  | 30 | 40 | 0.019117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1059-51_0_4_line_36 |  | 30 | 53 | 0.025423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1059-51_0_4_line_37 |  | 31 | 37 | 0.030211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1059-51_0_4_line_38 |  | 32 | 33 | 0.27063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1059-51_0_4_line_39 |  | 33 | 34 | 0.002824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1059-51_0_4_line_40 |  | 33 | 35 | 0.058388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1059-51_0_4_line_41 |  | 34 | 36 | 0.035237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1059-51_0_4_line_42 |  | 35 | 94 | 0.015977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1059-51_0_4_line_43 |  | 36 | 95 | 0.013265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1059-51_0_4_line_44 |  | 37 | 52 | 0.002484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1059-51_0_4_line_45 |  | 38 | 69 | 0.041331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1059-51_0_4_line_46 |  | 39 | 61 | 0.018301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1059-51_0_4_line_47 |  | 41 | 42 | 0.013819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_1059-51_0_4_line_48 |  | 42 | 44 | 0.027456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1059-51_0_4_line_49 |  | 42 | 45 | 0.011046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_1059-51_0_4_line_50 |  | 43 | 46 | 0.015821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1059-51_0_4_line_51 |  | 44 | 47 | 0.012873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1059-51_0_4_line_52 |  | 45 | 48 | 0.048053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_1059-51_0_4_line_53 |  | 46 | 49 | 0.010842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1059-51_0_4_line_54 |  | 47 | 50 | 0.0068453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1059-51_0_4_line_55 |  | 48 | 51 | 0.020615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_1059-51_0_4_line_56 |  | 49 | 96 | 0.024614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1059-51_0_4_line_57 |  | 51 | 113 | 0.019835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_1059-51_0_4_line_58 |  | 52 | 53 | 0.016418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_1059-51_0_4_line_59 |  | 52 | 54 | 0.050243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1059-51_0_4_line_60 |  | 55 | 56 | 0.087916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1059-51_0_4_line_61 |  | 55 | 57 | 0.0039502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1059-51_0_4_line_62 |  | 56 | 58 | 0.025132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1059-51_0_4_line_63 |  | 58 | 59 | 0.20788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1059-51_0_4_line_64 |  | 59 | 60 | 0.053358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1059-51_0_4_line_65 |  | 60 | 110 | 0.034506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1059-51_0_4_line_66 |  | 61 | 62 | 0.018296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1059-51_0_4_line_67 |  | 62 | 63 | 0.034407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1059-51_0_4_line_68 |  | 63 | 67 | 0.017837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1059-51_0_4_line_69 |  | 64 | 65 | 0.0064246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1059-51_0_4_line_70 |  | 64 | 66 | 0.0065335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1059-51_0_4_line_71 |  | 65 | 68 | 0.027541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1059-51_0_4_line_72 |  | 66 | 70 | 0.013464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1059-51_0_4_line_73 |  | 67 | 79 | 0.0088906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1059-51_0_4_line_74 |  | 67 | 80 | 0.038856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1059-51_0_4_line_75 |  | 68 | 114 | 0.0001995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1059-51_0_4_line_76 |  | 69 | 71 | 0.010635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1059-51_0_4_line_77 |  | 71 | 72 | 0.043812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1059-51_0_4_line_78 |  | 73 | 74 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1059-51_0_4_line_79 |  | 73 | 75 | 0.0011861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1059-51_0_4_line_80 |  | 75 | 76 | 0.0034066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1059-51_0_4_line_81 |  | 76 | 77 | 0.018061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1059-51_0_4_line_82 |  | 77 | 78 | 0.010384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1059-51_0_4_line_83 |  | 78 | 90 | 0.00046804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1059-51_0_4_line_84 |  | 80 | 81 | 0.01451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1059-51_0_4_line_85 |  | 80 | 82 | 0.014586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1059-51_0_4_line_86 |  | 81 | 83 | 4.7563e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1059-51_0_4_line_87 |  | 82 | 84 | 0.00010905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1059-51_0_4_line_88 |  | 83 | 118 | 3.8728e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1059-51_0_4_line_89 |  | 84 | 93 | 0.00010454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1059-51_0_4_line_90 |  | 85 | 86 | 0.013476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1059-51_0_4_line_91 |  | 85 | 87 | 0.0020438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1059-51_0_4_line_92 |  | 86 | 88 | 0.016923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1059-51_0_4_line_93 |  | 87 | 89 | 0.016733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1059-51_0_4_line_94 |  | 88 | 90 | 0.0053552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1059-51_0_4_line_95 |  | 89 | 91 | 0.0088476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1059-51_0_4_line_96 |  | 91 | 92 | 0.026853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1059-51_0_4_line_97 |  | 92 | 93 | 0.024889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1059-51_0_4_line_98 |  | 94 | 101 | 0.030842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_1059-51_0_4_line_99 |  | 96 | 97 | 0.011172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1059-51_0_4_line_100 |  | 97 | 98 | 0.0070855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1059-51_0_4_line_101 |  | 98 | 99 | 0.0074287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1059-51_0_4_line_102 |  | 99 | 100 | 0.0082734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1059-51_0_4_line_103 |  | 101 | 102 | 0.025912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_1059-51_0_4_line_104 |  | 102 | 103 | 0.0029733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_1059-51_0_4_line_105 |  | 103 | 104 | 0.00016209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1059-51_0_4_line_106 |  | 104 | 105 | 0.12433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1059-51_0_4_line_107 |  | 105 | 106 | 0.050302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_1059-51_0_4_line_108 |  | 106 | 107 | 0.11207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1059-51_0_4_line_109 |  | 107 | 115 | 0.3115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1059-51_0_4_line_110 |  | 108 | 109 | 0.021806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1059-51_0_4_line_111 |  | 108 | 110 | 0.014816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1059-51_0_4_line_112 |  | 109 | 111 | 0.049003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1059-51_0_4_line_113 |  | 111 | 112 | 0.03601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1059-51_0_4_line_114 |  | 112 | 113 | 0.020532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_1059-51_0_4_line_115 |  | 114 | 116 | 0.00020721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1059-51_0_4_line_116 |  | 116 | 117 | 0.00019801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1059-51_0_4_line_117 |  | 117 | 119 | 0.029025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1059-51_0_4_line_118 |  | 118 | 119 | 4.9229e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-51_0_4_trafo_34 | 0.63 MVA 20/0.4 kV | 120 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26
0 | 2663263.0988 | 1209269.1932 | 2663248.7668 | 1209247.2391 | 2663245.8338 | 1209243.5391 | 2663243.0698 | 1209241.8199 | 2663238.9811 | 1209241.0094 | 2663233.7088 | 1209243.5663 | 2663226.0268 | 1209249.4102
1 | 2663263.0988 | 1209269.1932 | 2663266.4713 | 1209267.2834 | 2663274.314 | 1209278.9625 | 2663276.802 | 1209277.31 | 2663277.3685 | 1209276.938
2 | 2663279.2805 | 1209278.7149 | 2663277.3685 | 1209276.938
3 | 2663277.3685 | 1209276.938 | 2663257.3905 | 1209245.485
4 | 2663231.5934 | 1209234.4494 | 2663232.2618 | 1209231.6326 | 2663232.4448 | 1209228.7105 | 2663231.8877 | 1209226.759 | 2663230.443 | 1209224.6424 | 2663225.5159 | 1209220.4543 | 2663219.5142 | 1209216.5217 | 2663212.656 | 1209213.0803 | 2663209.3985 | 1209212.0119 | 2663206.1995 | 1209211.1775 | 2663202.458 | 1209210.5931 | 2663199.0709 | 1209210.2904 | 2663195.9549 | 1209210.224 | 2663195.9521 | 1209209.7681 | 2663195.9247 | 1209208.0446
5 | 2663195.9247 | 1209208.0446 | 2663195.8835 | 1209205.4759 | 2663197.2901 | 1209205.4575 | 2663199.4938 | 1209204.8137 | 2663201.4947 | 1209203.2228 | 2663202.3584 | 1209199.1851 | 2663206.1962 | 1209198.5698 | 2663205.5493 | 1209194.3382 | 2663206.3668 | 1209189.644 | 2663208.8819 | 1209184.0005 | 2663213.449 | 1209179.8463
6 | 2663195.9247 | 1209208.0446 | 2663190.6971 | 1209207.8225 | 2663180.9194 | 1209204.4169 | 2663178.7827 | 1209203.1058
7 | 2663231.5934 | 1209234.4494 | 2663226.0628 | 1209237.7151 | 2663215.3832 | 1209246.532
8 | 2663231.5934 | 1209234.4494 | 2663238.2984 | 1209232.9862 | 2663240.8594 | 1209233.0578 | 2663248.1269 | 1209235.1806
9 | 2663213.449 | 1209179.8463 | 2663212.1233 | 1209175.8187 | 2663211.5959 | 1209173.2227 | 2663212.321 | 1209170.8984
10 | 2663172.0148 | 1209198.9527 | 2663178.7827 | 1209203.1058
11 | 2663248.1269 | 1209235.1806 | 2663247.5372 | 1209232.0057 | 2663242.2689 | 1209225.5793 | 2663238.1262 | 1209221.9777
12 | 2663248.1269 | 1209235.1806 | 2663251.2776 | 1209237.7044 | 2663257.3905 | 1209245.485
13 | 2663238.1262 | 1209221.9777 | 2663241.4101 | 1209219.1108 | 2663247.4634 | 1209216.7138
14 | 2663180.3842 | 1209280.289 | 2663191.0004 | 1209268.9072 | 2663196.375 | 1209263.1384 | 2663205.986 | 1209254.2903 | 2663215.3832 | 1209246.532
15 | 2663279.2805 | 1209278.7149 | 2663283.8792 | 1209279.453 | 2663292.2558 | 1209274.7755
16 | 2663293.3655 | 1209198.5378 | 2663247.4634 | 1209216.7138
17 | 2663214.3028 | 1209164.5461 | 2663212.321 | 1209170.8984
18 | 2663355.8852 | 1209238.3251 | 2663357.4655 | 1209240.5544 | 2663370.0257 | 1209231.749 | 2663373.6419 | 1209239.8367 | 2663375.4678 | 1209241.8351 | 2663378.378 | 1209242.6665 | 2663379.3216 | 1209242.5765
19 | 2663355.8852 | 1209238.3251 | 2663355.3683 | 1209237.6081 | 2663353.3705 | 1209220.8817
20 | 2663379.3216 | 1209242.5765 | 2663386.8321 | 1209241.8558
21 | 2663362.9609 | 1209270.6754 | 2663368.6805 | 1209268.2235 | 2663374.3518 | 1209264.6038 | 2663378.3916 | 1209261.4225 | 2663379.9248 | 1209260.2158 | 2663381.504 | 1209258.9652 | 2663380.1303 | 1209254.4701 | 2663379.7939 | 1209252.4986 | 2663379.3216 | 1209242.5765
22 | 2663351.8122 | 1209207.8356 | 2663353.3705 | 1209220.8817
23 | 2663426.3926 | 1209177.3701 | 2663425.0874 | 1209180.0134 | 2663419.3031 | 1209188.5349 | 2663416.0158 | 1209191.713 | 2663413.8784 | 1209188.2549
24 | 2663426.3926 | 1209177.3701 | 2663432.728 | 1209179.2163 | 2663446.9698 | 1209181.6946
25 | 2663413.8784 | 1209188.2549 | 2663420.8936 | 1209179.7909 | 2663427.1984 | 1209166.8878
26 | 2663413.8784 | 1209188.2549 | 2663410.0522 | 1209182.0549 | 2663407.2991 | 1209179.3129 | 2663403.0964 | 1209177.7896 | 2663377.4708 | 1209179.328
27 | 2663470.1085 | 1209111.0833 | 2663462.4915 | 1209119.652 | 2663450.3401 | 1209132.1526 | 2663436.4042 | 1209148.0475 | 2663427.1984 | 1209166.8878
28 | 2663333.5072 | 1209185.2109 | 2663353.0602 | 1209180.7935 | 2663377.4708 | 1209179.328
29 | 2663214.3028 | 1209164.5461 | 2663215.4366 | 1209165.1585 | 2663216.9182 | 1209165.9524 | 2663218.0198 | 1209167.4428 | 2663219.4228 | 1209170.6262
30 | 2663219.4228 | 1209170.6262 | 2663247.6396 | 1209159.3017
31 | 2663214.3028 | 1209164.5461 | 2663216.519 | 1209159.144 | 2663223.3523 | 1209147.7317 | 2663221.9506 | 1209146.5717
32 | 2663247.6396 | 1209159.3017 | 2663252.7005 | 1209157.2706 | 2663281.1983 | 1209145.8792
33 | 2663172.0148 | 1209198.9527 | 2663175.3728 | 1209183.3454
34 | 2663172.0148 | 1209198.9527 | 2663162.3113 | 1209192.1236
35 | 2663293.3655 | 1209198.5378 | 2663286.3499 | 1209180.7543
36 | 2663293.3655 | 1209198.5378 | 2663317.0431 | 1209189.2801
37 | 2663333.5072 | 1209185.2109 | 2663346.5078 | 1209196.5113 | 2663351.1587 | 1209202.3642 | 2663351.8122 | 1209207.8356
38 | 2663385.2254 | 1208945.8811 | 2663468.5991 | 1208949.2578 | 2663478.2088 | 1208949.9048 | 2663484.6506 | 1208952.4971 | 2663489.8003 | 1208956.4877 | 2663494.0236 | 1208961.0909 | 2663496.5651 | 1208965.8653 | 2663498.1835 | 1208971.6638 | 2663498.2976 | 1208975.2227 | 2663496.9965 | 1208982.48 | 2663494.8423 | 1208987.0265 | 2663486.5118 | 1208999.7679 | 2663483.5526 | 1209004.2502 | 2663479.7378 | 1209012.6926 | 2663477.8288 | 1209019.9211 | 2663471.9984 | 1209052.0453 | 2663470.8413 | 1209062.9174 | 2663470.6616 | 1209071.2316 | 2663471.9933 | 1209083.9646 | 2663474.5421 | 1209096.6217 | 2663474.5299 | 1209099.2009 | 2663474.5232 | 1209100.5461 | 2663473.6467 | 1209105.0506 | 2663471.7034 | 1209108.3653 | 2663470.1085 | 1209111.0833
39 | 2663385.2554 | 1208943.0575 | 2663385.2254 | 1208945.8811
40 | 2663385.2254 | 1208945.8811 | 2663375.3284 | 1208945.7982 | 2663370.594 | 1208946.3594 | 2663365.0534 | 1208947.6681 | 2663359.0431 | 1208950.2503 | 2663353.796 | 1208953.2742 | 2663334.2703 | 1208969.3768 | 2663334.1556 | 1208969.4236
41 | 2663385.2554 | 1208943.0575 | 2663373.8585 | 1208943.1921 | 2663365.0652 | 1208945.1222 | 2663355.0817 | 1208949.6079 | 2663351.8875 | 1208951.8313
42 | 2663318.8005 | 1208970.0389 | 2663320.6684 | 1208970.9891 | 2663322.4045 | 1208971.4411 | 2663326.7675 | 1208971.4874 | 2663330.4986 | 1208970.9155 | 2663334.1556 | 1208969.4236
43 | 2663351.8875 | 1208951.8313 | 2663343.7546 | 1208957.4925 | 2663341.3084 | 1208959.7893
44 | 2663332.2376 | 1209183.074 | 2663333.5072 | 1209185.2109
45 | 2663221.9506 | 1209146.5717 | 2663220.6319 | 1209145.4793 | 2663225.279 | 1209114.4096 | 2663226.7708 | 1209106.3428 | 2663226.7708 | 1209106.3428
46 | 2663298.1924 | 1209139.0862 | 2663281.1983 | 1209145.8792
47 | 2663152.6553 | 1209182.2377 | 2663162.3113 | 1209192.1236
48 | 2663152.6553 | 1209182.2377 | 2663154.4093 | 1209180.2773 | 2663154.8242 | 1209176.2681 | 2663154.3827 | 1209155.4781
49 | 2663152.6553 | 1209182.2377 | 2663146.45 | 1209173.0994
50 | 2663175.3728 | 1209183.3454 | 2663178.7029 | 1209167.8786
51 | 2663154.3827 | 1209155.4781 | 2663154.2865 | 1209150.9471 | 2663155.0883 | 1209142.6447
52 | 2663130.4851 | 1209130.9306 | 2663129.2857 | 1209132.8494 | 2663127.9194 | 1209137.6824 | 2663128.2439 | 1209144.3787 | 2663131.6222 | 1209151.2631 | 2663146.45 | 1209173.0994
53 | 2663180.985 | 1209157.2792 | 2663178.7029 | 1209167.8786
54 | 2663155.7464 | 1209135.8311 | 2663155.0883 | 1209142.6447
55 | 2663130.4851 | 1209130.9306 | 2663131.4122 | 1209129.4476 | 2663145.1108 | 1209116.4755
56 | 2663180.985 | 1209157.2792 | 2663186.1657 | 1209133.2171
57 | 2663145.1108 | 1209116.4755 | 2663159.5131 | 1209102.8371
58 | 2663332.2376 | 1209183.074 | 2663327.9982 | 1209184.9968 | 2663317.0431 | 1209189.2801
59 | 2663332.2376 | 1209183.074 | 2663356.133 | 1209164.1605 | 2663357.8613 | 1209162.4778 | 2663357.753 | 1209160.5088 | 2663351.9633 | 1209146.2561
60 | 2663072.4794 | 1208918.5109 | 2663073.4643 | 1208913.6486 | 2663084.4097 | 1208890.7948 | 2663090.2676 | 1208876.726 | 2663092.5992 | 1208868.3122 | 2663093.1783 | 1208861.7143 | 2663092.9238 | 1208857.031 | 2663090.2612 | 1208848.5755 | 2663085.1911 | 1208836.1003
61 | 2663083.7039 | 1208832.4408 | 2663085.1911 | 1208836.1003
62 | 2663072.4794 | 1208918.5109 | 2663072.0687 | 1208920.538 | 2663072.3383 | 1208934.5938 | 2663072.5148 | 1208943.5976
63 | 2663072.5148 | 1208943.5976 | 2663073.0149 | 1208969.1108 | 2663075.4507 | 1208973.8394 | 2663080.5583 | 1208975.3721 | 2663112.0364 | 1208976.9724 | 2663157.2665 | 1208981.4535 | 2663163.6663 | 1208983.7114 | 2663166.0891 | 1208986.0718 | 2663167.9822 | 1208989.6496 | 2663168.1041 | 1208993.2086 | 2663167.6501 | 1208997.3174 | 2663165.9868 | 1209000.0459 | 2663162.7904 | 1209003.97 | 2663158.5205 | 1209007.338 | 2663152.5506 | 1209011.8665 | 2663133.9683 | 1209022.2207 | 2663114.6875 | 1209037.5261 | 2663110.5907 | 1209041.5644
64 | 2663110.5907 | 1209041.5644 | 2663105.0236 | 1209047.0519 | 2663101.6069 | 1209053.1195 | 2663101.7296 | 1209060.9255 | 2663103.4794 | 1209065.8359 | 2663108.048 | 1209070.8761 | 2663112.8921 | 1209072.873 | 2663119.7555 | 1209073.6905 | 2663126.2736 | 1209072.6323
65 | 2663157.6201 | 1209058.5387 | 2663146.776 | 1209064.0259 | 2663129.7844 | 1209072.0622 | 2663126.2736 | 1209072.6323
66 | 2663298.1924 | 1209139.0862 | 2663315.1572 | 1209132.2341
67 | 2663315.1572 | 1209132.2341 | 2663329.6008 | 1209126.4004 | 2663337.4744 | 1209123.7157 | 2663347.6651 | 1209121.1409
68 | 2663365.1681 | 1209117.9616 | 2663356.9416 | 1209118.797 | 2663347.6651 | 1209121.1409
69 | 2663282.9358 | 1209100.3564 | 2663288.8735 | 1209097.9027
70 | 2663282.9358 | 1209100.3564 | 2663282.6983 | 1209099.8203 | 2663282.2971 | 1209098.9377 | 2663277.9124 | 1209101.2938
71 | 2663288.8735 | 1209097.9027 | 2663297.756 | 1209094.2321 | 2663312.2237 | 1209088.3708 | 2663314.4777 | 1209087.8196
72 | 2663277.9124 | 1209101.2938 | 2663272.8015 | 1209104.0402 | 2663266.3568 | 1209108.1838
73 | 2663365.1681 | 1209117.9616 | 2663372.0446 | 1209117.5455 | 2663374.0014 | 1209117.9665
74 | 2663357.9413 | 1209079.7839 | 2663358.8124 | 1209084.3738 | 2663359.1721 | 1209086.2898 | 2663360.1081 | 1209091.2139 | 2663360.2232 | 1209091.8266 | 2663360.6764 | 1209094.244 | 2663364.0956 | 1209112.2912 | 2663364.6859 | 1209115.4105 | 2663365.1681 | 1209117.9616
75 | 2663314.6715 | 1209087.7722 | 2663314.4777 | 1209087.8196
76 | 2663232.1848 | 1209097.2029 | 2663231.3953 | 1209098.209 | 2663226.7708 | 1209106.3428
77 | 2663264.7412 | 1209070.5677 | 2663251.5199 | 1209074.3077 | 2663247.8167 | 1209077.2814 | 2663232.1848 | 1209097.2029
78 | 2663305.8999 | 1209036.7515 | 2663288.0606 | 1209037.428
79 | 2663305.8999 | 1209036.7515 | 2663307.0852 | 1209036.7065
80 | 2663307.0852 | 1209036.7065 | 2663310.4894 | 1209036.5774
81 | 2663328.537 | 1209035.8929 | 2663310.4894 | 1209036.5774
82 | 2663338.9139 | 1209035.4994 | 2663328.537 | 1209035.8929
83 | 2663338.9139 | 1209035.4994 | 2663339.3816 | 1209035.4816
84 | 2663357.9413 | 1209079.7839 | 2663343.5427 | 1209081.5746
85 | 2663357.9413 | 1209079.7839 | 2663372.5244 | 1209080.0737
86 | 2663343.5427 | 1209081.5746 | 2663343.4955 | 1209081.5805
87 | 2663372.5244 | 1209080.0737 | 2663372.6334 | 1209080.0759
88 | 2663343.4955 | 1209081.5805 | 2663343.457 | 1209081.5853
89 | 2663372.6334 | 1209080.0759 | 2663372.7379 | 1209080.0779
90 | 2663375.0671 | 1209034.8475 | 2663371.4315 | 1209034.2661 | 2663361.6439 | 1209034.6373
91 | 2663375.0671 | 1209034.8475 | 2663377.0852 | 1209035.1703
92 | 2663361.6439 | 1209034.6373 | 2663344.7329 | 1209035.2787
93 | 2663377.0852 | 1209035.1703 | 2663377.3889 | 1209035.2188 | 2663382.6324 | 1209037.5426 | 2663386.7702 | 1209041.6112 | 2663388.9166 | 1209046.0021
94 | 2663339.3816 | 1209035.4816 | 2663344.7329 | 1209035.2787
95 | 2663391.4232 | 1209054.4446 | 2663389.8951 | 1209048.0038 | 2663388.9166 | 1209046.0021
96 | 2663397.6223 | 1209080.5723 | 2663391.4232 | 1209054.4446
97 | 2663397.6223 | 1209080.5723 | 2663372.7379 | 1209080.0779
98 | 2663318.8005 | 1208970.0389 | 2663316.9408 | 1208969.0928 | 2663313.9156 | 1208966.1812 | 2663311.8411 | 1208963.2352 | 2663310.3773 | 1208960.0511 | 2663309.664 | 1208955.6297 | 2663310.9006 | 1208948.7053 | 2663312.634 | 1208945.833 | 2663314.2779 | 1208943.8423
99 | 2663186.1657 | 1209133.2171 | 2663188.5173 | 1209122.2951
100 | 2663190.0087 | 1209115.3684 | 2663188.5173 | 1209122.2951
101 | 2663191.5723 | 1209108.106 | 2663190.0087 | 1209115.3684
102 | 2663193.3137 | 1209100.018 | 2663191.5723 | 1209108.106
103 | 2663314.2779 | 1208943.8423 | 2663330.7778 | 1208923.8624
104 | 2663332.6711 | 1208921.5699 | 2663330.7778 | 1208923.8624
105 | 2663332.7743 | 1208921.4449 | 2663332.6711 | 1208921.5699
106 | 2663322.8817 | 1208872.0414 | 2663334.6831 | 1208873.2006 | 2663345.2707 | 1208873.4019 | 2663367.6477 | 1208870.1708 | 2663370.7646 | 1208870.1705 | 2663373.289 | 1208870.8422 | 2663375.4425 | 1208872.0769 | 2663376.8021 | 1208873.6145 | 2663378.282 | 1208877.4325 | 2663378.3208 | 1208879.5008 | 2663377.7826 | 1208881.5075 | 2663376.2315 | 1208883.6812 | 2663372.23 | 1208886.8073 | 2663356.6247 | 1208896.6476 | 2663349.2057 | 1208902.3168 | 2663345.5637 | 1208905.9581 | 2663332.7743 | 1208921.4449
107 | 2663371.0895 | 1208866.783 | 2663343.4839 | 1208871.2817 | 2663322.9691 | 1208870.2523 | 2663322.8817 | 1208872.0414
108 | 2663371.0895 | 1208866.783 | 2663365.4974 | 1208859.3303 | 2663361.724 | 1208850.9963 | 2663361.594 | 1208846.0585 | 2663364.3141 | 1208841.1845 | 2663369.7453 | 1208837.3064 | 2663384.2255 | 1208833.191 | 2663423.8101 | 1208821.0373 | 2663432.1588 | 1208816.6011 | 2663436.6203 | 1208811.69 | 2663437.9839 | 1208807.8577
109 | 2663437.9839 | 1208807.8577 | 2663435.4787 | 1208801.0825 | 2663432.1664 | 1208797.3006 | 2663425.6497 | 1208795.2968 | 2663400.2036 | 1208794.0035 | 2663380.0382 | 1208792.255 | 2663363.8506 | 1208788.9034 | 2663355.703 | 1208785.1368 | 2663350.4468 | 1208781.8457 | 2663321.9739 | 1208754.138 | 2663317.9487 | 1208745.8791 | 2663317.6601 | 1208738.6939 | 2663320.0223 | 1208719.5518 | 2663325.1436 | 1208700.4612 | 2663325.432 | 1208692.6262 | 2663321.6427 | 1208686.4934 | 2663316.0564 | 1208682.0537 | 2663309.0075 | 1208680.0444 | 2663288.2564 | 1208674.71 | 2663259.6834 | 1208666.4133 | 2663246.7789 | 1208662.4075 | 2663241.8002 | 1208660.1756 | 2663237.6586 | 1208657.8637 | 2663234.323 | 1208654.8154 | 2663231.646 | 1208651.3182 | 2663229.914 | 1208646.8861 | 2663229.7178 | 1208645.1384
110 | 2663170.8404 | 1209051.849 | 2663190.2977 | 1209042.0033
111 | 2663170.8404 | 1209051.849 | 2663157.6201 | 1209058.5387
112 | 2663190.2977 | 1209042.0033 | 2663197.0278 | 1209038.5978 | 2663203.3958 | 1209038.1094 | 2663209.1667 | 1209040.1606 | 2663211.8179 | 1209044.647 | 2663211.8488 | 1209051.0512 | 2663209.506 | 1209055.4957 | 2663200.5681 | 1209063.9596
113 | 2663174.4213 | 1209088.7196 | 2663200.5681 | 1209063.9596
114 | 2663174.4213 | 1209088.7196 | 2663159.5131 | 1209102.8371
115 | 2663314.8728 | 1209087.723 | 2663314.6715 | 1209087.7722
116 | 2663315.0651 | 1209087.6759 | 2663314.8728 | 1209087.723
117 | 2663343.4082 | 1209081.5913 | 2663336.3615 | 1209082.4677 | 2663315.0651 | 1209087.6759
118 | 2663343.457 | 1209081.5853 | 2663343.4082 | 1209081.5913

## bus_geodata
| x | y | coords
0 | 2663226.0268 | 1209249.4102
1 | 2663263.0988 | 1209269.1932
2 | 2663277.3685 | 1209276.938
3 | 2663195.9247 | 1209208.0446
4 | 2663231.5934 | 1209234.4494
5 | 2663213.449 | 1209179.8463
6 | 2663178.7827 | 1209203.1058
7 | 2663248.1269 | 1209235.1806
8 | 2663238.1262 | 1209221.9777
9 | 2663257.3905 | 1209245.485
10 | 2663215.3832 | 1209246.532
11 | 2663279.2805 | 1209278.715
12 | 2663247.4634 | 1209216.7138
13 | 2663212.321 | 1209170.8984
14 | 2663355.8852 | 1209238.3251
15 | 2663379.3216 | 1209242.5765
16 | 2663353.3705 | 1209220.8817
17 | 2663426.3926 | 1209177.3701
18 | 2663413.8784 | 1209188.2549
19 | 2663446.9698 | 1209181.6946
20 | 2663427.1984 | 1209166.8878
21 | 2663377.4708 | 1209179.328
22 | 2663292.2558 | 1209274.7755
23 | 2663386.8321 | 1209241.8558
24 | 2663362.9609 | 1209270.6754
25 | 2663219.4228 | 1209170.6262
26 | 2663214.3028 | 1209164.5461
27 | 2663247.6396 | 1209159.3017
28 | 2663180.3842 | 1209280.289
29 | 2663172.0148 | 1209198.9527
30 | 2663293.3655 | 1209198.5378
31 | 2663351.8122 | 1209207.8356
32 | 2663470.1085 | 1209111.0833
33 | 2663385.2254 | 1208945.8811
34 | 2663385.2554 | 1208943.0575
35 | 2663334.1556 | 1208969.4236
36 | 2663351.8875 | 1208951.8313
37 | 2663333.5072 | 1209185.211
38 | 2663221.9506 | 1209146.5717
39 | 2663281.1983 | 1209145.8792
40 | 2663286.3499 | 1209180.7543
41 | 2663162.3113 | 1209192.1236
42 | 2663152.6553 | 1209182.2377
43 | 2663175.3728 | 1209183.3454
44 | 2663154.3827 | 1209155.4781
45 | 2663146.45 | 1209173.0994
46 | 2663178.7029 | 1209167.8786
47 | 2663155.0883 | 1209142.6447
48 | 2663130.4851 | 1209130.9306
49 | 2663180.985 | 1209157.2792
50 | 2663155.7464 | 1209135.8311
51 | 2663145.1108 | 1209116.4755
52 | 2663332.2376 | 1209183.074
53 | 2663317.0431 | 1209189.2801
54 | 2663351.9633 | 1209146.2561
55 | 2663085.1911 | 1208836.1003
56 | 2663072.4794 | 1208918.5109
57 | 2663083.7039 | 1208832.4408
58 | 2663072.5148 | 1208943.5976
59 | 2663110.5907 | 1209041.5644
60 | 2663126.2736 | 1209072.6323
61 | 2663298.1924 | 1209139.0862
62 | 2663315.1572 | 1209132.2341
63 | 2663347.6651 | 1209121.1409
64 | 2663282.9358 | 1209100.3564
65 | 2663288.8735 | 1209097.9027
66 | 2663277.9124 | 1209101.2938
67 | 2663365.1681 | 1209117.9616
68 | 2663314.4777 | 1209087.8196
69 | 2663226.7708 | 1209106.3428
70 | 2663266.3568 | 1209108.1838
71 | 2663232.1848 | 1209097.2029
72 | 2663264.7412 | 1209070.5677
73 | 2663305.8999 | 1209036.7515
74 | 2663288.0606 | 1209037.428
75 | 2663307.0852 | 1209036.7065
76 | 2663310.4894 | 1209036.5774
77 | 2663328.537 | 1209035.8929
78 | 2663338.9139 | 1209035.4994
79 | 2663374.0014 | 1209117.9665
80 | 2663357.9413 | 1209079.7839
81 | 2663343.5427 | 1209081.5746
82 | 2663372.5244 | 1209080.0737
83 | 2663343.4955 | 1209081.5805
84 | 2663372.6334 | 1209080.0759
85 | 2663375.0671 | 1209034.8475
86 | 2663361.6439 | 1209034.6373
87 | 2663377.0852 | 1209035.1703
88 | 2663344.7329 | 1209035.2787
89 | 2663388.9166 | 1209046.0021
90 | 2663339.3816 | 1209035.4816
91 | 2663391.4232 | 1209054.4446
92 | 2663397.6223 | 1209080.5723
93 | 2663372.7379 | 1209080.0779
94 | 2663318.8005 | 1208970.0389
95 | 2663341.3084 | 1208959.7893
96 | 2663186.1657 | 1209133.2171
97 | 2663188.5173 | 1209122.2951
98 | 2663190.0087 | 1209115.3684
99 | 2663191.5723 | 1209108.106
100 | 2663193.3137 | 1209100.018
101 | 2663314.2779 | 1208943.8423
102 | 2663330.7778 | 1208923.8624
103 | 2663332.6711 | 1208921.5699
104 | 2663332.7743 | 1208921.4449
105 | 2663322.8817 | 1208872.0414
106 | 2663371.0895 | 1208866.783
107 | 2663437.9839 | 1208807.8577
108 | 2663170.8404 | 1209051.849
109 | 2663190.2977 | 1209042.0033
110 | 2663157.6201 | 1209058.5387
111 | 2663200.5681 | 1209063.9596
112 | 2663174.4213 | 1209088.7196
113 | 2663159.5131 | 1209102.8371
114 | 2663314.6715 | 1209087.7722
115 | 2663229.7178 | 1208645.1384
116 | 2663314.8728 | 1209087.723
117 | 2663315.0651 | 1209087.6759
118 | 2663343.457 | 1209081.5853
119 | 2663343.4082 | 1209081.5913
120 | 2663298.1924 | 1209139.0862

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98018 | -0.37979 | 0.010669 | 0.002674
1 | 0.98071 | -0.36937 | 0 | 0
2 | 0.98092 | -0.36519 | 0 | 0
3 | 0.98646 | -0.25768 | 0 | 0
4 | 0.98295 | -0.32568 | 0 | 0
5 | 0.9903 | -0.18402 | 0 | 0
6 | 0.9859 | -0.26856 | 0.002827 | 0.00070852
7 | 0.98188 | -0.34642 | 0 | 0
8 | 0.98097 | -0.36422 | 0 | 0
9 | 0.9815 | -0.3538 | 0.012402 | 0.0031082
10 | 0.98257 | -0.33315 | 0.011078 | 0.0027764
11 | 0.98091 | -0.36548 | 0 | 0
12 | 0.98038 | -0.37561 | 0.0085929 | 0.0021536
13 | 0.99123 | -0.16614 | 0.0035806 | 0.00089739
14 | 0.97378 | -0.50512 | 0 | 0
15 | 0.97283 | -0.52395 | 0 | 0
16 | 0.97428 | -0.4952 | 0.022805 | 0.0057154
17 | 0.97425 | -0.49603 | 0 | 0
18 | 0.97446 | -0.49175 | 0 | 0
19 | 0.97404 | -0.50016 | 0.010658 | 0.0026712
20 | 0.9742 | -0.49704 | 0.01662 | 0.0041654
21 | 0.97504 | -0.48044 | 0.015583 | 0.0039056
22 | 0.98083 | -0.36708 | 0.0062084 | 0.001556
23 | 0.97276 | -0.52527 | 0.0095129 | 0.0023842
24 | 0.97207 | -0.53886 | 0.020935 | 0.0052467
25 | 0.99279 | -0.13647 | 0 | 0
26 | 0.99191 | -0.15327 | 0 | 0
27 | 0.99602 | -0.075146 | 0.013147 | 0.0032949
28 | 0.98215 | -0.34136 | 0.0093332 | 0.0023391
29 | 0.98566 | -0.27321 | 0.0016078 | 0.00040296
30 | 0.97786 | -0.42494 | 0 | 0
31 | 0.97494 | -0.48236 | 0.012924 | 0.0032391
32 | 0.97381 | -0.50464 | 0 | 0
33 | 0.97235 | -0.53363 | 0 | 0
34 | 0.97234 | -0.53385 | 0 | 0
35 | 0.97211 | -0.5384 | 0.002055 | 0.00051503
36 | 0.9722 | -0.53656 | 0.0020535 | 0.00051465
37 | 0.97587 | -0.46404 | 0 | 0
38 | 0.9916 | -0.15914 | 0 | 0
39 | 1 | 0 | -0.47931 | -0.12287
40 | 0.97761 | -0.42987 | 0.014142 | 0.0035444
41 | 0.98539 | -0.27851 | 0.0033672 | 0.00084389
42 | 0.98508 | -0.28441 | 0 | 0
43 | 0.98534 | -0.2794 | 0 | 0
44 | 0.985 | -0.28602 | 0.0011041 | 0.00027672
45 | 0.98485 | -0.28891 | 0.0016045 | 0.00040211
46 | 0.98503 | -0.28554 | 0.0015439 | 0.00038694
47 | 0.98497 | -0.28651 | 0.0010692 | 0.00026797
48 | 0.98386 | -0.30806 | 0.0012785 | 0.00032041
49 | 0.98483 | -0.28945 | 0.0020822 | 0.00052185
50 | 0.98497 | -0.28664 | 0.0010783 | 0.00027024
51 | 0.98344 | -0.31613 | 0.00097147 | 0.00024347
52 | 0.97596 | -0.46213 | 0 | 0
53 | 0.97667 | -0.44824 | 0.011985 | 0.0030036
54 | 0.9754 | -0.47334 | 0.01219 | 0.0030552
55 | 0.97059 | -0.56804 | 0.00465 | 0.0011654
56 | 0.9714 | -0.55214 | 0.0030095 | 0.00075425
57 | 0.97057 | -0.56841 | 0.005127 | 0.001285
58 | 0.9717 | -0.54621 | 0.0016363 | 0.00041009
59 | 0.9745 | -0.49099 | 0.0063565 | 0.0015931
60 | 0.97553 | -0.47066 | 0.0055723 | 0.0013966
61 | 0.9981 | -0.036152 | 0 | 0
62 | 0.9962 | -0.072432 | 0.013373 | 0.0033515
63 | 0.99305 | -0.1329 | 0.013586 | 0.0034051
64 | 0.98763 | -0.23782 | 0 | 0
65 | 0.98769 | -0.23665 | 0.0042991 | 0.0010775
66 | 0.98757 | -0.23901 | 0.0031533 | 0.00079028
67 | 0.99164 | -0.1601 | 0 | 0
68 | 0.98805 | -0.22951 | 0.0018949 | 0.0004749
69 | 0.991 | -0.17072 | 0.0031996 | 0.0008019
70 | 0.98748 | -0.24071 | 0.0070551 | 0.0017682
71 | 0.99088 | -0.1731 | 0.0061576 | 0.0015432
72 | 0.99062 | -0.17812 | 0.0064457 | 0.0016155
73 | 0.98442 | -0.30016 | 0.0018959 | 0.00047515
74 | 0.98428 | -0.30288 | 0.008484 | 0.0021263
75 | 0.98443 | -0.29994 | 0.0018918 | 0.00047412
76 | 0.98447 | -0.29919 | 0.0035918 | 0.0009002
77 | 0.98474 | -0.29403 | 0.0030323 | 0.00075998
78 | 0.98492 | -0.29051 | 0.0018713 | 0.000469
79 | 0.99153 | -0.16225 | 0.013653 | 0.0034217
80 | 0.98905 | -0.21016 | 0 | 0
81 | 0.98866 | -0.21782 | 0.0018747 | 0.00046984
82 | 0.98847 | -0.22132 | 0.0018046 | 0.00045228
83 | 0.98865 | -0.21784 | 0.0018747 | 0.00046984
84 | 0.98847 | -0.2214 | 0.0018026 | 0.00045178
85 | 0.98581 | -0.27312 | 0.001802 | 0.00045163
86 | 0.98545 | -0.28015 | 0.0027381 | 0.00068624
87 | 0.98587 | -0.27199 | 0.0030179 | 0.00075636
88 | 0.98504 | -0.28815 | 0.0036969 | 0.00092652
89 | 0.98639 | -0.26182 | 0.0018046 | 0.00045228
90 | 0.98492 | -0.29033 | 0.0018755 | 0.00047004
91 | 0.98668 | -0.25616 | 0.0018026 | 0.00045178
92 | 0.98761 | -0.23815 | 0 | 0
93 | 0.98847 | -0.22148 | 0.001802 | 0.00045163
94 | 0.97206 | -0.5395 | 0.0017758 | 0.00044505
95 | 0.97218 | -0.53708 | 0.002117 | 0.00053058
96 | 0.98442 | -0.2974 | 0.010584 | 0.0026525
97 | 0.98434 | -0.29889 | 0.0013349 | 0.00033456
98 | 0.9843 | -0.29966 | 0.0014042 | 0.00035194
99 | 0.98427 | -0.30028 | 0.0014517 | 0.00036384
100 | 0.98425 | -0.30076 | 0.0031996 | 0.0008019
101 | 0.97197 | -0.54129 | 0.0035851 | 0.00089851
102 | 0.97192 | -0.54222 | 0.0012464 | 0.00031238
103 | 0.97192 | -0.5423 | 0.0016219 | 0.0004065
104 | 0.97192 | -0.54231 | 0.0020771 | 0.00052057
105 | 0.97188 | -0.54299 | 0.00057967 | 0.00014528
106 | 0.97188 | -0.54308 | 0 | 0
107 | 0.97187 | -0.54329 | 0 | 0
108 | 0.97694 | -0.44308 | 0.0028176 | 0.00070615
109 | 0.97781 | -0.4259 | 0.014739 | 0.003694
110 | 0.97638 | -0.45401 | 0.014002 | 0.0035092
111 | 0.98045 | -0.37429 | 0.0018698 | 0.00046861
112 | 0.98245 | -0.33533 | 0.0025481 | 0.00063861
113 | 0.98305 | -0.32378 | 0.0018494 | 0.0004635
114 | 0.98806 | -0.22945 | 0.0018941 | 0.0004747
115 | 0.97185 | -0.54382 | 0.00026358 | 6.606e-05
116 | 0.98806 | -0.22939 | 0.0018941 | 0.0004747
117 | 0.98806 | -0.22932 | 0.0018931 | 0.00047445
118 | 0.98865 | -0.21786 | 0.0018747 | 0.00046984
119 | 0.98865 | -0.21788 | 0.0018743 | 0.00046975
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010669 | -0.002674 | 0.010675 | 0.0026767 | 5.3003e-06 | 2.7128e-06 | 0.016197 | 0.016197 | 0.016197 | 0.98018 | -0.37979 | 0.98071 | -0.36937 | 4.4498
1 | -0.010675 | -0.0026767 | 0.010677 | 0.0026778 | 2.1258e-06 | 1.0878e-06 | 0.016197 | 0.016197 | 0.016197 | 0.98071 | -0.36937 | 0.98092 | -0.36519 | 4.4498
2 | 0.006209 | 0.0015561 | -0.0062089 | -0.0015561 | 8.6694e-08 | 2.2588e-08 | 0.0094187 | 0.0094188 | 0.0094188 | 0.98092 | -0.36519 | 0.98091 | -0.36548 | 2.5876
3 | -0.016886 | -0.0042339 | 0.016895 | 0.0042393 | 9.1687e-06 | 5.3973e-06 | 0.025616 | 0.025616 | 0.025616 | 0.98092 | -0.36519 | 0.9815 | -0.3538 | 7.0373
4 | 0.22517 | 0.057217 | -0.22444 | -0.056748 | 0.00073463 | 0.00046822 | 0.33994 | 0.33994 | 0.33994 | 0.98646 | -0.25768 | 0.98295 | -0.32568 | 31.1302
5 | -0.32656 | -0.082886 | 0.32772 | 0.083628 | 0.0011617 | 0.00074201 | 0.49297 | 0.49297 | 0.49297 | 0.98646 | -0.25768 | 0.9903 | -0.18402 | 45.1439
6 | 0.10139 | 0.025669 | -0.10134 | -0.025636 | 5.2964e-05 | 3.3204e-05 | 0.15303 | 0.15303 | 0.15303 | 0.98646 | -0.25768 | 0.9859 | -0.26856 | 14.0138
7 | 0.020422 | 0.0051216 | -0.020415 | -0.0051172 | 7.2662e-06 | 4.3935e-06 | 0.030917 | 0.030917 | 0.030917 | 0.98295 | -0.32568 | 0.98257 | -0.33315 | 8.4936
8 | 0.20402 | 0.051627 | -0.20381 | -0.051498 | 0.00020288 | 0.0001292 | 0.30902 | 0.30902 | 0.30902 | 0.98295 | -0.32568 | 0.98188 | -0.34642 | 28.299
9 | -0.32772 | -0.083628 | 0.32801 | 0.083809 | 0.00028324 | 0.00018091 | 0.49297 | 0.49297 | 0.49297 | 0.9903 | -0.18402 | 0.99123 | -0.16614 | 45.1438
10 | 0.098508 | 0.024927 | -0.098486 | -0.024914 | 2.1966e-05 | 1.3755e-05 | 0.14876 | 0.14876 | 0.14876 | 0.9859 | -0.26856 | 0.98566 | -0.27321 | 13.6231
11 | 0.17451 | 0.044144 | -0.17436 | -0.044049 | 0.00014888 | 9.464e-05 | 0.26461 | 0.26461 | 0.26461 | 0.98188 | -0.34642 | 0.98097 | -0.36422 | 24.2315
12 | 0.029307 | 0.0073539 | -0.029297 | -0.0073475 | 1.0307e-05 | 6.4204e-06 | 0.044417 | 0.044417 | 0.044417 | 0.98188 | -0.34642 | 0.9815 | -0.3538 | 12.2026
13 | 0.17436 | 0.044049 | -0.17426 | -0.043989 | 9.5135e-05 | 6.0475e-05 | 0.26461 | 0.26461 | 0.26461 | 0.98097 | -0.36422 | 0.98038 | -0.37561 | 24.2315
14 | 0.0093368 | 0.0023408 | -0.0093332 | -0.0023391 | 3.6514e-06 | 1.7204e-06 | 0.01414 | 0.01414 | 0.01414 | 0.98257 | -0.33315 | 0.98215 | -0.34136 | 3.8847
15 | 0.0062089 | 0.0015561 | -0.0062084 | -0.001556 | 4.7412e-07 | 1.2355e-07 | 0.0094188 | 0.0094188 | 0.0094188 | 0.98091 | -0.36548 | 0.98083 | -0.36708 | 2.5876
16 | 0.16567 | 0.041835 | -0.16528 | -0.041587 | 0.00039055 | 0.00024809 | 0.25157 | 0.25157 | 0.25157 | 0.98038 | -0.37561 | 0.97786 | -0.42494 | 23.0372
17 | -0.33159 | -0.084706 | 0.33179 | 0.084838 | 0.00020657 | 0.00013195 | 0.49835 | 0.49835 | 0.49835 | 0.99123 | -0.16614 | 0.99191 | -0.15327 | 45.636
18 | 0.030491 | 0.0076573 | -0.030463 | -0.0076402 | 2.7369e-05 | 1.7099e-05 | 0.046598 | 0.046598 | 0.046598 | 0.97378 | -0.50512 | 0.97283 | -0.52395 | 12.8016
19 | -0.030491 | -0.0076573 | 0.030505 | 0.0076664 | 1.4436e-05 | 9.0184e-06 | 0.046598 | 0.046598 | 0.046598 | 0.97378 | -0.50512 | 0.97428 | -0.4952 | 12.8016
20 | 0.0095135 | 0.0023845 | -0.0095129 | -0.0023842 | 5.9738e-07 | 2.8893e-07 | 0.014552 | 0.014552 | 0.014552 | 0.97283 | -0.52395 | 0.97276 | -0.52527 | 3.9977
21 | 0.02095 | 0.0052558 | -0.020935 | -0.0052467 | 1.4884e-05 | 9.0465e-06 | 0.032046 | 0.032046 | 0.032046 | 0.97283 | -0.52395 | 0.97207 | -0.53886 | 8.8039
22 | -0.05331 | -0.013382 | 0.053342 | 0.013403 | 3.2668e-05 | 2.0744e-05 | 0.081427 | 0.081427 | 0.081427 | 0.97428 | -0.4952 | 0.97494 | -0.48236 | 22.3701
23 | -0.01066 | -0.0026723 | 0.010663 | 0.0026734 | 2.1758e-06 | 1.1199e-06 | 0.016282 | 0.016282 | 0.016282 | 0.97425 | -0.49603 | 0.97446 | -0.49175 | 4.4732
24 | 0.01066 | 0.0026723 | -0.010658 | -0.0026712 | 2.0933e-06 | 1.0776e-06 | 0.016282 | 0.016283 | 0.016283 | 0.97425 | -0.49603 | 0.97404 | -0.50016 | 4.4732
25 | 0.034039 | 0.0085066 | -0.034031 | -0.0085021 | 8.5598e-06 | 4.5309e-06 | 0.051969 | 0.05197 | 0.05197 | 0.97446 | -0.49175 | 0.9742 | -0.49704 | 4.7591
26 | -0.044702 | -0.01118 | 0.044726 | 0.011194 | 2.4056e-05 | 1.3851e-05 | 0.068252 | 0.068251 | 0.068252 | 0.97446 | -0.49175 | 0.97504 | -0.48044 | 6.2502
27 | 0.017411 | 0.0043367 | -0.017404 | -0.0043354 | 6.2728e-06 | 1.3633e-06 | 0.026584 | 0.026585 | 0.026585 | 0.9742 | -0.49704 | 0.97381 | -0.50464 | 2.4345
28 | -0.060309 | -0.015099 | 0.060356 | 0.015128 | 4.7115e-05 | 2.8487e-05 | 0.092033 | 0.092033 | 0.092033 | 0.97504 | -0.48044 | 0.97587 | -0.46404 | 8.428
29 | 0.3479 | 0.088988 | -0.34761 | -0.088807 | 0.00028255 | 0.00018051 | 0.52208 | 0.52208 | 0.52208 | 0.99279 | -0.13647 | 0.99191 | -0.15327 | 47.8093
30 | -0.3479 | -0.088988 | 0.34893 | 0.08965 | 0.0010359 | 0.00066179 | 0.52208 | 0.52208 | 0.52208 | 0.99279 | -0.13647 | 0.99602 | -0.075146 | 47.8093
31 | 0.015819 | 0.0039694 | -0.015815 | -0.0039668 | 4.4271e-06 | 2.5629e-06 | 0.023733 | 0.023733 | 0.023733 | 0.99191 | -0.15327 | 0.9916 | -0.15914 | 6.52
32 | -0.36208 | -0.092944 | 0.3634 | 0.093792 | 0.0013258 | 0.00084711 | 0.54172 | 0.54172 | 0.54172 | 0.99602 | -0.075146 | 1 | 0 | 49.6079
33 | 0.021624 | 0.0054277 | -0.021618 | -0.0054239 | 6.382e-06 | 3.881e-06 | 0.032649 | 0.032649 | 0.032649 | 0.98566 | -0.27321 | 0.98534 | -0.2794 | 8.9694
34 | 0.075254 | 0.019083 | -0.075235 | -0.019071 | 1.917e-05 | 1.1816e-05 | 0.11369 | 0.11369 | 0.11369 | 0.98566 | -0.27321 | 0.98539 | -0.27851 | 10.411
35 | 0.014146 | 0.0035463 | -0.014142 | -0.0035444 | 3.3218e-06 | 1.8862e-06 | 0.021526 | 0.021526 | 0.021526 | 0.97786 | -0.42494 | 0.97761 | -0.42987 | 5.9137
36 | 0.15113 | 0.038041 | -0.15097 | -0.037934 | 0.00016817 | 0.00010667 | 0.23004 | 0.23004 | 0.23004 | 0.97786 | -0.42494 | 0.97667 | -0.44824 | 21.066
37 | -0.066266 | -0.016642 | 0.066324 | 0.016678 | 5.796e-05 | 3.634e-05 | 0.10115 | 0.10115 | 0.10115 | 0.97494 | -0.48236 | 0.97587 | -0.46404 | 13.8946
38 | 0.017404 | 0.0043354 | -0.01738 | -0.0043301 | 2.3912e-05 | 5.2178e-06 | 0.026585 | 0.026588 | 0.026588 | 0.97381 | -0.50464 | 0.97235 | -0.53363 | 2.4348
39 | 0.0041712 | 0.001045 | -0.0041711 | -0.001045 | 4.3148e-08 | -7.4134e-09 | 0.0063831 | 0.0063831 | 0.0063831 | 0.97235 | -0.53363 | 0.97234 | -0.53385 | 1.7536
40 | 0.013209 | 0.0032851 | -0.013206 | -0.0032854 | 2.9798e-06 | -2.6512e-07 | 0.020205 | 0.020206 | 0.020206 | 0.97235 | -0.53363 | 0.97211 | -0.5384 | 1.8504
41 | 0.0041711 | 0.001045 | -0.0041706 | -0.0010451 | 5.384e-07 | -9.2427e-08 | 0.0063831 | 0.0063833 | 0.0063833 | 0.97234 | -0.53385 | 0.9722 | -0.53656 | 1.7536
42 | 0.011151 | 0.0027704 | -0.011151 | -0.0027706 | 5.813e-07 | -2.2218e-07 | 0.017061 | 0.017061 | 0.017061 | 0.97211 | -0.5384 | 0.97206 | -0.5395 | 1.5623
43 | 0.0021171 | 0.00053045 | -0.002117 | -0.00053058 | 5.2228e-08 | -1.3105e-07 | 0.0032403 | 0.0032403 | 0.0032403 | 0.9722 | -0.53656 | 0.97218 | -0.53708 | 0.8902
44 | -0.12668 | -0.031806 | 0.12669 | 0.031813 | 1.1588e-05 | 7.3232e-06 | 0.19318 | 0.19318 | 0.19318 | 0.97587 | -0.46404 | 0.97596 | -0.46213 | 17.6909
45 | 0.015815 | 0.0039668 | -0.015806 | -0.0039618 | 8.73e-06 | 5.0544e-06 | 0.023733 | 0.023733 | 0.023733 | 0.9916 | -0.15914 | 0.991 | -0.17072 | 6.5201
46 | 0.11426 | 0.029079 | -0.11406 | -0.028952 | 0.00019875 | 0.00012696 | 0.17018 | 0.17018 | 0.17018 | 1 | 0 | 0.9981 | -0.036152 | 46.7516
47 | 0.071868 | 0.018227 | -0.071847 | -0.018215 | 2.0374e-05 | 1.2512e-05 | 0.1086 | 0.1086 | 0.1086 | 0.98539 | -0.27851 | 0.98508 | -0.28441 | 9.9454
48 | 0.0032519 | 0.00081452 | -0.0032516 | -0.00081471 | 2.4842e-07 | -1.9052e-07 | 0.004912 | 0.0049121 | 0.0049121 | 0.98508 | -0.28441 | 0.985 | -0.28602 | 1.3495
49 | 0.068596 | 0.0174 | -0.068581 | -0.017391 | 1.4846e-05 | 9.0796e-06 | 0.10369 | 0.10369 | 0.10369 | 0.98508 | -0.28441 | 0.98485 | -0.28891 | 9.4956
50 | 0.021618 | 0.0054239 | -0.021612 | -0.00542 | 6.3242e-06 | 3.846e-06 | 0.032649 | 0.032649 | 0.032649 | 0.98534 | -0.2794 | 0.98503 | -0.28554 | 8.9694
51 | 0.0021475 | 0.00053799 | -0.0021475 | -0.00053812 | 5.0807e-08 | -1.3134e-07 | 0.0032441 | 0.0032442 | 0.0032442 | 0.985 | -0.28602 | 0.98497 | -0.28651 | 0.89126
52 | 0.066976 | 0.016989 | -0.066915 | -0.016951 | 6.1599e-05 | 3.7591e-05 | 0.10127 | 0.10127 | 0.10127 | 0.98485 | -0.28891 | 0.98386 | -0.30806 | 9.2737
53 | 0.020068 | 0.0050331 | -0.020064 | -0.0050308 | 3.7369e-06 | 2.2536e-06 | 0.030316 | 0.030316 | 0.030316 | 0.98503 | -0.28554 | 0.98483 | -0.28945 | 8.3287
54 | 0.0010783 | 0.00027015 | -0.0010783 | -0.00027024 | 6.8112e-09 | -8.2767e-08 | 0.0016289 | 0.0016289 | 0.0016289 | 0.98497 | -0.28651 | 0.98497 | -0.28664 | 0.44751
55 | 0.065636 | 0.016631 | -0.065611 | -0.016615 | 2.5427e-05 | 1.5488e-05 | 0.099335 | 0.099335 | 0.099335 | 0.98386 | -0.30806 | 0.98344 | -0.31613 | 9.0966
56 | 0.017982 | 0.004509 | -0.017975 | -0.0045049 | 6.8139e-06 | 4.0479e-06 | 0.02717 | 0.02717 | 0.02717 | 0.98483 | -0.28945 | 0.98442 | -0.2974 | 7.4644
57 | 0.064639 | 0.016372 | -0.064616 | -0.016357 | 2.3747e-05 | 1.4443e-05 | 0.097865 | 0.097866 | 0.097866 | 0.98344 | -0.31613 | 0.98305 | -0.32378 | 8.9621
58 | -0.13889 | -0.034872 | 0.13898 | 0.03493 | 9.2045e-05 | 5.8293e-05 | 0.21178 | 0.21178 | 0.21178 | 0.97596 | -0.46213 | 0.97667 | -0.44824 | 19.394
59 | 0.012197 | 0.0030588 | -0.01219 | -0.0030552 | 6.5162e-06 | 3.5429e-06 | 0.018597 | 0.018597 | 0.018597 | 0.97596 | -0.46213 | 0.9754 | -0.47334 | 5.1091
60 | -0.0097771 | -0.0024504 | 0.0097845 | 0.002454 | 7.4071e-06 | 3.6531e-06 | 0.014989 | 0.014989 | 0.014989 | 0.97059 | -0.56804 | 0.9714 | -0.55214 | 4.1179
61 | 0.0051271 | 0.001285 | -0.005127 | -0.001285 | 9.1524e-08 | 9.756e-09 | 0.0078604 | 0.0078604 | 0.0078604 | 0.97059 | -0.56804 | 0.97057 | -0.56841 | 2.1594
62 | -0.012794 | -0.0032083 | 0.012798 | 0.0032103 | 3.6201e-06 | 2.0057e-06 | 0.019599 | 0.019599 | 0.019599 | 0.9714 | -0.55214 | 0.9717 | -0.54621 | 5.3843
63 | -0.014434 | -0.0036204 | 0.014472 | 0.0036422 | 3.8088e-05 | 2.1794e-05 | 0.022105 | 0.022104 | 0.022105 | 0.9717 | -0.54621 | 0.9745 | -0.49099 | 6.0727
64 | -0.020829 | -0.0052352 | 0.020849 | 0.0052475 | 2.0246e-05 | 1.2292e-05 | 0.03181 | 0.03181 | 0.03181 | 0.9745 | -0.49099 | 0.97553 | -0.47066 | 8.7389
65 | -0.026421 | -0.0066441 | 0.026442 | 0.0066571 | 2.1025e-05 | 1.3025e-05 | 0.040309 | 0.040309 | 0.040309 | 0.97553 | -0.47066 | 0.97638 | -0.45401 | 11.0739
66 | 0.11406 | 0.028952 | -0.11386 | -0.028825 | 0.0001987 | 0.00012693 | 0.17018 | 0.17018 | 0.17018 | 0.9981 | -0.036152 | 0.9962 | -0.072432 | 46.7516
67 | 0.10049 | 0.025473 | -0.1002 | -0.025288 | 0.00029109 | 0.00018585 | 0.1502 | 0.1502 | 0.1502 | 0.9962 | -0.072432 | 0.99305 | -0.1329 | 41.2641
68 | 0.086611 | 0.021883 | -0.086499 | -0.021811 | 0.00011277 | 7.1941e-05 | 0.12984 | 0.12984 | 0.12984 | 0.99305 | -0.1329 | 0.99164 | -0.1601 | 35.6712
69 | -0.01021 | -0.0025589 | 0.01021 | 0.0025592 | 5.7007e-07 | 2.8262e-07 | 0.015382 | 0.015382 | 0.015382 | 0.98763 | -0.23782 | 0.98769 | -0.23665 | 4.2259
70 | 0.01021 | 0.0025589 | -0.010209 | -0.0025587 | 5.7973e-07 | 2.8743e-07 | 0.015382 | 0.015382 | 0.015382 | 0.98763 | -0.23782 | 0.98757 | -0.23901 | 4.2259
71 | -0.014509 | -0.0036367 | 0.014514 | 0.0036395 | 4.935e-06 | 2.8058e-06 | 0.021859 | 0.021859 | 0.021859 | 0.98769 | -0.23665 | 0.98805 | -0.22951 | 6.0053
72 | 0.0070557 | 0.0017684 | -0.0070551 | -0.0017682 | 5.7066e-07 | 1.9296e-07 | 0.010631 | 0.010631 | 0.010631 | 0.98757 | -0.23901 | 0.98748 | -0.24071 | 2.9207
73 | 0.013654 | 0.0034225 | -0.013653 | -0.0034217 | 1.3996e-06 | 7.8107e-07 | 0.020489 | 0.020489 | 0.020489 | 0.99164 | -0.1601 | 0.99153 | -0.16225 | 5.6289
74 | 0.072844 | 0.018388 | -0.07267 | -0.018277 | 0.00017424 | 0.00011102 | 0.10935 | 0.10935 | 0.10935 | 0.99164 | -0.1601 | 0.98905 | -0.21016 | 30.0424
75 | -0.016409 | -0.0041144 | 0.016409 | 0.0041144 | 4.5691e-08 | 2.6686e-08 | 0.024713 | 0.024713 | 0.024713 | 0.98805 | -0.22951 | 0.98806 | -0.22945 | 6.7892
76 | 0.012606 | 0.0031599 | -0.012605 | -0.0031591 | 1.429e-06 | 7.7755e-07 | 0.018929 | 0.018929 | 0.018929 | 0.991 | -0.17072 | 0.99088 | -0.1731 | 5.2002
77 | 0.0064473 | 0.0016159 | -0.0064457 | -0.0016155 | 1.5401e-06 | 4.2149e-07 | 0.009682 | 0.0096822 | 0.0096822 | 0.99088 | -0.1731 | 0.99062 | -0.17812 | 2.6599
78 | 0.0084851 | 0.0021268 | -0.008484 | -0.0021263 | 1.1013e-06 | 4.7789e-07 | 0.012826 | 0.012826 | 0.012826 | 0.98442 | -0.30016 | 0.98428 | -0.30288 | 3.5236
79 | -0.010381 | -0.0026019 | 0.010381 | 0.002602 | 1.0952e-07 | 5.5014e-08 | 0.015692 | 0.015692 | 0.015692 | 0.98442 | -0.30016 | 0.98443 | -0.29994 | 4.3109
80 | -0.012273 | -0.0030761 | 0.012273 | 0.0030763 | 4.3964e-07 | 2.3806e-07 | 0.018551 | 0.018551 | 0.018551 | 0.98443 | -0.29994 | 0.98447 | -0.29919 | 5.0965
81 | -0.015865 | -0.0039765 | 0.015869 | 0.0039788 | 3.8946e-06 | 2.2629e-06 | 0.02398 | 0.02398 | 0.02398 | 0.98447 | -0.29919 | 0.98474 | -0.29403 | 6.5879
82 | -0.018901 | -0.0047388 | 0.018905 | 0.0047407 | 3.1768e-06 | 1.901e-06 | 0.028562 | 0.028562 | 0.028562 | 0.98474 | -0.29403 | 0.98492 | -0.29051 | 7.8467
83 | -0.020776 | -0.0052097 | 0.020776 | 0.0052098 | 1.7293e-07 | 1.0472e-07 | 0.031389 | 0.031389 | 0.031389 | 0.98492 | -0.29051 | 0.98492 | -0.29033 | 8.6234
84 | 0.029612 | 0.0074317 | -0.029601 | -0.007425 | 1.0801e-05 | 6.7265e-06 | 0.044554 | 0.044554 | 0.044554 | 0.98905 | -0.21016 | 0.98866 | -0.21782 | 12.2402
85 | 0.043058 | 0.010845 | -0.043035 | -0.010831 | 2.2968e-05 | 1.4512e-05 | 0.0648 | 0.0648 | 0.0648 | 0.98905 | -0.21016 | 0.98847 | -0.22132 | 17.8023
86 | 0.027726 | 0.0069552 | -0.027726 | -0.0069551 | 3.1062e-08 | 1.927e-08 | 0.041733 | 0.041733 | 0.041733 | 0.98866 | -0.21782 | 0.98865 | -0.21784 | 11.465
87 | 0.041231 | 0.010379 | -0.041231 | -0.010378 | 1.5762e-07 | 9.9479e-08 | 0.062084 | 0.062084 | 0.062084 | 0.98847 | -0.22132 | 0.98847 | -0.2214 | 17.056
88 | 0.025852 | 0.0064853 | -0.025851 | -0.0064853 | 2.1987e-08 | 1.3575e-08 | 0.038911 | 0.038911 | 0.038911 | 0.98865 | -0.21784 | 0.98865 | -0.21786 | 10.6899
89 | 0.039428 | 0.0099267 | -0.039428 | -0.0099266 | 1.3818e-07 | 8.7093e-08 | 0.05937 | 0.05937 | 0.05937 | 0.98847 | -0.2214 | 0.98847 | -0.22148 | 16.3105
90 | 0.029109 | 0.0073063 | -0.029099 | -0.0073002 | 9.758e-06 | 6.0733e-06 | 0.043942 | 0.043942 | 0.043942 | 0.98581 | -0.27312 | 0.98545 | -0.28015 | 12.0719
91 | -0.030911 | -0.007758 | 0.030912 | 0.007759 | 1.6688e-06 | 1.0419e-06 | 0.046662 | 0.046662 | 0.046662 | 0.98581 | -0.27312 | 0.98587 | -0.27199 | 12.8192
92 | 0.026361 | 0.006614 | -0.026351 | -0.0066078 | 1.0056e-05 | 6.2205e-06 | 0.039807 | 0.039807 | 0.039807 | 0.98545 | -0.28015 | 0.98504 | -0.28815 | 10.9361
93 | -0.03393 | -0.0085153 | 0.033947 | 0.0085257 | 1.646e-05 | 1.0321e-05 | 0.051217 | 0.051217 | 0.051217 | 0.98587 | -0.27199 | 0.98639 | -0.26182 | 14.0706
94 | 0.022654 | 0.0056813 | -0.022652 | -0.0056798 | 2.352e-06 | 1.4371e-06 | 0.034223 | 0.034223 | 0.034223 | 0.98504 | -0.28815 | 0.98492 | -0.29033 | 9.4019
95 | -0.035751 | -0.0089779 | 0.035761 | 0.008984 | 9.6531e-06 | 6.065e-06 | 0.053939 | 0.053939 | 0.053939 | 0.98639 | -0.26182 | 0.98668 | -0.25616 | 14.8184
96 | -0.037564 | -0.0094358 | 0.037596 | 0.0094561 | 3.2325e-05 | 2.0345e-05 | 0.056658 | 0.056657 | 0.056658 | 0.98668 | -0.25616 | 0.98761 | -0.23815 | 15.5653
97 | -0.037596 | -0.0094561 | 0.037626 | 0.009475 | 2.9961e-05 | 1.8856e-05 | 0.056657 | 0.056657 | 0.056657 | 0.98761 | -0.23815 | 0.98847 | -0.22148 | 15.5652
98 | 0.0093749 | 0.0023255 | -0.0093741 | -0.0023262 | 7.9306e-07 | -6.3931e-07 | 0.014342 | 0.014343 | 0.014343 | 0.97206 | -0.5395 | 0.97197 | -0.54129 | 1.3134
99 | 0.0073915 | 0.0018524 | -0.0073909 | -0.0018522 | 5.2298e-07 | 1.9268e-07 | 0.011173 | 0.011173 | 0.011173 | 0.98442 | -0.2974 | 0.98434 | -0.29889 | 3.0694
100 | 0.006056 | 0.0015177 | -0.0060558 | -0.0015176 | 2.2269e-07 | 5.2454e-08 | 0.0091547 | 0.0091548 | 0.0091548 | 0.98434 | -0.29889 | 0.9843 | -0.29966 | 2.515
101 | 0.0046516 | 0.0011657 | -0.0046514 | -0.0011657 | 1.3775e-07 | -6.2603e-09 | 0.0070319 | 0.007032 | 0.007032 | 0.9843 | -0.29966 | 0.98427 | -0.30028 | 1.9319
102 | 0.0031997 | 0.00080184 | -0.0031996 | -0.0008019 | 7.2596e-08 | -5.869e-08 | 0.0048372 | 0.0048373 | 0.0048373 | 0.98427 | -0.30028 | 0.98425 | -0.30076 | 1.3289
103 | 0.005789 | 0.0014277 | -0.0057888 | -0.0014285 | 2.5395e-07 | -8.009e-07 | 0.0088543 | 0.0088547 | 0.0088547 | 0.97197 | -0.54129 | 0.97192 | -0.54222 | 0.81087
104 | 0.0045424 | 0.0011161 | -0.0045424 | -0.0011162 | 1.7934e-08 | -9.9064e-08 | 0.0069464 | 0.0069464 | 0.0069464 | 0.97192 | -0.54222 | 0.97192 | -0.5423 | 0.63612
105 | 0.0029204 | 0.00070969 | -0.0029204 | -0.0007097 | 4.0313e-10 | -5.7705e-09 | 0.0044633 | 0.0044633 | 0.0044633 | 0.97192 | -0.5423 | 0.97192 | -0.54231 | 0.40872
106 | 0.00084329 | 0.00018912 | -0.00084326 | -0.00019373 | 2.5631e-08 | -4.6059e-06 | 0.0012835 | 0.001285 | 0.001285 | 0.97192 | -0.54231 | 0.97188 | -0.54299 | 0.11767
107 | 0.00026359 | 4.845e-05 | -0.00026359 | -5.0319e-05 | 9.9741e-10 | -1.8694e-06 | 0.00039803 | 0.00039854 | 0.00039854 | 0.97188 | -0.54299 | 0.97188 | -0.54308 | 0.036496
108 | 0.00026359 | 5.0319e-05 | -0.00026359 | -5.4484e-05 | 2.2318e-09 | -4.1649e-06 | 0.00039854 | 0.00039975 | 0.00039975 | 0.97188 | -0.54308 | 0.97187 | -0.54329 | 0.036607
109 | 0.00026359 | 5.4484e-05 | -0.00026358 | -6.606e-05 | 6.2792e-09 | -1.1576e-05 | 0.00039975 | 0.00040358 | 0.00040358 | 0.97187 | -0.54329 | 0.97185 | -0.54382 | 0.036958
110 | -0.043283 | -0.010886 | 0.043318 | 0.010908 | 3.5556e-05 | 2.2482e-05 | 0.06594 | 0.06594 | 0.06594 | 0.97694 | -0.44308 | 0.97781 | -0.4259 | 18.1153
111 | 0.040465 | 0.01018 | -0.040444 | -0.010166 | 2.1116e-05 | 1.3329e-05 | 0.061648 | 0.061648 | 0.061648 | 0.97694 | -0.44308 | 0.97638 | -0.45401 | 16.9363
112 | -0.058058 | -0.014602 | 0.058201 | 0.014694 | 0.0001435 | 9.1226e-05 | 0.08837 | 0.088369 | 0.08837 | 0.97781 | -0.4259 | 0.98045 | -0.37429 | 24.2774
113 | -0.060071 | -0.015162 | 0.060183 | 0.015234 | 0.00011233 | 7.1439e-05 | 0.091207 | 0.091207 | 0.091207 | 0.98045 | -0.37429 | 0.98245 | -0.33533 | 25.0569
114 | -0.062731 | -0.015872 | 0.062766 | 0.015894 | 3.4792e-05 | 2.1747e-05 | 0.095066 | 0.095066 | 0.095066 | 0.98245 | -0.33533 | 0.98305 | -0.32378 | 13.0586
115 | -0.018303 | -0.0045891 | 0.018303 | 0.0045891 | 5.9043e-08 | 3.5133e-08 | 0.027565 | 0.027565 | 0.027565 | 0.98806 | -0.22945 | 0.98806 | -0.22939 | 7.5729
116 | -0.020197 | -0.0050638 | 0.020197 | 0.0050639 | 6.87e-08 | 4.1432e-08 | 0.030418 | 0.030418 | 0.030418 | 0.98806 | -0.22939 | 0.98806 | -0.22932 | 8.3565
117 | -0.02209 | -0.0055383 | 0.022102 | 0.0055457 | 1.2047e-05 | 7.338e-06 | 0.033269 | 0.033269 | 0.033269 | 0.98806 | -0.22932 | 0.98865 | -0.21788 | 9.1397
118 | 0.023977 | 0.0060154 | -0.023977 | -0.0060154 | 2.4042e-08 | 1.4755e-08 | 0.03609 | 0.03609 | 0.03609 | 0.98865 | -0.21786 | 0.98865 | -0.21788 | 9.9147

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4922 | 0.1261

## res_load
| p_mw | q_mvar
0 | 0.010669 | 0.002674
1 | 0.002827 | 0.00070852
2 | 0.012402 | 0.0031082
3 | 0.011078 | 0.0027764
4 | 0.0085929 | 0.0021536
5 | 0.0035806 | 0.00089739
6 | 0.022805 | 0.0057154
7 | 0.010658 | 0.0026712
8 | 0.01662 | 0.0041654
9 | 0.015583 | 0.0039056
10 | 0.0062084 | 0.001556
11 | 0.0095129 | 0.0023842
12 | 0.020935 | 0.0052467
13 | 0.013147 | 0.0032949
14 | 0.0093332 | 0.0023391
15 | 0.0016078 | 0.00040296
16 | 0.012924 | 0.0032391
17 | 0.002055 | 0.00051503
18 | 0.0020535 | 0.00051465
19 | 0.012883 | 0.0032287
20 | 0.014142 | 0.0035444
21 | 0.0033672 | 0.00084389
22 | 0.0011041 | 0.00027672
23 | 0.0016045 | 0.00040211
24 | 0.0015439 | 0.00038694
25 | 0.0010692 | 0.00026797
26 | 0.0012785 | 0.00032041
27 | 0.0020822 | 0.00052185
28 | 0.0010783 | 0.00027024
29 | 0.00097147 | 0.00024347
30 | 0.011985 | 0.0030036
31 | 0.01219 | 0.0030552
32 | 0.00465 | 0.0011654
33 | 0.0030095 | 0.00075425
34 | 0.005127 | 0.001285
35 | 0.0016363 | 0.00041009
36 | 0.0063565 | 0.0015931
37 | 0.0055723 | 0.0013966
38 | 0.013373 | 0.0033515
39 | 0.013586 | 0.0034051
40 | 0.0042991 | 0.0010775
41 | 0.0031533 | 0.00079028
42 | 0.0018949 | 0.0004749
43 | 0.0031996 | 0.0008019
44 | 0.0070551 | 0.0017682
45 | 0.0061576 | 0.0015432
46 | 0.0064457 | 0.0016155
47 | 0.0018959 | 0.00047515
48 | 0.008484 | 0.0021263
49 | 0.0018918 | 0.00047412
50 | 0.0035918 | 0.0009002
51 | 0.0030323 | 0.00075998
52 | 0.0018713 | 0.000469
53 | 0.013653 | 0.0034217
54 | 0.0018747 | 0.00046984
55 | 0.0018046 | 0.00045228
56 | 0.0018747 | 0.00046984
57 | 0.0018026 | 0.00045178
58 | 0.001802 | 0.00045163
59 | 0.0027381 | 0.00068624
60 | 0.0030179 | 0.00075636
61 | 0.0036969 | 0.00092652
62 | 0.0018046 | 0.00045228
63 | 0.0018755 | 0.00047004
64 | 0.0018026 | 0.00045178
65 | 0.001802 | 0.00045163
66 | 0.0017758 | 0.00044505
67 | 0.002117 | 0.00053058
68 | 0.010584 | 0.0026525
69 | 0.0013349 | 0.00033456
70 | 0.0014042 | 0.00035194
71 | 0.0014517 | 0.00036384
72 | 0.0031996 | 0.0008019
73 | 0.0035851 | 0.00089851
74 | 0.0012464 | 0.00031238
75 | 0.0016219 | 0.0004065
76 | 0.0020771 | 0.00052057
77 | 0.00057967 | 0.00014528
78 | 0.0028176 | 0.00070615
79 | 0.014739 | 0.003694
80 | 0.014002 | 0.0035092
81 | 0.0018698 | 0.00046861
82 | 0.0025481 | 0.00063861
83 | 0.0018494 | 0.0004635
84 | 0.0018941 | 0.0004747
85 | 0.00026358 | 6.606e-05
86 | 0.0018941 | 0.0004747
87 | 0.0018931 | 0.00047445
88 | 0.0018747 | 0.00046984
89 | 0.0018743 | 0.00046975

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1