## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-59_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-59_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1059-59_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1059-59_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1059-59_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1059-59_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1059-59_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1059-59_0_4_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_1059-59_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1059-59_0_4_node_69 | 0.4 | n |  | TRUE
10 | bus_LV_1059-59_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1059-59_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1059-59_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1059-59_0_4_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1059-59_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1059-59_0_4_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_1059-59_0_4_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1059-59_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1059-59_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1059-59_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1059-59_0_4_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_1059-59_0_4_node_37 | 0.4 | n |  | TRUE
22 | bus_LV_1059-59_0_4_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_1059-59_0_4_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_1059-59_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1059-59_0_4_node_68 | 0.4 | n |  | TRUE
26 | bus_LV_1059-59_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1059-59_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1059-59_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1059-59_0_4_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1059-59_0_4_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_1059-59_0_4_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1059-59_0_4_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1059-59_0_4_node_66 | 0.4 | n |  | TRUE
34 | bus_LV_1059-59_0_4_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_1059-59_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1059-59_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1059-59_0_4_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_1059-59_0_4_node_67 | 0.4 | n |  | TRUE
39 | bus_LV_1059-59_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1059-59_0_4_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_1059-59_0_4_node_60 | 0.4 | n |  | TRUE
42 | bus_LV_1059-59_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1059-59_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1059-59_0_4_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1059-59_0_4_node_65 | 0.4 | n |  | TRUE
46 | bus_LV_1059-59_0_4_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_1059-59_0_4_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_1059-59_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_1059-59_0_4_node_63 | 0.4 | n |  | TRUE
50 | bus_LV_1059-59_0_4_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_1059-59_0_4_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_1059-59_0_4_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_1059-59_0_4_node_62 | 0.4 | n |  | TRUE
54 | bus_LV_1059-59_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1059-59_0_4_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_1059-59_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_1059-59_0_4_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_1059-59_0_4_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_1059-59_0_4_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_1059-59_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_1059-59_0_4_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_1059-59_0_4_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_1059-59_0_4_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_1059-59_0_4_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_1059-59_0_4_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_1059-59_0_4_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_1059-59_0_4_node_58 | 0.4 | n |  | TRUE
68 | bus_MV_24_1_node_192 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-59_0_4_load_0 | 0 | 0.0033143 | 0.00083064 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-59_0_4_load_1 | 1 | 0.0030401 | 0.00076193 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-59_0_4_load_3 | 3 | 0.00078385 | 0.00019645 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-59_0_4_load_4 | 6 | 0.015525 | 0.003891 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-59_0_4_load_44 | 7 | 0.010764 | 0.0026976 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-59_0_4_load_69 | 9 | 0.008033 | 0.0020133 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-59_0_4_load_43 | 13 | 0.0083883 | 0.0021023 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-59_0_4_load_30 | 16 | 0.0042809 | 0.0010729 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-59_0_4_load_32 | 20 | 0.01047 | 0.002624 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-59_0_4_load_37 | 21 | 0.0058818 | 0.0014741 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-59_0_4_load_49 | 22 | 0.0068512 | 0.0017171 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1059-59_0_4_load_45 | 23 | 0.0055487 | 0.0013906 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1059-59_0_4_load_68 | 25 | 0.0065078 | 0.001631 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1059-59_0_4_load_24 | 27 | 0.0031515 | 0.00078985 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1059-59_0_4_load_33 | 29 | 0.010071 | 0.0025241 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1059-59_0_4_load_48 | 30 | 0.013332 | 0.0033414 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1059-59_0_4_load_31 | 31 | 0.021421 | 0.0053687 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1059-59_0_4_load_28 | 32 | 0.019128 | 0.004794 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1059-59_0_4_load_66 | 33 | 0.0017324 | 0.00043418 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1059-59_0_4_load_50 | 37 | 0.0031765 | 0.0007961 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1059-59_0_4_load_67 | 38 | 0.0013663 | 0.00034244 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1059-59_0_4_load_27 | 39 | 0.0020576 | 0.0005157 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1059-59_0_4_load_61 | 40 | 0.00263 | 0.00065914 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1059-59_0_4_load_60 | 41 | 0.0026133 | 0.00065497 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1059-59_0_4_load_29 | 42 | 0.010699 | 0.0026815 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1059-59_0_4_load_35 | 43 | 0.0066809 | 0.0016744 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1059-59_0_4_load_65 | 45 | 0.0023347 | 0.00058512 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1059-59_0_4_load_23 | 46 | 0.0024194 | 0.00060635 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1059-59_0_4_load_55 | 47 | 0.0073592 | 0.0018444 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1059-59_0_4_load_41 | 48 | 0.002138 | 0.00053583 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1059-59_0_4_load_63 | 49 | 0.0017142 | 0.00042963 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1059-59_0_4_load_64 | 50 | 0.0016566 | 0.00041519 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1059-59_0_4_load_25 | 51 | 0.00236 | 0.00059147 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1059-59_0_4_load_26 | 52 | 0.0020842 | 0.00052236 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1059-59_0_4_load_62 | 53 | 0.0029923 | 0.00074994 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1059-59_0_4_load_42 | 54 | 0.0020758 | 0.00052026 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1059-59_0_4_load_34 | 55 | 0.0065864 | 0.0016507 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1059-59_0_4_load_36 | 56 | 0.012613 | 0.003161 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1059-59_0_4_load_38 | 57 | 0.0033415 | 0.00083746 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1059-59_0_4_load_39 | 58 | 0.0032924 | 0.00082516 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1059-59_0_4_load_40 | 59 | 0.0020406 | 0.00051143 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1059-59_0_4_load_53 | 61 | 0.0056301 | 0.001411 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1059-59_0_4_load_51 | 62 | 0.0061395 | 0.0015387 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1059-59_0_4_load_52 | 63 | 0.011547 | 0.002894 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1059-59_0_4_load_59 | 64 | 0.0024047 | 0.00060268 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1059-59_0_4_load_56 | 65 | 0.0036445 | 0.00091339 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1059-59_0_4_load_57 | 66 | 0.0025848 | 0.00064782 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1059-59_0_4_load_58 | 67 | 0.0068321 | 0.0017123 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-59_0_4_line_0 |  | 0 | 1 | 0.035712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1059-59_0_4_line_1 |  | 0 | 2 | 0.12941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1059-59_0_4_line_2 |  | 1 | 3 | 0.012135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1059-59_0_4_line_3 |  | 2 | 4 | 0.126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1059-59_0_4_line_4 |  | 3 | 5 | 0.054398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1059-59_0_4_line_5 |  | 4 | 13 | 0.22718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1059-59_0_4_line_6 |  | 5 | 21 | 0.0061878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1059-59_0_4_line_7 |  | 5 | 17 | 0.046905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1059-59_0_4_line_8 |  | 6 | 7 | 0.051342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1059-59_0_4_line_9 |  | 7 | 10 | 0.07959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1059-59_0_4_line_10 |  | 8 | 9 | 0.01263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1059-59_0_4_line_11 |  | 8 | 10 | 0.03235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1059-59_0_4_line_12 |  | 8 | 11 | 0.032914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1059-59_0_4_line_13 |  | 10 | 12 | 0.031712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1059-59_0_4_line_14 |  | 11 | 24 | 0.023905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1059-59_0_4_line_15 |  | 11 | 25 | 0.0078342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1059-59_0_4_line_16 |  | 12 | 13 | 0.045307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1059-59_0_4_line_17 |  | 14 | 15 | 0.025416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1059-59_0_4_line_18 |  | 14 | 16 | 0.039146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1059-59_0_4_line_19 |  | 15 | 40 | 0.018989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1059-59_0_4_line_20 |  | 15 | 41 | 0.012267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1059-59_0_4_line_21 |  | 16 | 42 | 0.037916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1059-59_0_4_line_22 |  | 17 | 18 | 0.030896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1059-59_0_4_line_23 |  | 17 | 19 | 0.069715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1059-59_0_4_line_24 |  | 17 | 20 | 0.02312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1059-59_0_4_line_25 |  | 18 | 22 | 0.01778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1059-59_0_4_line_26 |  | 18 | 23 | 0.015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1059-59_0_4_line_27 |  | 19 | 31 | 0.036788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1059-59_0_4_line_28 |  | 19 | 32 | 0.0077181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1059-59_0_4_line_29 |  | 19 | 26 | 0.012393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1059-59_0_4_line_30 |  | 20 | 29 | 0.051515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1059-59_0_4_line_31 |  | 21 | 43 | 0.010552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1059-59_0_4_line_32 |  | 23 | 44 | 0.020515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1059-59_0_4_line_33 |  | 24 | 33 | 0.02228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1059-59_0_4_line_34 |  | 25 | 45 | 0.036035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1059-59_0_4_line_35 |  | 26 | 27 | 0.094724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1059-59_0_4_line_36 |  | 27 | 46 | 0.021945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1059-59_0_4_line_37 |  | 28 | 29 | 0.017858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1059-59_0_4_line_38 |  | 28 | 30 | 0.019046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1059-59_0_4_line_39 |  | 31 | 47 | 0.055761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1059-59_0_4_line_40 |  | 32 | 42 | 0.049613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1059-59_0_4_line_41 |  | 33 | 38 | 0.0084267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1059-59_0_4_line_42 |  | 34 | 35 | 0.027354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1059-59_0_4_line_43 |  | 34 | 36 | 0.033561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1059-59_0_4_line_44 |  | 34 | 37 | 0.02145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1059-59_0_4_line_45 |  | 35 | 38 | 0.038346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1059-59_0_4_line_46 |  | 36 | 39 | 0.023241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1059-59_0_4_line_47 |  | 37 | 48 | 0.0068483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1059-59_0_4_line_48 |  | 39 | 51 | 0.0055315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1059-59_0_4_line_49 |  | 41 | 64 | 0.023083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1059-59_0_4_line_50 |  | 43 | 55 | 0.017692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1059-59_0_4_line_51 |  | 44 | 60 | 0.023165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1059-59_0_4_line_52 |  | 45 | 50 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1059-59_0_4_line_53 |  | 48 | 58 | 0.0079221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1059-59_0_4_line_54 |  | 49 | 50 | 0.0050104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1059-59_0_4_line_55 |  | 51 | 52 | 0.012435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1059-59_0_4_line_56 |  | 53 | 54 | 0.021574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1059-59_0_4_line_57 |  | 54 | 59 | 0.0054258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1059-59_0_4_line_58 |  | 55 | 56 | 0.00090302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1059-59_0_4_line_59 |  | 57 | 58 | 0.030284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1059-59_0_4_line_60 |  | 57 | 59 | 0.0075135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1059-59_0_4_line_61 |  | 60 | 61 | 0.017521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1059-59_0_4_line_62 |  | 60 | 62 | 0.026846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1059-59_0_4_line_63 |  | 62 | 63 | 0.0061033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1059-59_0_4_line_64 |  | 64 | 66 | 0.0014997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1059-59_0_4_line_65 |  | 65 | 66 | 0.02341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1059-59_0_4_line_66 |  | 65 | 67 | 0.0099236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-59_0_4_trafo_46 | 0.63 MVA 20/0.4 kV | 68 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2663349.3853 | 1210079.083 | 2663357.7465 | 1210085.1269 | 2663370.2943 | 1210095.9333 | 2663376.4657 | 1210102.2555
1 | 2663250.9012 | 1210000.898 | 2663249.7061 | 1210003.22 | 2663249.6187 | 1210005.7318 | 2663250.4233 | 1210007.975 | 2663252.4086 | 1210009.9861 | 2663302.2999 | 1210045.0475 | 2663349.3853 | 1210079.083
2 | 2663376.4657 | 1210102.2555 | 2663384.9422 | 1210110.939
3 | 2663250.9012 | 1210000.898 | 2663250.2683 | 1210000.3798 | 2663245.6716 | 1209996.6288 | 2663241.8588 | 1209993.4977 | 2663241.4444 | 1209993.1597 | 2663244.1853 | 1209991.9992 | 2663246.2728 | 1209989.3864 | 2663263.3988 | 1209985.6545 | 2663265.5945 | 1209985.7445 | 2663269.5736 | 1209987.521 | 2663289.2243 | 1209988.6856 | 2663350.2073 | 1210007.0548
4 | 2663424.0033 | 1210148.5247 | 2663421.9843 | 1210145.4014 | 2663407.0288 | 1210130.1665 | 2663391.6024 | 1210117.7618 | 2663384.9422 | 1210110.939
5 | 2663350.2073 | 1210007.0548 | 2663424.8878 | 1210030.3065 | 2663508.3113 | 1210055.4199 | 2663560.7232 | 1210068.4524 | 2663568.3986 | 1210070.0276
6 | 2663424.0033 | 1210148.5247 | 2663428.1344 | 1210146.0004 | 2663428.2536 | 1210144.6592
7 | 2663424.0033 | 1210148.5247 | 2663427.2484 | 1210153.5512 | 2663435.2469 | 1210159.7288 | 2663438.5103 | 1210160.8975 | 2663442.9155 | 1210161.189 | 2663457.3032 | 1210158.3291 | 2663457.4856 | 1210159.0426 | 2663458.4418 | 1210162.755 | 2663459.1645 | 1210165.5533 | 2663459.3614 | 1210166.3336
8 | 2663549.3226 | 1210072.9565 | 2663512.9195 | 1210064.4967 | 2663499.5523 | 1210060.4406
9 | 2663625.323 | 1210088.9198 | 2663619.975 | 1210083.6707 | 2663613.7343 | 1210080.8692 | 2663610.1792 | 1210079.9752 | 2663604.4093 | 1210079.3578 | 2663580.6794 | 1210079.4383 | 2663574.0898 | 1210078.7122 | 2663549.3226 | 1210072.9565
10 | 2663660.5181 | 1210106.3168 | 2663658.1039 | 1210106.0576 | 2663653.2217 | 1210104.8826 | 2663648.0193 | 1210104.5046
11 | 2663625.323 | 1210088.9198 | 2663628.999 | 1210086.3241 | 2663632.6559 | 1210091.2105 | 2663634.7526 | 1210094.168 | 2663642.5057 | 1210104.09 | 2663648.0193 | 1210104.5046
12 | 2663667.8884 | 1210130.7437 | 2663657.78 | 1210117.1831 | 2663648.0193 | 1210104.5046
13 | 2663611.3213 | 1210066.9572 | 2663614.0045 | 1210074.7795 | 2663620.5049 | 1210079.5961 | 2663624.2845 | 1210082.9607 | 2663628.999 | 1210086.3241 | 2663625.323 | 1210088.9198
14 | 2663667.8884 | 1210130.7437 | 2663672.5874 | 1210136.9754 | 2663682.1627 | 1210149.9187
15 | 2663667.8884 | 1210130.7437 | 2663675.618 | 1210132.0195
16 | 2663611.3213 | 1210066.9572 | 2663603.5726 | 1210065.874 | 2663601.2065 | 1210068.9395 | 2663598.6103 | 1210070.7796 | 2663592.4746 | 1210071.6815 | 2663575.5803 | 1210071.5014 | 2663568.3986 | 1210070.0276
17 | 2663370.8954 | 1210143.0907 | 2663374.1347 | 1210141.5241 | 2663388.4697 | 1210125.0329
18 | 2663388.4697 | 1210125.0329 | 2663407.0564 | 1210144.0197 | 2663415.8703 | 1210152.9903
19 | 2663370.8954 | 1210143.0907 | 2663369.872 | 1210146.4152 | 2663359.8076 | 1210158.2167
20 | 2663370.8954 | 1210143.0907 | 2663368.176 | 1210142.9395 | 2663360.6656 | 1210137.0512
21 | 2663444.5913 | 1210177.731 | 2663434.3635 | 1210169.1807 | 2663428.8575 | 1210164.486 | 2663417.2674 | 1210154.4123 | 2663415.8703 | 1210152.9903
22 | 2663485.3869 | 1210159.773 | 2663470.6965 | 1210160.3616 | 2663465.0178 | 1210161.1795 | 2663458.4418 | 1210162.755 | 2663459.1645 | 1210165.5533 | 2663459.3614 | 1210166.3336
23 | 2663459.3614 | 1210166.3336 | 2663457.2091 | 1210167.1779 | 2663455.8713 | 1210168.6201 | 2663454.9102 | 1210170.3665 | 2663454.6949 | 1210172.7435 | 2663455.1691 | 1210175.3279 | 2663458.723 | 1210179.1902 | 2663467.645 | 1210187.1344 | 2663471.005 | 1210189.9385 | 2663488.121 | 1210204.2403 | 2663491.4913 | 1210206.7888 | 2663493.2306 | 1210207.619 | 2663492.638 | 1210208.3131 | 2663490.2368 | 1210211.1115 | 2663488.3666 | 1210213.304 | 2663487.7664 | 1210213.9981
24 | 2663459.3614 | 1210166.3336 | 2663465.7163 | 1210164.8225 | 2663479.6338 | 1210164.0144 | 2663482.2805 | 1210164.0685
25 | 2663485.3869 | 1210159.773 | 2663484.0965 | 1210149.6198 | 2663482.5344 | 1210146.4234 | 2663479.368 | 1210143.9994
26 | 2663485.3869 | 1210159.773 | 2663501.2809 | 1210161.3468
27 | 2663487.7664 | 1210213.9981 | 2663497.0502 | 1210221.5014 | 2663510.881 | 1210233.1112 | 2663515.7899 | 1210237.8076
28 | 2663487.7664 | 1210213.9981 | 2663486.4989 | 1210213.1174 | 2663482.6013 | 1210212.2643 | 2663480.9106 | 1210210.8804
29 | 2663496.8978 | 1210216.5412 | 2663490.2368 | 1210211.1115 | 2663488.3666 | 1210213.304 | 2663487.7664 | 1210213.9981
30 | 2663531.8031 | 1210175.1113 | 2663530.2928 | 1210173.8483 | 2663527.0168 | 1210171.7232 | 2663524.2782 | 1210170.5267 | 2663520.6877 | 1210169.3878 | 2663515.3062 | 1210167.9852 | 2663502.8127 | 1210165.6842 | 2663491.0093 | 1210164.2467 | 2663482.2805 | 1210164.0685
31 | 2663429.1877 | 1210134.1488 | 2663428.2536 | 1210144.6592
32 | 2663521.4495 | 1210164.9376 | 2663507.9062 | 1210162.0028 | 2663501.2809 | 1210161.3468
33 | 2663682.1627 | 1210149.9187 | 2663695.4147 | 1210167.8298
34 | 2663675.618 | 1210132.0195 | 2663684.5953 | 1210133.5013 | 2663689.4254 | 1210129.5949 | 2663709.7615 | 1210133.5845
35 | 2663496.8978 | 1210216.5412 | 2663525.711 | 1210244.3759 | 2663538.9439 | 1210259.3036 | 2663546.9276 | 1210271.1291 | 2663548.1883 | 1210282.6274 | 2663546.7895 | 1210291.2177 | 2663546.7058 | 1210291.3703
36 | 2663532.7213 | 1210307.8396 | 2663533.5669 | 1210307.4535 | 2663542.5034 | 1210299.0213 | 2663546.7058 | 1210291.3703
37 | 2663545.5412 | 1210186.5183 | 2663544.7418 | 1210185.9317 | 2663531.8031 | 1210175.1113
38 | 2663545.5412 | 1210186.5183 | 2663551.2571 | 1210190.7596 | 2663561.9245 | 1210196.0986
39 | 2663542.1198 | 1210282.9518 | 2663543.0506 | 1210277.6252 | 2663542.1876 | 1210273.7358 | 2663543.3657 | 1210271.5915 | 2663541.6241 | 1210267.4149 | 2663536.383 | 1210259.9768 | 2663525.3943 | 1210246.9963 | 2663515.7899 | 1210237.8076
40 | 2663444.5913 | 1210177.731 | 2663445.6788 | 1210178.6401 | 2663457.2949 | 1210188.4029 | 2663458.2432 | 1210190.0028 | 2663459.0762 | 1210192.4243 | 2663464.0506 | 1210197.08 | 2663480.9106 | 1210210.8804
41 | 2663695.4147 | 1210167.8298 | 2663699.5001 | 1210173.3514 | 2663700.2811 | 1210174.6995
42 | 2663699.9518 | 1210190.8335 | 2663708.0808 | 1210206.8189 | 2663712.1407 | 1210208.1297 | 2663717.2238 | 1210208.9845
43 | 2663699.9518 | 1210190.8335 | 2663690.4704 | 1210174.8003 | 2663681.646 | 1210162.721
44 | 2663699.9518 | 1210190.8335 | 2663697.4114 | 1210193.1412 | 2663694.8406 | 1210195.4485 | 2663691.9539 | 1210198.1638 | 2663689.6035 | 1210199.0503 | 2663681.6624 | 1210197.5152
45 | 2663717.2238 | 1210208.9845 | 2663715.9553 | 1210204.6461 | 2663707.9705 | 1210187.9729 | 2663700.2811 | 1210174.6995
46 | 2663681.646 | 1210162.721 | 2663676.1795 | 1210167.1543 | 2663673.194 | 1210169.8686 | 2663670.6314 | 1210171.4088 | 2663667.1643 | 1210171.5275 | 2663661.5566 | 1210170.4555
47 | 2663674.9386 | 1210196.2154 | 2663681.6624 | 1210197.5152
48 | 2663661.5566 | 1210170.4555 | 2663656.1236 | 1210169.4169
49 | 2663360.6656 | 1210137.0512 | 2663342.4998 | 1210122.8091
50 | 2663429.1877 | 1210134.1488 | 2663429.1877 | 1210134.1488 | 2663432.1309 | 1210132.5458 | 2663444.717 | 1210125.6719
51 | 2663529.8576 | 1210143.3473 | 2663521.4495 | 1210164.9376
52 | 2663709.7615 | 1210133.5845 | 2663720.6514 | 1210135.7208 | 2663720.7882 | 1210132.1646 | 2663720.7882 | 1210132.1646
53 | 2663667.1604 | 1210194.7118 | 2663674.9386 | 1210196.2154
54 | 2663725.6941 | 1210133.1822 | 2663720.7882 | 1210132.1646
55 | 2663656.1236 | 1210169.4169 | 2663651.395 | 1210168.513 | 2663647.0814 | 1210166.7659 | 2663646.352 | 1210163.8897
56 | 2663612.293 | 1210177.0066 | 2663610.8291 | 1210184.3902 | 2663624.6498 | 1210186.899
57 | 2663624.6498 | 1210186.899 | 2663629.9884 | 1210187.868
58 | 2663445.5096 | 1210125.2391 | 2663444.717 | 1210125.6719
59 | 2663667.1604 | 1210194.7118 | 2663658.9836 | 1210193.1312 | 2663637.381 | 1210189.2099
60 | 2663629.9884 | 1210187.868 | 2663637.381 | 1210189.2099
61 | 2663529.8576 | 1210143.3473 | 2663525.4379 | 1210140.1316 | 2663515.316 | 1210133.5199
62 | 2663529.8576 | 1210143.3473 | 2663534.5347 | 1210135.2366 | 2663537.5564 | 1210132.6894 | 2663541.5611 | 1210131.3312 | 2663550.1985 | 1210134.7867
63 | 2663555.8652 | 1210137.0536 | 2663550.1985 | 1210134.7867
64 | 2663341.3196 | 1210121.8838 | 2663342.4998 | 1210122.8091
65 | 2663322.8969 | 1210107.4402 | 2663341.3196 | 1210121.8838
66 | 2663315.0874 | 1210101.3174 | 2663322.8969 | 1210107.4402

## bus_geodata
| x | y | coords
0 | 2663349.3853 | 1210079.083
1 | 2663376.4657 | 1210102.2555
2 | 2663250.9012 | 1210000.898
3 | 2663384.9422 | 1210110.939
4 | 2663350.2073 | 1210007.0548
5 | 2663424.0033 | 1210148.5247
6 | 2663499.5523 | 1210060.4406
7 | 2663549.3226 | 1210072.9565
8 | 2663648.0193 | 1210104.5046
9 | 2663660.5181 | 1210106.3168
10 | 2663625.323 | 1210088.9198
11 | 2663667.8884 | 1210130.7437
12 | 2663611.3213 | 1210066.9572
13 | 2663568.3986 | 1210070.0276
14 | 2663388.4697 | 1210125.0329
15 | 2663370.8954 | 1210143.0907
16 | 2663415.8703 | 1210152.9903
17 | 2663459.3614 | 1210166.3336
18 | 2663485.3869 | 1210159.773
19 | 2663487.7664 | 1210213.9981
20 | 2663482.2805 | 1210164.0685
21 | 2663428.2536 | 1210144.6592
22 | 2663479.368 | 1210143.9994
23 | 2663501.2809 | 1210161.3468
24 | 2663682.1627 | 1210149.9187
25 | 2663675.618 | 1210132.0195
26 | 2663496.8978 | 1210216.5412
27 | 2663546.7058 | 1210291.3703
28 | 2663545.5412 | 1210186.5183
29 | 2663531.8031 | 1210175.1113
30 | 2663561.9245 | 1210196.0986
31 | 2663515.7899 | 1210237.8076
32 | 2663480.9106 | 1210210.8804
33 | 2663695.4147 | 1210167.8298
34 | 2663699.9518 | 1210190.8335
35 | 2663717.2238 | 1210208.9845
36 | 2663681.646 | 1210162.721
37 | 2663681.6624 | 1210197.5152
38 | 2663700.2811 | 1210174.6995
39 | 2663661.5566 | 1210170.4555
40 | 2663359.8076 | 1210158.2167
41 | 2663360.6656 | 1210137.0512
42 | 2663444.5913 | 1210177.731
43 | 2663429.1877 | 1210134.1488
44 | 2663521.4495 | 1210164.9376
45 | 2663709.7615 | 1210133.5845
46 | 2663532.7213 | 1210307.8396
47 | 2663542.1198 | 1210282.9518
48 | 2663674.9386 | 1210196.2154
49 | 2663725.6941 | 1210133.1822
50 | 2663720.7882 | 1210132.1646
51 | 2663656.1236 | 1210169.4169
52 | 2663646.352 | 1210163.8897
53 | 2663612.293 | 1210177.0066
54 | 2663624.6498 | 1210186.899
55 | 2663444.717 | 1210125.6719
56 | 2663445.5096 | 1210125.2391
57 | 2663637.381 | 1210189.2099
58 | 2663667.1604 | 1210194.7118
59 | 2663629.9884 | 1210187.868
60 | 2663529.8576 | 1210143.3473
61 | 2663515.316 | 1210133.5199
62 | 2663550.1985 | 1210134.7867
63 | 2663555.8652 | 1210137.0536
64 | 2663342.4998 | 1210122.8091
65 | 2663322.8969 | 1210107.4402
66 | 2663341.3196 | 1210121.8838
67 | 2663315.0874 | 1210101.3174
68 | 2663529.8576 | 1210143.3473

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99019 | -0.1866 | 0.0033143 | 0.00083064
1 | 0.99116 | -0.16821 | 0.0030401 | 0.00076193
2 | 0.98683 | -0.25096 | 0 | 0
3 | 0.99149 | -0.16175 | 0.00078385 | 0.00019645
4 | 0.98356 | -0.31404 | 0 | 0
5 | 0.99303 | -0.1326 | 0 | 0
6 | 0.97317 | -0.51713 | 0.015525 | 0.003891
7 | 0.97391 | -0.50247 | 0.010764 | 0.0026976
8 | 0.97537 | -0.47376 | 0 | 0
9 | 0.97527 | -0.47562 | 0.008033 | 0.0020133
10 | 0.97586 | -0.4641 | 0 | 0
11 | 0.97474 | -0.48609 | 0 | 0
12 | 0.9766 | -0.44956 | 0 | 0
13 | 0.97766 | -0.42882 | 0.0083883 | 0.0021023
14 | 0.98545 | -0.27961 | 0 | 0
15 | 0.98497 | -0.28906 | 0 | 0
16 | 0.9862 | -0.26507 | 0.0042809 | 0.0010729
17 | 0.9948 | -0.098792 | 0 | 0
18 | 0.99713 | -0.054342 | 0 | 0
19 | 0.98909 | -0.20893 | 0 | 0
20 | 0.99409 | -0.1126 | 0.01047 | 0.002624
21 | 0.99285 | -0.13608 | 0.0058818 | 0.0014741
22 | 0.99702 | -0.056477 | 0.0068512 | 0.0017171
23 | 0.99837 | -0.030806 | 0.0055487 | 0.0013906
24 | 0.97442 | -0.49238 | 0 | 0
25 | 0.97465 | -0.48785 | 0.0065078 | 0.001631
26 | 0.98903 | -0.21016 | 0 | 0
27 | 0.98854 | -0.21957 | 0.0031515 | 0.00078985
28 | 0.99277 | -0.1381 | 0 | 0
29 | 0.99299 | -0.13389 | 0.010071 | 0.0025241
30 | 0.99254 | -0.14259 | 0.013332 | 0.0033414
31 | 0.98812 | -0.22781 | 0.021421 | 0.0053687
32 | 0.9887 | -0.21647 | 0.019128 | 0.004794
33 | 0.97383 | -0.50411 | 0.0017324 | 0.00043418
34 | 0.97205 | -0.53922 | 0 | 0
35 | 0.9727 | -0.52633 | 0 | 0
36 | 0.97184 | -0.54324 | 0 | 0
37 | 0.97167 | -0.54676 | 0.0031765 | 0.0007961
38 | 0.97361 | -0.50828 | 0.0013663 | 0.00034244
39 | 0.9717 | -0.54603 | 0.0020576 | 0.0005157
40 | 0.98492 | -0.28996 | 0.00263 | 0.00065914
41 | 0.98476 | -0.29305 | 0.0026133 | 0.00065497
42 | 0.98707 | -0.2481 | 0.010699 | 0.0026815
43 | 0.9926 | -0.14091 | 0.0066809 | 0.0016744
44 | 1 | 0 | -0.28657 | -0.072791
45 | 0.97446 | -0.49162 | 0.0023347 | 0.00058512
46 | 0.98849 | -0.22052 | 0.0024194 | 0.00060635
47 | 0.98774 | -0.23514 | 0.0073592 | 0.0018444
48 | 0.97156 | -0.54877 | 0.002138 | 0.00053583
49 | 0.97441 | -0.49269 | 0.0017142 | 0.00042963
50 | 0.97442 | -0.49253 | 0.0016566 | 0.00041519
51 | 0.97168 | -0.54649 | 0.00236 | 0.00059147
52 | 0.97166 | -0.54697 | 0.0020842 | 0.00052236
53 | 0.97103 | -0.55932 | 0.0029923 | 0.00074994
54 | 0.97109 | -0.55812 | 0.0020758 | 0.00052026
55 | 0.99229 | -0.14692 | 0.0065864 | 0.0016507
56 | 0.99228 | -0.14712 | 0.012613 | 0.003161
57 | 0.97117 | -0.55663 | 0.0033415 | 0.00083746
58 | 0.97146 | -0.55078 | 0.0032924 | 0.00082516
59 | 0.97112 | -0.55762 | 0.0020406 | 0.00051143
60 | 0.99951 | -0.0094196 | 0 | 0
61 | 0.99942 | -0.011141 | 0.0056301 | 0.001411
62 | 0.99908 | -0.017708 | 0.0061395 | 0.0015387
63 | 0.99902 | -0.018938 | 0.011547 | 0.002894
64 | 0.98444 | -0.29947 | 0.0024047 | 0.00060268
65 | 0.98419 | -0.30423 | 0.0036445 | 0.00091339
66 | 0.98442 | -0.29982 | 0.0025848 | 0.00064782
67 | 0.98413 | -0.30545 | 0.0068321 | 0.0017123
68 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.088199 | -0.022583 | 0.088278 | 0.022631 | 7.8622e-05 | 4.8939e-05 | 0.13271 | 0.13271 | 0.13271 | 0.99019 | -0.1866 | 0.99116 | -0.16821 | 12.1532
1 | 0.084885 | 0.021752 | -0.084621 | -0.021588 | 0.00026393 | 0.00016394 | 0.12773 | 0.12773 | 0.12773 | 0.99019 | -0.1866 | 0.98683 | -0.25096 | 11.6973
2 | -0.091318 | -0.023393 | 0.091346 | 0.023411 | 2.8585e-05 | 1.7825e-05 | 0.13728 | 0.13728 | 0.13728 | 0.99116 | -0.16821 | 0.99149 | -0.16175 | 12.5711
3 | 0.084621 | 0.021588 | -0.084364 | -0.021428 | 0.00025698 | 0.00015965 | 0.12773 | 0.12774 | 0.12774 | 0.98683 | -0.25096 | 0.98356 | -0.31404 | 11.6974
4 | -0.09213 | -0.023608 | 0.092261 | 0.023689 | 0.00013034 | 8.1312e-05 | 0.13845 | 0.13845 | 0.13845 | 0.99149 | -0.16175 | 0.99303 | -0.1326 | 12.6788
5 | 0.084364 | 0.021428 | -0.083901 | -0.02114 | 0.00046336 | 0.00028795 | 0.12774 | 0.12774 | 0.12774 | 0.98356 | -0.31404 | 0.97766 | -0.42882 | 11.6977
6 | 0.031779 | 0.0079706 | -0.031773 | -0.0079673 | 5.2622e-06 | 3.2878e-06 | 0.047621 | 0.047621 | 0.047621 | 0.99303 | -0.1326 | 0.99285 | -0.13608 | 13.0828
7 | -0.12404 | -0.03166 | 0.12424 | 0.031788 | 0.000203 | 0.00012809 | 0.18607 | 0.18607 | 0.18607 | 0.99303 | -0.1326 | 0.9948 | -0.098792 | 17.0396
8 | -0.015525 | -0.003891 | 0.015536 | 0.0038973 | 1.0849e-05 | 6.3053e-06 | 0.023739 | 0.023738 | 0.023739 | 0.97317 | -0.51713 | 0.97391 | -0.50247 | 6.5216
9 | -0.0263 | -0.0065949 | 0.026348 | 0.0066248 | 4.8194e-05 | 2.9851e-05 | 0.040184 | 0.040184 | 0.040184 | 0.97391 | -0.50247 | 0.97586 | -0.4641 | 11.0395
10 | 0.0080338 | 0.0020136 | -0.008033 | -0.0020133 | 7.1147e-07 | 2.9772e-07 | 0.012256 | 0.012256 | 0.012256 | 0.97537 | -0.47376 | 0.97527 | -0.47562 | 3.3671
11 | -0.049015 | -0.012321 | 0.049037 | 0.012335 | 2.2618e-05 | 1.3264e-05 | 0.07479 | 0.074789 | 0.07479 | 0.97537 | -0.47376 | 0.97586 | -0.4641 | 6.8489
12 | 0.040981 | 0.010308 | -0.040957 | -0.010293 | 2.4133e-05 | 1.4624e-05 | 0.062533 | 0.062534 | 0.062534 | 0.97537 | -0.47376 | 0.97474 | -0.48609 | 8.5898
13 | -0.075385 | -0.018959 | 0.075437 | 0.018992 | 5.2398e-05 | 3.2346e-05 | 0.11497 | 0.11497 | 0.11497 | 0.97586 | -0.4641 | 0.9766 | -0.44956 | 10.5287
14 | 0.028741 | 0.0072317 | -0.028733 | -0.0072268 | 8.6326e-06 | 4.9291e-06 | 0.043886 | 0.043886 | 0.043886 | 0.97474 | -0.48609 | 0.97442 | -0.49238 | 6.0283
15 | 0.012216 | 0.0030616 | -0.012215 | -0.003061 | 1.0216e-06 | 5.562e-07 | 0.018648 | 0.018648 | 0.018648 | 0.97474 | -0.48609 | 0.97465 | -0.48785 | 5.1231
16 | -0.075437 | -0.018992 | 0.075512 | 0.019038 | 7.4862e-05 | 4.6209e-05 | 0.11497 | 0.11497 | 0.11497 | 0.9766 | -0.44956 | 0.97766 | -0.42882 | 10.5286
17 | 0.02073 | 0.0052019 | -0.020721 | -0.0051963 | 9.34e-06 | 5.6539e-06 | 0.031304 | 0.031304 | 0.031304 | 0.98545 | -0.27961 | 0.98497 | -0.28906 | 8.6001
18 | -0.02073 | -0.0052019 | 0.020744 | 0.0052106 | 1.4385e-05 | 8.7075e-06 | 0.031304 | 0.031304 | 0.031304 | 0.98545 | -0.27961 | 0.9862 | -0.26507 | 8.6
19 | 0.0026301 | 0.00065897 | -0.00263 | -0.00065914 | 1.1242e-07 | -1.6973e-07 | 0.0039733 | 0.0039734 | 0.0039734 | 0.98497 | -0.28906 | 0.98492 | -0.28996 | 1.0916
20 | 0.018091 | 0.0045373 | -0.018087 | -0.0045353 | 3.4363e-06 | 2.0431e-06 | 0.027331 | 0.027331 | 0.027331 | 0.98497 | -0.28906 | 0.98476 | -0.29305 | 7.5085
21 | -0.025025 | -0.0062835 | 0.025046 | 0.006296 | 2.0277e-05 | 1.2493e-05 | 0.037763 | 0.037763 | 0.037763 | 0.9862 | -0.26507 | 0.98707 | -0.2481 | 10.3745
22 | -0.24797 | -0.063055 | 0.2485 | 0.063394 | 0.00053224 | 0.00033943 | 0.37123 | 0.37123 | 0.37123 | 0.9948 | -0.098792 | 0.99713 | -0.054342 | 33.9957
23 | 0.089802 | 0.022746 | -0.08933 | -0.022445 | 0.0004723 | 0.00030137 | 0.13441 | 0.13441 | 0.13441 | 0.9948 | -0.098792 | 0.98909 | -0.20893 | 36.9259
24 | 0.033925 | 0.0085211 | -0.033903 | -0.0085071 | 2.2332e-05 | 1.3992e-05 | 0.050751 | 0.050752 | 0.050752 | 0.9948 | -0.098792 | 0.99409 | -0.1126 | 13.9427
25 | 0.0068519 | 0.0017173 | -0.0068512 | -0.0017171 | 6.9711e-07 | 2.1425e-07 | 0.010225 | 0.010225 | 0.010225 | 0.99713 | -0.054342 | 0.99702 | -0.056477 | 2.8091
26 | -0.25535 | -0.065111 | 0.25564 | 0.065297 | 0.00029051 | 0.0001853 | 0.38146 | 0.38146 | 0.38146 | 0.99713 | -0.054342 | 0.99837 | -0.030806 | 34.932
27 | 0.028809 | 0.0072301 | -0.028783 | -0.007214 | 2.5919e-05 | 1.6116e-05 | 0.043345 | 0.043345 | 0.043345 | 0.98909 | -0.20893 | 0.98812 | -0.22781 | 11.9079
28 | 0.054947 | 0.013818 | -0.054927 | -0.013805 | 1.9786e-05 | 1.2564e-05 | 0.082681 | 0.082681 | 0.082681 | 0.98909 | -0.20893 | 0.9887 | -0.21647 | 22.7144
29 | 0.0055738 | 0.0013964 | -0.0055735 | -0.0013964 | 3.2677e-07 | 5.0084e-08 | 0.0083852 | 0.0083853 | 0.0083853 | 0.98909 | -0.20893 | 0.98903 | -0.21016 | 2.3037
30 | 0.023433 | 0.0058831 | -0.023409 | -0.0058686 | 2.3773e-05 | 1.4547e-05 | 0.03508 | 0.03508 | 0.03508 | 0.99409 | -0.1126 | 0.99299 | -0.13389 | 9.6373
31 | 0.025892 | 0.0064932 | -0.025886 | -0.0064895 | 5.9588e-06 | 3.6772e-06 | 0.038806 | 0.038806 | 0.038806 | 0.99285 | -0.13608 | 0.9926 | -0.14091 | 10.661
32 | -0.26119 | -0.066687 | 0.26158 | 0.066936 | 0.0003895 | 0.00024847 | 0.38973 | 0.38973 | 0.38973 | 0.99837 | -0.030806 | 1 | 0 | 35.6893
33 | 0.028733 | 0.0072268 | -0.028716 | -0.0072167 | 1.6092e-05 | 1.0021e-05 | 0.043886 | 0.043886 | 0.043886 | 0.97442 | -0.49238 | 0.97383 | -0.50411 | 12.0566
34 | 0.0057067 | 0.00143 | -0.0057057 | -0.0014298 | 1.0257e-06 | 2.0748e-07 | 0.0087124 | 0.0087126 | 0.0087126 | 0.97465 | -0.48785 | 0.97446 | -0.49162 | 2.3936
35 | 0.0055735 | 0.0013964 | -0.005571 | -0.001396 | 2.4978e-06 | 3.8357e-07 | 0.0083853 | 0.0083857 | 0.0083857 | 0.98903 | -0.21016 | 0.98854 | -0.21957 | 2.3038
36 | 0.0024195 | 0.00060614 | -0.0024194 | -0.00060635 | 1.0915e-07 | -2.1148e-07 | 0.0036419 | 0.003642 | 0.003642 | 0.98854 | -0.21957 | 0.98849 | -0.22052 | 1.0005
37 | -0.013335 | -0.003343 | 0.013338 | 0.0033445 | 2.6755e-06 | 1.4813e-06 | 0.019988 | 0.019988 | 0.019988 | 0.99277 | -0.1381 | 0.99299 | -0.13389 | 5.4911
38 | 0.013335 | 0.003343 | -0.013332 | -0.0033414 | 2.8535e-06 | 1.58e-06 | 0.019988 | 0.019988 | 0.019988 | 0.99277 | -0.1381 | 0.99254 | -0.14259 | 5.4912
39 | 0.0073618 | 0.0018453 | -0.0073592 | -0.0018444 | 2.5701e-06 | 9.3084e-07 | 0.011086 | 0.011086 | 0.011086 | 0.98812 | -0.22781 | 0.98774 | -0.23514 | 3.0457
40 | 0.035799 | 0.0090115 | -0.035745 | -0.0089775 | 5.4035e-05 | 3.3947e-05 | 0.053892 | 0.053892 | 0.053892 | 0.9887 | -0.21647 | 0.98707 | -0.2481 | 14.8056
41 | 0.026984 | 0.0067826 | -0.026979 | -0.0067792 | 5.3741e-06 | 3.3346e-06 | 0.041239 | 0.041239 | 0.041239 | 0.97383 | -0.50411 | 0.97361 | -0.50828 | 11.3294
42 | -0.025575 | -0.0064134 | 0.02559 | 0.0064232 | 1.5723e-05 | 9.7236e-06 | 0.039151 | 0.039151 | 0.039151 | 0.97205 | -0.53922 | 0.9727 | -0.52633 | 10.7558
43 | 0.0065041 | 0.00163 | -0.0065029 | -0.0016297 | 1.2476e-06 | 3.8255e-07 | 0.0099565 | 0.0099567 | 0.0099567 | 0.97205 | -0.53922 | 0.97184 | -0.54324 | 2.7354
44 | 0.01907 | 0.0047834 | -0.019064 | -0.0047793 | 6.8558e-06 | 4.1219e-06 | 0.029195 | 0.029195 | 0.029195 | 0.97205 | -0.53922 | 0.97167 | -0.54676 | 8.0205
45 | -0.02559 | -0.0064232 | 0.025612 | 0.0064368 | 2.2041e-05 | 1.363e-05 | 0.039151 | 0.039151 | 0.039151 | 0.9727 | -0.52633 | 0.97361 | -0.50828 | 10.7558
46 | 0.0065029 | 0.0016297 | -0.006502 | -0.0016294 | 8.6403e-07 | 2.6504e-07 | 0.0099567 | 0.0099568 | 0.0099568 | 0.97184 | -0.54324 | 0.9717 | -0.54603 | 2.7354
47 | 0.015887 | 0.0039832 | -0.015886 | -0.0039823 | 1.5202e-06 | 8.8812e-07 | 0.02433 | 0.02433 | 0.02433 | 0.97167 | -0.54676 | 0.97156 | -0.54877 | 6.6841
48 | 0.0044444 | 0.0011137 | -0.0044443 | -0.0011137 | 9.608e-08 | -7.0271e-09 | 0.0068058 | 0.0068058 | 0.0068058 | 0.9717 | -0.54603 | 0.97168 | -0.54649 | 1.8697
49 | 0.015474 | 0.0038803 | -0.015469 | -0.0038776 | 4.7326e-06 | 2.7353e-06 | 0.023382 | 0.023382 | 0.023382 | 0.98476 | -0.29305 | 0.98444 | -0.29947 | 6.4237
50 | 0.019205 | 0.0048151 | -0.019199 | -0.0048118 | 5.4995e-06 | 3.2911e-06 | 0.028791 | 0.028791 | 0.028791 | 0.9926 | -0.14091 | 0.99229 | -0.14692 | 7.9095
51 | 0.023335 | 0.0058547 | -0.023325 | -0.0058483 | 1.0475e-05 | 6.4004e-06 | 0.034726 | 0.034726 | 0.034726 | 1 | 0 | 0.99951 | -0.0094196 | 9.54
52 | 0.003371 | 0.00084467 | -0.0033709 | -0.00084476 | 1.4563e-07 | -8.9371e-08 | 0.0051475 | 0.0051476 | 0.0051476 | 0.97446 | -0.49162 | 0.97442 | -0.49253 | 1.4142
53 | 0.013748 | 0.0034465 | -0.013746 | -0.0034457 | 1.3171e-06 | 7.4484e-07 | 0.021056 | 0.021056 | 0.021056 | 0.97156 | -0.54877 | 0.97146 | -0.55078 | 5.7845
54 | -0.0017142 | -0.00042963 | 0.0017142 | 0.00042957 | 1.2876e-08 | -5.4171e-08 | 0.0026178 | 0.0026178 | 0.0026178 | 0.97441 | -0.49269 | 0.97442 | -0.49253 | 0.71918
55 | 0.0020843 | 0.00052224 | -0.0020842 | -0.00052236 | 4.7508e-08 | -1.2362e-07 | 0.0031918 | 0.0031919 | 0.0031919 | 0.97168 | -0.54649 | 0.97166 | -0.54697 | 0.87688
56 | -0.0029923 | -0.00074994 | 0.0029925 | 0.00074978 | 1.701e-07 | -1.5803e-07 | 0.0045854 | 0.0045853 | 0.0045854 | 0.97103 | -0.55932 | 0.97109 | -0.55812 | 1.2597
57 | -0.0050683 | -0.00127 | 0.0050684 | 0.00127 | 1.2272e-07 | 1.1411e-08 | 0.0077662 | 0.0077661 | 0.0077662 | 0.97109 | -0.55812 | 0.97112 | -0.55762 | 2.1336
58 | 0.012613 | 0.0031611 | -0.012613 | -0.003161 | 1.2114e-07 | 6.5865e-08 | 0.018914 | 0.018914 | 0.018914 | 0.99229 | -0.14692 | 0.99228 | -0.14712 | 5.1961
59 | -0.010451 | -0.0026191 | 0.010454 | 0.0026206 | 2.9119e-06 | 1.4888e-06 | 0.016013 | 0.016013 | 0.016013 | 0.97117 | -0.55663 | 0.97146 | -0.55078 | 4.3991
60 | 0.0071094 | 0.0017816 | -0.0071091 | -0.0017815 | 3.3432e-07 | 1.21e-07 | 0.010893 | 0.010893 | 0.010893 | 0.97117 | -0.55663 | 0.97112 | -0.55762 | 2.9926
61 | 0.0056305 | 0.0014111 | -0.0056301 | -0.001411 | 4.6167e-07 | 6.5851e-08 | 0.0083824 | 0.0083825 | 0.0083825 | 0.99951 | -0.0094196 | 0.99942 | -0.011141 | 2.3029
62 | 0.017694 | 0.0044372 | -0.017687 | -0.0044331 | 6.9865e-06 | 4.1197e-06 | 0.026343 | 0.026343 | 0.026343 | 0.99951 | -0.0094196 | 0.99908 | -0.017708 | 7.2372
63 | 0.011548 | 0.0028944 | -0.011547 | -0.002894 | 6.7705e-07 | 3.5339e-07 | 0.017199 | 0.017199 | 0.017199 | 0.99908 | -0.017708 | 0.99902 | -0.018938 | 4.7251
64 | 0.013064 | 0.0032749 | -0.013064 | -0.0032747 | 2.1931e-07 | 1.2129e-07 | 0.019747 | 0.019747 | 0.019747 | 0.98444 | -0.29947 | 0.98442 | -0.29982 | 5.4251
65 | -0.010477 | -0.0026258 | 0.010479 | 0.0026269 | 2.2027e-06 | 1.1122e-06 | 0.01584 | 0.01584 | 0.01584 | 0.98419 | -0.30423 | 0.98442 | -0.29982 | 4.3518
66 | 0.0068325 | 0.0017124 | -0.0068321 | -0.0017123 | 3.9712e-07 | 1.2806e-07 | 0.01033 | 0.01033 | 0.01033 | 0.98419 | -0.30423 | 0.98413 | -0.30545 | 2.838

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28657 | 0.072791

## res_load
| p_mw | q_mvar
0 | 0.0033143 | 0.00083064
1 | 0.0030401 | 0.00076193
2 | 0.00078385 | 0.00019645
3 | 0.015525 | 0.003891
4 | 0.010764 | 0.0026976
5 | 0.008033 | 0.0020133
6 | 0.0083883 | 0.0021023
7 | 0.0042809 | 0.0010729
8 | 0.01047 | 0.002624
9 | 0.0058818 | 0.0014741
10 | 0.0068512 | 0.0017171
11 | 0.0055487 | 0.0013906
12 | 0.0065078 | 0.001631
13 | 0.0031515 | 0.00078985
14 | 0.010071 | 0.0025241
15 | 0.013332 | 0.0033414
16 | 0.021421 | 0.0053687
17 | 0.019128 | 0.004794
18 | 0.0017324 | 0.00043418
19 | 0.0031765 | 0.0007961
20 | 0.0013663 | 0.00034244
21 | 0.0020576 | 0.0005157
22 | 0.00263 | 0.00065914
23 | 0.0026133 | 0.00065497
24 | 0.010699 | 0.0026815
25 | 0.0066809 | 0.0016744
26 | 0.0023347 | 0.00058512
27 | 0.0024194 | 0.00060635
28 | 0.0073592 | 0.0018444
29 | 0.002138 | 0.00053583
30 | 0.0017142 | 0.00042963
31 | 0.0016566 | 0.00041519
32 | 0.00236 | 0.00059147
33 | 0.0020842 | 0.00052236
34 | 0.0029923 | 0.00074994
35 | 0.0020758 | 0.00052026
36 | 0.0065864 | 0.0016507
37 | 0.012613 | 0.003161
38 | 0.0033415 | 0.00083746
39 | 0.0032924 | 0.00082516
40 | 0.0020406 | 0.00051143
41 | 0.0056301 | 0.001411
42 | 0.0061395 | 0.0015387
43 | 0.011547 | 0.002894
44 | 0.0024047 | 0.00060268
45 | 0.0036445 | 0.00091339
46 | 0.0025848 | 0.00064782
47 | 0.0068321 | 0.0017123

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1