## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1059-65_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1059-65_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1059-65_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1059-65_0_2_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_1059-65_0_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1059-65_0_2_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_1059-65_0_2_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1059-65_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1059-65_0_2_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1059-65_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1059-65_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1059-65_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1059-65_0_2_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1059-65_0_2_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1059-65_0_2_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1059-65_0_2_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1059-65_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_MV_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1059-65_0_2_load_0 | 0 | 0.00022812 | 5.7173e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1059-65_0_2_load_2 | 2 | 0.00069201 | 0.00017343 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1059-65_0_2_load_15 | 3 | 0.00031134 | 7.8029e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1059-65_0_2_load_13 | 6 | 0.0011223 | 0.00028128 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1059-65_0_2_load_4 | 8 | 0.001295 | 0.00032455 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1059-65_0_2_load_7 | 9 | 0.00010341 | 2.5916e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1059-65_0_2_load_5 | 10 | 0.00124 | 0.00031076 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1059-65_0_2_load_8 | 11 | 0.0005086 | 0.00012747 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1059-65_0_2_load_9 | 12 | 0.0072169 | 0.0018087 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1059-65_0_2_load_14 | 15 | 0.0018835 | 0.00047204 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1059-65_0_2_load_12 | 16 | 0.0099631 | 0.002497 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1059-65_0_2_line_0 |  | 0 | 1 | 0.064116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1059-65_0_2_line_1 |  | 0 | 2 | 0.35984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1059-65_0_2_line_2 |  | 1 | 3 | 0.40083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1059-65_0_2_line_3 |  | 2 | 4 | 0.0064894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1059-65_0_2_line_4 |  | 3 | 5 | 0.083555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1059-65_0_2_line_5 |  | 4 | 7 | 0.042599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1059-65_0_2_line_6 |  | 4 | 8 | 0.059861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1059-65_0_2_line_7 |  | 5 | 6 | 0.58128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1059-65_0_2_line_8 |  | 6 | 16 | 0.030464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1059-65_0_2_line_9 |  | 7 | 9 | 0.006023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1059-65_0_2_line_10 |  | 8 | 10 | 0.01913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1059-65_0_2_line_11 |  | 9 | 11 | 0.036827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1059-65_0_2_line_12 |  | 12 | 13 | 0.1882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1059-65_0_2_line_13 |  | 13 | 14 | 0.17347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1059-65_0_2_line_14 |  | 14 | 15 | 0.22432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1059-65_0_2_line_15 |  | 15 | 16 | 0.053884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1059-65_0_2_trafo_13 | 0.63 MVA 20/0.4 kV | 17 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2660369.9169 | 1209007.0996 | 2660366.1779 | 1209009.9969 | 2660363.9509 | 1209013.7211 | 2660362.3124 | 1209020.8866 | 2660363.6445 | 1209028.2267 | 2660366.2448 | 1209034.1899 | 2660373.2058 | 1209042.6765 | 2660385.0051 | 1209052.3239 | 2660391.0142 | 1209056.8341
1 | 2660160.557 | 1209333.1938 | 2660391.0142 | 1209056.8341
2 | 2660369.9169 | 1209007.0996 | 2660103.1298 | 1208707.9519
3 | 2660155.5453 | 1209337.1901 | 2660158.1902 | 1209335.727 | 2660160.557 | 1209333.1938 | 2660160.557 | 1209333.1938
4 | 2660028.5973 | 1208745.1561 | 2660035.7691 | 1208743.3494 | 2660043.7215 | 1208740.283 | 2660103.1298 | 1208707.9519
5 | 2660155.5453 | 1209337.1901 | 2660153.0602 | 1209337.1317 | 2660150.268 | 1209336.6255 | 2660145.7605 | 1209335.1014 | 2660126.941 | 1209326.629 | 2660115.8662 | 1209322.048
6 | 2660155.5453 | 1209337.1901 | 2660158.2653 | 1209351.6485 | 2660179.8157 | 1209381.7616 | 2660184.1623 | 1209388.6188
7 | 2660028.5973 | 1208745.1561 | 2659504.395 | 1208996.3507
8 | 2659474.5362 | 1208990.362 | 2659482.3931 | 1208991.5709 | 2659504.395 | 1208996.3507
9 | 2660115.8662 | 1209322.048 | 2660115.4757 | 1209320.0651 | 2660114.8062 | 1209318.613 | 2660113.1018 | 1209316.919
10 | 2660184.1623 | 1209388.6188 | 2660194.4039 | 1209404.7758
11 | 2660113.1018 | 1209316.919 | 2660095.7425 | 1209299.6653 | 2660086.6159 | 1209291.3426
12 | 2659191.0286 | 1208707.9717 | 2659174.7274 | 1208710.4783 | 2659129.1398 | 1208727.8148 | 2659110.1789 | 1208742.5026 | 2659104.5205 | 1208757.3221 | 2659104.322 | 1208777.3655 | 2659109.0427 | 1208791.9654 | 2659134.5703 | 1208832.2573
13 | 2659191.0286 | 1208707.9717 | 2659193.2517 | 1208719.1449 | 2659209.6134 | 1208758.0416 | 2659214.0676 | 1208772.6723 | 2659215.0065 | 1208788.3688 | 2659213.4894 | 1208838.595 | 2659215.8648 | 1208853.5609 | 2659219.6508 | 1208865.0275 | 2659225.2845 | 1208874.9227
14 | 2659225.2845 | 1208874.9227 | 2659238.2362 | 1208887.392 | 2659250.7604 | 1208896.2104 | 2659275.6383 | 1208908.7983 | 2659323.3762 | 1208928.94 | 2659355.7859 | 1208945.4943 | 2659397.5063 | 1208970.6021 | 2659418.0576 | 1208980.1901 | 2659421.5017 | 1208981.0983
15 | 2659474.5362 | 1208990.362 | 2659431.5536 | 1208983.7488 | 2659421.5017 | 1208981.0983

## bus_geodata
| x | y | coords
0 | 2660391.0142 | 1209056.8341
1 | 2660369.9169 | 1209007.0996
2 | 2660160.557 | 1209333.1938
3 | 2660103.1298 | 1208707.9519
4 | 2660155.5453 | 1209337.1901
5 | 2660028.5973 | 1208745.1561
6 | 2659504.395 | 1208996.3507
7 | 2660115.8662 | 1209322.048
8 | 2660184.1623 | 1209388.6188
9 | 2660113.1018 | 1209316.919
10 | 2660194.4039 | 1209404.7758
11 | 2660086.6159 | 1209291.3426
12 | 2659134.5703 | 1208832.2573
13 | 2659191.0286 | 1208707.9717
14 | 2659225.2845 | 1208874.9227
15 | 2659421.5017 | 1208981.0983
16 | 2659474.5362 | 1208990.362
17 | 2659504.395 | 1208996.3507

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99563 | -0.084784 | 0.00022812 | 5.7173e-05
1 | 0.99587 | -0.080179 | 0 | 0
2 | 0.99437 | -0.10918 | 0.00069201 | 0.00017343
3 | 0.99735 | -0.051386 | 0.00031134 | 7.8029e-05
4 | 0.99435 | -0.10954 | 0 | 0
5 | 0.99768 | -0.044927 | 0 | 0
6 | 1 | 0 | -0.025152 | -0.0058836
7 | 0.99433 | -0.11 | 0 | 0
8 | 0.99421 | -0.11222 | 0.001295 | 0.00032455
9 | 0.99432 | -0.11006 | 0.00010341 | 2.5916e-05
10 | 0.99419 | -0.11263 | 0.00124 | 0.00031076
11 | 0.99431 | -0.1104 | 0.0005086 | 0.00012747
12 | 0.99517 | -0.092958 | 0.0072169 | 0.0018087
13 | 0.99641 | -0.069074 | 0 | 0
14 | 0.99755 | -0.047093 | 0 | 0
15 | 0.99903 | -0.018718 | 0.0018835 | 0.00047204
16 | 0.99947 | -0.010139 | 0.0099631 | 0.002497
17 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0040719 | -0.0010155 | 0.0040728 | 0.0010153 | 8.8991e-07 | -2.6448e-07 | 0.0060839 | 0.0060836 | 0.0060839 | 0.99563 | -0.084784 | 0.99587 | -0.080179 | 1.6714
1 | 0.0038438 | 0.00095835 | -0.0038393 | -0.00096018 | 4.4519e-06 | -1.8246e-06 | 0.005743 | 0.0057446 | 0.0057446 | 0.99563 | -0.084784 | 0.99437 | -0.10918 | 1.5782
2 | -0.0040728 | -0.0010153 | 0.0040784 | 0.0010136 | 5.5614e-06 | -1.6637e-06 | 0.0060836 | 0.0060818 | 0.0060836 | 0.99587 | -0.080179 | 0.99735 | -0.051386 | 1.6713
3 | 0.0031473 | 0.00078674 | -0.0031473 | -0.00078679 | 5.3965e-08 | -4.9642e-08 | 0.0047091 | 0.0047091 | 0.0047091 | 0.99437 | -0.10918 | 0.99435 | -0.10954 | 1.2937
4 | -0.0043897 | -0.0010916 | 0.004391 | 0.0010914 | 1.3427e-06 | -2.3143e-07 | 0.0065463 | 0.0065459 | 0.0065463 | 0.99735 | -0.051386 | 0.99768 | -0.044927 | 1.7984
5 | 0.00061203 | 0.00015229 | -0.00061202 | -0.00015283 | 1.3392e-08 | -5.4399e-07 | 0.0009155 | 0.00091569 | 0.00091569 | 0.99435 | -0.10954 | 0.99433 | -0.11 | 0.25156
6 | 0.0025353 | 0.0006345 | -0.0025349 | -0.00063507 | 3.2308e-07 | -5.696e-07 | 0.0037936 | 0.0037939 | 0.0037939 | 0.99435 | -0.10954 | 0.99421 | -0.11222 | 1.0423
7 | -0.004391 | -0.0010914 | 0.0044004 | 0.0010898 | 9.3365e-06 | -1.633e-06 | 0.0065459 | 0.0065433 | 0.0065459 | 0.99768 | -0.044927 | 1 | 0 | 1.7983
8 | 0.019102 | 0.0047937 | -0.019093 | -0.0047882 | 9.2315e-06 | 5.5087e-06 | 0.028426 | 0.028427 | 0.028427 | 1 | 0 | 0.99947 | -0.010139 | 7.8095
9 | 0.00061202 | 0.00015283 | -0.00061201 | -0.00015291 | 1.8939e-09 | -7.6911e-08 | 0.00091569 | 0.00091572 | 0.00091572 | 0.99433 | -0.11 | 0.99432 | -0.11006 | 0.25157
10 | 0.00124 | 0.00031053 | -0.00124 | -0.00031076 | 2.4706e-08 | -2.3225e-07 | 0.0018558 | 0.0018558 | 0.0018558 | 0.99421 | -0.11222 | 0.99419 | -0.11263 | 0.50985
11 | 0.00050861 | 0.00012699 | -0.0005086 | -0.00012747 | 7.9988e-09 | -4.7255e-07 | 0.00076097 | 0.00076114 | 0.00076114 | 0.99432 | -0.11006 | 0.99431 | -0.1104 | 0.2091
12 | -0.0072169 | -0.0018087 | 0.0072252 | 0.0018115 | 8.2175e-06 | 2.8109e-06 | 0.010791 | 0.01079 | 0.010791 | 0.99517 | -0.092958 | 0.99641 | -0.069074 | 2.9646
13 | -0.0072252 | -0.0018115 | 0.0072327 | 0.0018141 | 7.5733e-06 | 2.5848e-06 | 0.01079 | 0.010789 | 0.01079 | 0.99641 | -0.069074 | 0.99755 | -0.047093 | 2.9643
14 | -0.0072327 | -0.0018141 | 0.0072425 | 0.0018175 | 9.7913e-06 | 3.3336e-06 | 0.010789 | 0.010788 | 0.010789 | 0.99755 | -0.047093 | 0.99903 | -0.018718 | 2.9641
15 | -0.009126 | -0.0022895 | 0.0091297 | 0.0022912 | 3.7338e-06 | 1.6838e-06 | 0.013594 | 0.013593 | 0.013594 | 0.99903 | -0.018718 | 0.99947 | -0.010139 | 3.7345

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.026275 | 0.0061649

## res_load
| p_mw | q_mvar
0 | 0.00022812 | 5.7173e-05
1 | 0.00069201 | 0.00017343
2 | 0.00031134 | 7.8029e-05
3 | 0.0011223 | 0.00028128
4 | 0.001295 | 0.00032455
5 | 0.00010341 | 2.5916e-05
6 | 0.00124 | 0.00031076
7 | 0.0005086 | 0.00012747
8 | 0.0072169 | 0.0018087
9 | 0.0018835 | 0.00047204
10 | 0.0099631 | 0.002497

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1