## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-115_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-115_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-115_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-115_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-115_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-115_0_5_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_1061-115_0_5_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1061-115_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1061-115_0_5_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1061-115_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1061-115_0_5_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1061-115_0_5_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_1061-115_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1061-115_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1061-115_0_5_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_1061-115_0_5_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_1061-115_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1061-115_0_5_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_1061-115_0_5_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_1061-115_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1061-115_0_5_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_1061-115_0_5_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_1061-115_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1061-115_0_5_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1061-115_0_5_node_5 | 0.4 | n |  | TRUE
25 | bus_LV_1061-115_0_5_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1061-115_0_5_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1061-115_0_5_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_1061-115_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1061-115_0_5_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1061-115_0_5_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_1061-115_0_5_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1061-115_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1061-115_0_5_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1061-115_0_5_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1061-115_0_5_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1061-115_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1061-115_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1061-115_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1061-115_0_5_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_1061-115_0_5_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_1061-115_0_5_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_1061-115_0_5_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_1061-115_0_5_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_1061-115_0_5_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_1061-115_0_5_node_44 | 0.4 | n |  | TRUE
46 | bus_MV_215_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-115_0_5_load_0 | 0 | 0.033645 | 0.0084324 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-115_0_5_load_1 | 1 | 0.0078145 | 0.0019585 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-115_0_5_load_2 | 2 | 0.0034487 | 0.00086433 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-115_0_5_load_3 | 3 | 0.0087713 | 0.0021983 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-115_0_5_load_21 | 6 | 0.0034124 | 0.00085523 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-115_0_5_load_29 | 8 | 0.012146 | 0.0030441 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-115_0_5_load_22 | 11 | 0.0074966 | 0.0018788 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-115_0_5_load_42 | 14 | 0.13623 | 0.034142 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-115_0_5_load_40 | 15 | 0.0076383 | 0.0019143 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-115_0_5_load_39 | 17 | 0.054342 | 0.013619 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-115_0_5_load_47 | 18 | 0.0088 | 0.0022055 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-115_0_5_load_41 | 20 | 0.006813 | 0.0017075 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-115_0_5_load_33 | 21 | 0.0086648 | 0.0021716 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-115_0_5_load_32 | 23 | 0.02241 | 0.0056166 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-115_0_5_load_5 | 24 | 0.0066495 | 0.0016665 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-115_0_5_load_23 | 25 | 0.0051216 | 0.0012836 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-115_0_5_load_20 | 26 | 0.010466 | 0.0026229 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-115_0_5_load_17 | 28 | 0.024864 | 0.0062316 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-115_0_5_load_18 | 29 | 0.029262 | 0.0073338 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-115_0_5_load_46 | 30 | 0.0060931 | 0.0015271 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-115_0_5_load_30 | 31 | 0.020445 | 0.0051241 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-115_0_5_load_19 | 32 | 0.013657 | 0.0034228 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-115_0_5_load_25 | 33 | 0.0069609 | 0.0017446 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-115_0_5_load_26 | 34 | 0.0089884 | 0.0022527 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-115_0_5_load_35 | 35 | 0.00088164 | 0.00022096 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-115_0_5_load_28 | 36 | 0.005532 | 0.0013864 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-115_0_5_load_24 | 37 | 0.00586 | 0.0014686 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-115_0_5_load_27 | 38 | 0.0052203 | 0.0013083 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-115_0_5_load_45 | 39 | 0.0065957 | 0.001653 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-115_0_5_load_43 | 40 | 0.0092519 | 0.0023187 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-115_0_5_load_31 | 41 | 0.025925 | 0.0064975 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-115_0_5_load_36 | 42 | 0.020322 | 0.0050933 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-115_0_5_load_37 | 43 | 0.01124 | 0.0028171 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1061-115_0_5_load_38 | 44 | 0.01199 | 0.003005 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1061-115_0_5_load_44 | 45 | 0.0059649 | 0.001495 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-115_0_5_line_0 |  | 0 | 1 | 0.031242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1061-115_0_5_line_1 |  | 0 | 2 | 0.036744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1061-115_0_5_line_2 |  | 1 | 3 | 0.012762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1061-115_0_5_line_3 |  | 2 | 4 | 0.023306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1061-115_0_5_line_4 |  | 3 | 5 | 0.0018587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1061-115_0_5_line_5 |  | 4 | 6 | 0.011533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-115_0_5_line_6 |  | 5 | 7 | 0.011137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1061-115_0_5_line_7 |  | 6 | 8 | 0.033951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-115_0_5_line_8 |  | 7 | 18 | 0.024755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1061-115_0_5_line_9 |  | 7 | 19 | 0.062242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1061-115_0_5_line_10 |  | 8 | 36 | 0.0062694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-115_0_5_line_11 |  | 9 | 10 | 0.027256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-115_0_5_line_12 |  | 9 | 11 | 0.019336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-115_0_5_line_13 |  | 9 | 12 | 0.072035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-115_0_5_line_14 |  | 10 | 21 | 0.0030455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-115_0_5_line_15 |  | 11 | 25 | 0.017623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-115_0_5_line_16 |  | 12 | 24 | 0.058865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-115_0_5_line_17 |  | 13 | 14 | 0.003001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-115_0_5_line_18 |  | 13 | 15 | 0.044937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1061-115_0_5_line_19 |  | 13 | 16 | 0.096735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1061-115_0_5_line_20 |  | 15 | 20 | 0.010205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1061-115_0_5_line_21 |  | 16 | 17 | 0.0072589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-115_0_5_line_22 |  | 17 | 22 | 0.0014944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-115_0_5_line_23 |  | 18 | 30 | 0.00046973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1061-115_0_5_line_24 |  | 19 | 20 | 0.038962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1061-115_0_5_line_25 |  | 21 | 27 | 0.045203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-115_0_5_line_26 |  | 22 | 23 | 0.0059341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-115_0_5_line_27 |  | 23 | 31 | 0.0064637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-115_0_5_line_28 |  | 25 | 37 | 0.013815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-115_0_5_line_29 |  | 26 | 27 | 0.0025259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-115_0_5_line_30 |  | 27 | 35 | 0.012736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-115_0_5_line_31 |  | 28 | 29 | 0.0028467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-115_0_5_line_32 |  | 29 | 32 | 0.021317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-115_0_5_line_33 |  | 30 | 45 | 0.007451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1061-115_0_5_line_34 |  | 31 | 41 | 0.019913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1061-115_0_5_line_35 |  | 32 | 33 | 0.023007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1061-115_0_5_line_36 |  | 33 | 34 | 0.004932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1061-115_0_5_line_37 |  | 34 | 39 | 0.0034489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1061-115_0_5_line_38 |  | 35 | 42 | 0.025949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1061-115_0_5_line_39 |  | 36 | 38 | 0.014684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1061-115_0_5_line_40 |  | 37 | 38 | 0.00027236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1061-115_0_5_line_41 |  | 39 | 40 | 0.0061652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1061-115_0_5_line_42 |  | 40 | 45 | 0.0015963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1061-115_0_5_line_43 |  | 42 | 43 | 0.015075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1061-115_0_5_line_44 |  | 43 | 44 | 0.010829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-115_0_5_trafo_19 | 0.63 MVA 20/0.4 kV | 46 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2666434.3255 | 1210432.8749 | 2666425.4323 | 1210446.7116 | 2666420.3937 | 1210454.8716 | 2666417.5434 | 1210459.2257
1 | 2666434.3255 | 1210432.8749 | 2666440.9704 | 1210422.5363 | 2666450.9103 | 1210407.6378 | 2666454.4974 | 1210402.1649
2 | 2666417.5434 | 1210459.2257 | 2666411.1233 | 1210469.0327 | 2666410.5141 | 1210469.8756
3 | 2666465.221 | 1210381.7701 | 2666464.5926 | 1210385.6433 | 2666461.7038 | 1210391.1701 | 2666454.4974 | 1210402.1649
4 | 2666409.4251 | 1210471.3819 | 2666410.5141 | 1210469.8756
5 | 2666465.221 | 1210381.7701 | 2666465.3108 | 1210381.2152 | 2666465.0111 | 1210378.0988 | 2666463.5986 | 1210373.9028 | 2666461.7079 | 1210371.0618
6 | 2666409.4251 | 1210471.3819 | 2666402.8948 | 1210480.4148
7 | 2666434.4006 | 1210351.2341 | 2666442.6618 | 1210356.659 | 2666456.2916 | 1210365.3161 | 2666460.9001 | 1210369.848 | 2666461.7079 | 1210371.0618
8 | 2666402.8948 | 1210480.4148 | 2666382.1997 | 1210466.8314
9 | 2666402.8948 | 1210480.4148 | 2666396.0825 | 1210490.8899 | 2666380.095 | 1210515.1826 | 2666368.8213 | 1210532.5012
10 | 2666429.1602 | 1210347.7928 | 2666434.4006 | 1210351.2341
11 | 2666374.0492 | 1210311.9792 | 2666359.1718 | 1210334.839
12 | 2666374.0492 | 1210311.9792 | 2666378.692 | 1210314.8104 | 2666390.4465 | 1210322.2264
13 | 2666311.0207 | 1210278.3468 | 2666319.6332 | 1210280.2882 | 2666328.9206 | 1210283.7379 | 2666338.4211 | 1210288.5242 | 2666364.2224 | 1210305.7884 | 2666367.2929 | 1210307.846 | 2666369.5424 | 1210309.2274 | 2666374.0492 | 1210311.9792
14 | 2666359.1718 | 1210334.839 | 2666357.6252 | 1210337.4625
15 | 2666405.1627 | 1210331.921 | 2666393.6886 | 1210324.2719 | 2666390.4465 | 1210322.2264
16 | 2666311.0207 | 1210278.3468 | 2666306.0495 | 1210277.7134 | 2666300.3752 | 1210277.4169 | 2666293.3071 | 1210277.3939 | 2666267.8491 | 1210279.8238 | 2666252.4007 | 1210281.4107
17 | 2666298.8658 | 1210499.37 | 2666297.1436 | 1210501.8302
18 | 2666297.1436 | 1210501.8302 | 2666309.9114 | 1210512.1228 | 2666310.5604 | 1210511.1739 | 2666319.1777 | 1210498.9843 | 2666319.8387 | 1210497.6353 | 2666323.7289 | 1210500.4691 | 2666328.7383 | 1210504.0277
19 | 2666248.12 | 1210527.3904 | 2666247.1828 | 1210518.0298 | 2666248.7211 | 1210510.9092 | 2666251.0773 | 1210504.0533 | 2666266.246 | 1210480.8964 | 2666270.0444 | 1210485.1523 | 2666278.5247 | 1210492.1285 | 2666283.2192 | 1210496.45 | 2666293.0659 | 1210507.6662 | 2666297.1436 | 1210501.8302
20 | 2666328.7383 | 1210504.0277 | 2666337.0581 | 1210509.9378
21 | 2666248.12 | 1210527.3904 | 2666245.5448 | 1210525.9165 | 2666243.5179 | 1210522.1336
22 | 2666242.8122 | 1210520.8163 | 2666243.5179 | 1210522.1336
23 | 2666381.807 | 1210466.5736 | 2666382.1997 | 1210466.8314
24 | 2666368.8213 | 1210532.5012 | 2666337.0581 | 1210509.9378
25 | 2666334.6696 | 1210376.4033 | 2666357.6252 | 1210337.4625
26 | 2666242.8122 | 1210520.8163 | 2666240.0721 | 1210515.705 | 2666240.023 | 1210515.5796
27 | 2666237.6652 | 1210509.5613 | 2666240.023 | 1210515.5796
28 | 2666405.1627 | 1210331.921 | 2666416.5179 | 1210339.4908 | 2666416.6581 | 1210339.5829
29 | 2666334.6696 | 1210376.4033 | 2666333.2857 | 1210378.5163
30 | 2666334.6696 | 1210376.4033 | 2666345.414 | 1210383.2423
31 | 2666322.6478 | 1210427.7437 | 2666325.0276 | 1210429.3057
32 | 2666325.0276 | 1210429.3057 | 2666342.8487 | 1210441.0028
33 | 2666375.578 | 1210462.4851 | 2666381.807 | 1210466.5736
34 | 2666237.6652 | 1210509.5613 | 2666230.4013 | 1210491.0203
35 | 2666362.0829 | 1210453.6274 | 2666342.8487 | 1210441.0028
36 | 2666362.0829 | 1210453.6274 | 2666366.2061 | 1210456.3337
37 | 2666369.0894 | 1210458.2262 | 2666366.2061 | 1210456.3337
38 | 2666367.3049 | 1210397.1763 | 2666345.414 | 1210383.2423
39 | 2666429.1602 | 1210347.7928 | 2666416.8858 | 1210339.7324
40 | 2666416.6581 | 1210339.5829 | 2666416.8858 | 1210339.7324
41 | 2666374.2435 | 1210461.6092 | 2666369.0894 | 1210458.2262
42 | 2666374.2435 | 1210461.6092 | 2666375.578 | 1210462.4851
43 | 2666367.3049 | 1210397.1763 | 2666380.022 | 1210405.2709
44 | 2666389.1578 | 1210411.086 | 2666380.022 | 1210405.2709

## bus_geodata
| x | y | coords
0 | 2666434.3255 | 1210432.8749
1 | 2666417.5434 | 1210459.2257
2 | 2666454.4974 | 1210402.1649
3 | 2666410.5141 | 1210469.8756
4 | 2666465.221 | 1210381.7701
5 | 2666409.4251 | 1210471.3819
6 | 2666461.7079 | 1210371.0618
7 | 2666402.8948 | 1210480.4148
8 | 2666434.4006 | 1210351.2341
9 | 2666374.0492 | 1210311.9792
10 | 2666359.1718 | 1210334.839
11 | 2666390.4465 | 1210322.2264
12 | 2666311.0207 | 1210278.3468
13 | 2666297.1436 | 1210501.8302
14 | 2666298.8658 | 1210499.37
15 | 2666328.7383 | 1210504.0277
16 | 2666248.12 | 1210527.3904
17 | 2666243.5179 | 1210522.1336
18 | 2666382.1997 | 1210466.8314
19 | 2666368.8213 | 1210532.5012
20 | 2666337.0581 | 1210509.9378
21 | 2666357.6252 | 1210337.4625
22 | 2666242.8122 | 1210520.8163
23 | 2666240.023 | 1210515.5796
24 | 2666252.4007 | 1210281.4107
25 | 2666405.1627 | 1210331.921
26 | 2666333.2857 | 1210378.5163
27 | 2666334.6696 | 1210376.4033
28 | 2666322.6478 | 1210427.7437
29 | 2666325.0276 | 1210429.3057
30 | 2666381.807 | 1210466.5736
31 | 2666237.6652 | 1210509.5613
32 | 2666342.8487 | 1210441.0028
33 | 2666362.0829 | 1210453.6274
34 | 2666366.2061 | 1210456.3337
35 | 2666345.414 | 1210383.2423
36 | 2666429.1602 | 1210347.7928
37 | 2666416.6581 | 1210339.5829
38 | 2666416.8858 | 1210339.7324
39 | 2666369.0894 | 1210458.2262
40 | 2666374.2435 | 1210461.6092
41 | 2666230.4013 | 1210491.0203
42 | 2666367.3049 | 1210397.1763
43 | 2666380.022 | 1210405.2709
44 | 2666389.1578 | 1210411.086
45 | 2666375.578 | 1210462.4851
46 | 2666307.5396 | 1210417.8273

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98974 | -0.19483 | 0.033645 | 0.0084324
1 | 0.99121 | -0.16668 | 0.0078145 | 0.0019585
2 | 0.98839 | -0.22068 | 0.0034487 | 0.00086433
3 | 0.99168 | -0.15763 | 0.0087713 | 0.0021983
4 | 0.98756 | -0.23663 | 0 | 0
5 | 0.99175 | -0.15624 | 0 | 0
6 | 0.98633 | -0.26037 | 0.0034124 | 0.00085523
7 | 0.99219 | -0.14792 | 0 | 0
8 | 0.98281 | -0.3285 | 0.012146 | 0.0030441
9 | 0.97731 | -0.43554 | 0 | 0
10 | 0.97569 | -0.46721 | 0 | 0
11 | 0.97858 | -0.41079 | 0.0074966 | 0.0018788
12 | 0.97687 | -0.44429 | 0 | 0
13 | 0.9797 | -0.38885 | 0 | 0
14 | 0.97932 | -0.39628 | 0.13623 | 0.034142
15 | 0.98512 | -0.28361 | 0.0076383 | 0.0019143
16 | 0.97415 | -0.49761 | 0 | 0
17 | 0.97332 | -0.51404 | 0.054342 | 0.013619
18 | 0.99473 | -0.099559 | 0.0088 | 0.0022055
19 | 0.98823 | -0.22366 | 0 | 0
20 | 0.98575 | -0.27138 | 0.006813 | 0.0017075
21 | 0.97551 | -0.47075 | 0.0086648 | 0.0021716
22 | 0.97322 | -0.51593 | 0 | 0
23 | 0.97284 | -0.52345 | 0.02241 | 0.0056166
24 | 0.9765 | -0.45144 | 0.0066495 | 0.0016665
25 | 0.97985 | -0.38589 | 0.0051216 | 0.0012836
26 | 0.97317 | -0.5168 | 0.010466 | 0.0026229
27 | 0.9732 | -0.51632 | 0 | 0
28 | 0.99889 | -0.021368 | 0.024864 | 0.0062316
29 | 0.99895 | -0.020131 | 0.029262 | 0.0073338
30 | 0.99478 | -0.098625 | 0.0060931 | 0.0015271
31 | 0.97256 | -0.52897 | 0.020445 | 0.0051241
32 | 1 | 0 | -0.5602 | -0.14358
33 | 0.99736 | -0.049776 | 0.0069609 | 0.0017446
34 | 0.9968 | -0.06033 | 0.0089884 | 0.0022527
35 | 0.97267 | -0.52674 | 0.00088164 | 0.00022096
36 | 0.98223 | -0.33975 | 0.005532 | 0.0013864
37 | 0.98092 | -0.36514 | 0.00586 | 0.0014686
38 | 0.98094 | -0.3647 | 0.0052203 | 0.0013083
39 | 0.99642 | -0.067581 | 0.0065957 | 0.001653
40 | 0.99574 | -0.080378 | 0.0092519 | 0.0023187
41 | 0.97208 | -0.53849 | 0.025925 | 0.0064975
42 | 0.97161 | -0.54758 | 0.020322 | 0.0050933
43 | 0.97129 | -0.55405 | 0.01124 | 0.0028171
44 | 0.97117 | -0.55645 | 0.01199 | 0.003005
45 | 0.99557 | -0.08363 | 0.0059649 | 0.001495
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.15357 | -0.039057 | 0.15378 | 0.039189 | 0.00020856 | 0.00013227 | 0.23109 | 0.23109 | 0.23109 | 0.98974 | -0.19483 | 0.99121 | -0.16668 | 21.1623
1 | 0.11993 | 0.030625 | -0.11978 | -0.03053 | 0.00014965 | 9.4364e-05 | 0.18051 | 0.18051 | 0.18051 | 0.98974 | -0.19483 | 0.98839 | -0.22068 | 16.5302
2 | -0.1616 | -0.041148 | 0.16167 | 0.041192 | 7.0543e-05 | 4.4489e-05 | 0.24282 | 0.24282 | 0.24282 | 0.99121 | -0.16668 | 0.99168 | -0.15763 | 16.6774
3 | 0.11633 | 0.029666 | -0.11624 | -0.02961 | 8.9543e-05 | 5.6412e-05 | 0.17532 | 0.17532 | 0.17532 | 0.98839 | -0.22068 | 0.98756 | -0.23663 | 16.0548
4 | -0.17044 | -0.043391 | 0.17045 | 0.043398 | 1.1419e-05 | 7.212e-06 | 0.25598 | 0.25598 | 0.25598 | 0.99168 | -0.15763 | 0.99175 | -0.15624 | 17.5813
5 | 0.11624 | 0.02961 | -0.11611 | -0.029525 | 0.00013293 | 8.4927e-05 | 0.17532 | 0.17532 | 0.17532 | 0.98756 | -0.23663 | 0.98633 | -0.26037 | 48.1643
6 | -0.17045 | -0.043398 | 0.17052 | 0.043441 | 6.8417e-05 | 4.3212e-05 | 0.25598 | 0.25598 | 0.25598 | 0.99175 | -0.15624 | 0.99219 | -0.14792 | 17.5813
7 | 0.1127 | 0.02867 | -0.11233 | -0.028434 | 0.00036868 | 0.00023553 | 0.17017 | 0.17017 | 0.17017 | 0.98633 | -0.26037 | 0.98281 | -0.3285 | 46.75
8 | -0.44829 | -0.11459 | 0.44934 | 0.11526 | 0.0010515 | 0.00067168 | 0.67312 | 0.67312 | 0.67312 | 0.99219 | -0.14792 | 0.99473 | -0.099559 | 46.2306
9 | 0.27777 | 0.071152 | -0.27676 | -0.070505 | 0.0010153 | 0.0006466 | 0.41713 | 0.41713 | 0.41713 | 0.99219 | -0.14792 | 0.98823 | -0.22366 | 28.6493
10 | 0.10018 | 0.02539 | -0.10013 | -0.025355 | 5.4161e-05 | 3.4583e-05 | 0.15178 | 0.15178 | 0.15178 | 0.98281 | -0.3285 | 0.98223 | -0.33975 | 41.6978
11 | 0.063866 | 0.016122 | -0.06377 | -0.016061 | 9.673e-05 | 6.1566e-05 | 0.097282 | 0.097283 | 0.097283 | 0.97731 | -0.43554 | 0.97569 | -0.46721 | 26.726
12 | -0.070521 | -0.01779 | 0.070605 | 0.017844 | 8.3662e-05 | 5.3301e-05 | 0.10741 | 0.10741 | 0.10741 | 0.97731 | -0.43554 | 0.97858 | -0.41079 | 29.5095
13 | 0.0066546 | 0.0016681 | -0.0066518 | -0.0016672 | 2.7733e-06 | 8.7265e-07 | 0.010132 | 0.010132 | 0.010132 | 0.97731 | -0.43554 | 0.97687 | -0.44429 | 2.7836
14 | 0.06377 | 0.016061 | -0.063759 | -0.016054 | 1.0808e-05 | 6.8792e-06 | 0.097283 | 0.097283 | 0.097283 | 0.97569 | -0.46721 | 0.97551 | -0.47075 | 26.726
15 | -0.078101 | -0.019722 | 0.078195 | 0.019782 | 9.3295e-05 | 5.9487e-05 | 0.11881 | 0.11881 | 0.11881 | 0.97858 | -0.41079 | 0.97985 | -0.38589 | 32.6411
16 | 0.0066518 | 0.0016672 | -0.0066495 | -0.0016665 | 2.2664e-06 | 7.138e-07 | 0.010132 | 0.010133 | 0.010133 | 0.97687 | -0.44429 | 0.9765 | -0.45144 | 2.7837
17 | 0.13628 | 0.034173 | -0.13623 | -0.034142 | 4.8218e-05 | 3.0821e-05 | 0.20699 | 0.20699 | 0.20699 | 0.9797 | -0.38885 | 0.97932 | -0.39628 | 56.866
18 | -0.2602 | -0.065536 | 0.26151 | 0.066378 | 0.0013167 | 0.00084156 | 0.39531 | 0.39531 | 0.39531 | 0.9797 | -0.38885 | 0.98512 | -0.28361 | 54.3013
19 | 0.12392 | 0.031363 | -0.12327 | -0.030954 | 0.00064327 | 0.00040927 | 0.18832 | 0.18832 | 0.18832 | 0.9797 | -0.38885 | 0.97415 | -0.49761 | 25.8685
20 | -0.26915 | -0.068292 | 0.26931 | 0.068393 | 0.00015837 | 0.00010084 | 0.40685 | 0.40685 | 0.40685 | 0.98512 | -0.28361 | 0.98575 | -0.27138 | 27.9431
21 | 0.12327 | 0.030954 | -0.12318 | -0.030892 | 9.654e-05 | 6.1695e-05 | 0.18832 | 0.18832 | 0.18832 | 0.97415 | -0.49761 | 0.97332 | -0.51404 | 51.737
22 | 0.068836 | 0.017273 | -0.06883 | -0.017269 | 6.2072e-06 | 3.954e-06 | 0.10524 | 0.10524 | 0.10524 | 0.97332 | -0.51404 | 0.97322 | -0.51593 | 28.9133
23 | -0.45814 | -0.11747 | 0.45816 | 0.11748 | 2.0741e-05 | 1.325e-05 | 0.68628 | 0.68628 | 0.68628 | 0.99473 | -0.099559 | 0.99478 | -0.098625 | 47.1346
24 | 0.27676 | 0.070505 | -0.27612 | -0.070101 | 0.00063557 | 0.00040477 | 0.41713 | 0.41714 | 0.41714 | 0.98823 | -0.22366 | 0.98575 | -0.27138 | 28.6494
25 | 0.055094 | 0.013882 | -0.054974 | -0.013806 | 0.0001198 | 7.6106e-05 | 0.084066 | 0.084066 | 0.084066 | 0.97551 | -0.47075 | 0.9732 | -0.51632 | 23.095
26 | 0.06883 | 0.017269 | -0.068805 | -0.017253 | 2.4648e-05 | 1.5701e-05 | 0.10524 | 0.10524 | 0.10524 | 0.97322 | -0.51593 | 0.97284 | -0.52345 | 28.9133
27 | 0.046395 | 0.011637 | -0.046382 | -0.011629 | 1.2207e-05 | 7.7324e-06 | 0.070966 | 0.070966 | 0.070966 | 0.97284 | -0.52345 | 0.97256 | -0.52897 | 19.4963
28 | -0.083316 | -0.021065 | 0.083399 | 0.021118 | 8.302e-05 | 5.2959e-05 | 0.12659 | 0.12659 | 0.12659 | 0.97985 | -0.38589 | 0.98092 | -0.36514 | 34.7779
29 | -0.010466 | -0.0026229 | 0.010466 | 0.002623 | 2.4255e-07 | 1.2385e-07 | 0.016002 | 0.016002 | 0.016002 | 0.97317 | -0.5168 | 0.9732 | -0.51632 | 4.3962
30 | 0.044509 | 0.011183 | -0.044486 | -0.011169 | 2.2126e-05 | 1.4003e-05 | 0.068064 | 0.068064 | 0.068064 | 0.9732 | -0.51632 | 0.97267 | -0.52674 | 18.6988
31 | -0.024864 | -0.0062316 | 0.024866 | 0.0062325 | 1.4645e-06 | 9.0004e-07 | 0.03704 | 0.03704 | 0.03704 | 0.99889 | -0.021368 | 0.99895 | -0.020131 | 10.1757
32 | -0.054128 | -0.013566 | 0.05418 | 0.013599 | 5.1967e-05 | 3.2979e-05 | 0.080628 | 0.080628 | 0.080628 | 0.99895 | -0.020131 | 1 | 0 | 22.1505
33 | -0.46426 | -0.11901 | 0.4646 | 0.11923 | 0.00033779 | 0.0002158 | 0.69539 | 0.69539 | 0.69539 | 0.99478 | -0.098625 | 0.99557 | -0.08363 | 47.7606
34 | 0.025937 | 0.0065048 | -0.025925 | -0.0064975 | 1.1761e-05 | 7.2799e-06 | 0.039685 | 0.039685 | 0.039685 | 0.97256 | -0.52897 | 0.97208 | -0.53849 | 10.9026
35 | 0.50437 | 0.12998 | -0.50315 | -0.1292 | 0.0012191 | 0.000779 | 0.75179 | 0.75179 | 0.75179 | 1 | 0 | 0.99736 | -0.049776 | 51.6337
36 | 0.49619 | 0.12746 | -0.49594 | -0.12729 | 0.00025416 | 0.0001624 | 0.7414 | 0.7414 | 0.7414 | 0.99736 | -0.049776 | 0.9968 | -0.06033 | 50.9205
37 | 0.48695 | 0.12504 | -0.48678 | -0.12493 | 0.00017135 | 0.00010949 | 0.72798 | 0.72798 | 0.72798 | 0.9968 | -0.06033 | 0.99642 | -0.067581 | 49.9989
38 | 0.043605 | 0.010948 | -0.043561 | -0.010921 | 4.3312e-05 | 2.7398e-05 | 0.066715 | 0.066715 | 0.066715 | 0.97267 | -0.52674 | 0.97161 | -0.54758 | 18.3283
39 | 0.094595 | 0.023969 | -0.094481 | -0.023897 | 0.00011324 | 7.2285e-05 | 0.1434 | 0.1434 | 0.1434 | 0.98223 | -0.33975 | 0.98094 | -0.3647 | 39.3955
40 | -0.089259 | -0.022587 | 0.089261 | 0.022588 | 1.8747e-06 | 1.1964e-06 | 0.13548 | 0.13548 | 0.13548 | 0.98092 | -0.36514 | 0.98094 | -0.3647 | 37.22
41 | 0.48018 | 0.12328 | -0.47989 | -0.12309 | 0.00029808 | 0.00019045 | 0.71813 | 0.71813 | 0.71813 | 0.99642 | -0.067581 | 0.99574 | -0.080378 | 49.3224
42 | 0.47063 | 0.12077 | -0.47056 | -0.12072 | 7.4237e-05 | 4.7429e-05 | 0.70431 | 0.70431 | 0.70431 | 0.99574 | -0.080378 | 0.99557 | -0.08363 | 48.3729
43 | 0.023239 | 0.0058272 | -0.023232 | -0.0058228 | 7.1609e-06 | 4.3964e-06 | 0.035591 | 0.035591 | 0.035591 | 0.97161 | -0.54758 | 0.97129 | -0.55405 | 9.7779
44 | 0.011992 | 0.0030058 | -0.01199 | -0.003005 | 1.3706e-06 | 7.4318e-07 | 0.018371 | 0.018371 | 0.018371 | 0.97129 | -0.55405 | 0.97117 | -0.55645 | 5.0471

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57386 | 0.147

## res_load
| p_mw | q_mvar
0 | 0.033645 | 0.0084324
1 | 0.0078145 | 0.0019585
2 | 0.0034487 | 0.00086433
3 | 0.0087713 | 0.0021983
4 | 0.0034124 | 0.00085523
5 | 0.012146 | 0.0030441
6 | 0.0074966 | 0.0018788
7 | 0.13623 | 0.034142
8 | 0.0076383 | 0.0019143
9 | 0.054342 | 0.013619
10 | 0.0088 | 0.0022055
11 | 0.006813 | 0.0017075
12 | 0.0086648 | 0.0021716
13 | 0.02241 | 0.0056166
14 | 0.0066495 | 0.0016665
15 | 0.0051216 | 0.0012836
16 | 0.010466 | 0.0026229
17 | 0.024864 | 0.0062316
18 | 0.029262 | 0.0073338
19 | 0.0060931 | 0.0015271
20 | 0.020445 | 0.0051241
21 | 0.013657 | 0.0034228
22 | 0.0069609 | 0.0017446
23 | 0.0089884 | 0.0022527
24 | 0.00088164 | 0.00022096
25 | 0.005532 | 0.0013864
26 | 0.00586 | 0.0014686
27 | 0.0052203 | 0.0013083
28 | 0.0065957 | 0.001653
29 | 0.0092519 | 0.0023187
30 | 0.025925 | 0.0064975
31 | 0.020322 | 0.0050933
32 | 0.01124 | 0.0028171
33 | 0.01199 | 0.003005
34 | 0.0059649 | 0.001495

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1