## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-11_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-11_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-11_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-11_0_5_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_1061-11_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1061-11_0_5_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_1061-11_0_5_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1061-11_0_5_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1061-11_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1061-11_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1061-11_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1061-11_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1061-11_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1061-11_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1061-11_0_5_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1061-11_0_5_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1061-11_0_5_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1061-11_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1061-11_0_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1061-11_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1061-11_0_5_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1061-11_0_5_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_1061-11_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1061-11_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1061-11_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1061-11_0_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1061-11_0_5_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1061-11_0_5_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_1061-11_0_5_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1061-11_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1061-11_0_5_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1061-11_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1061-11_0_5_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1061-11_0_5_node_22 | 0.4 | n |  | TRUE
34 | bus_MV_219_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-11_0_5_load_0 | 0 | 0.042079 | 0.010546 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-11_0_5_load_29 | 3 | 0.015987 | 0.0040067 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-11_0_5_load_35 | 6 | 0.043904 | 0.011003 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-11_0_5_load_26 | 7 | 0.016882 | 0.0042311 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-11_0_5_load_4 | 8 | 0.0074124 | 0.0018577 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-11_0_5_load_5 | 9 | 0.059436 | 0.014896 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-11_0_5_load_7 | 11 | 0.010678 | 0.0026761 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-11_0_5_load_8 | 12 | 0.022501 | 0.0056393 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-11_0_5_load_9 | 13 | 0.0050609 | 0.0012684 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-11_0_5_load_27 | 15 | 0.011167 | 0.0027988 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-11_0_5_load_13 | 17 | 0.012166 | 0.0030491 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-11_0_5_load_10 | 18 | 0.0063826 | 0.0015996 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-11_0_5_load_11 | 19 | 0.0099082 | 0.0024832 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-11_0_5_load_12 | 20 | 0.010831 | 0.0027144 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-11_0_5_load_33 | 21 | 0.021712 | 0.0054414 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-11_0_5_load_15 | 22 | 0.016115 | 0.0040389 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-11_0_5_load_16 | 23 | 0.023905 | 0.0059912 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-11_0_5_load_17 | 24 | 0.013402 | 0.0033589 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-11_0_5_load_18 | 25 | 0.018494 | 0.004635 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-11_0_5_load_19 | 26 | 0.01057 | 0.002649 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-11_0_5_load_34 | 27 | 0.0088683 | 0.0022226 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-11_0_5_load_30 | 28 | 0.014938 | 0.0037438 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-11_0_5_load_31 | 30 | 0.035861 | 0.0089875 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-11_0_5_load_20 | 31 | 0.011395 | 0.0028558 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-11_0_5_load_21 | 32 | 0.024212 | 0.006068 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-11_0_5_line_0 |  | 0 | 1 | 0.0076616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-11_0_5_line_1 |  | 1 | 2 | 0.023511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-11_0_5_line_2 |  | 2 | 3 | 0.0035637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-11_0_5_line_3 |  | 3 | 5 | 0.0099227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-11_0_5_line_4 |  | 4 | 5 | 0.018387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-11_0_5_line_5 |  | 4 | 6 | 0.10619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-11_0_5_line_6 |  | 5 | 7 | 0.02116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-11_0_5_line_7 |  | 7 | 15 | 0.0095682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-11_0_5_line_8 |  | 8 | 9 | 3.9896e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1061-11_0_5_line_9 |  | 8 | 10 | 0.016294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1061-11_0_5_line_10 |  | 9 | 11 | 0.00044636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1061-11_0_5_line_11 |  | 10 | 12 | 0.030266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-11_0_5_line_12 |  | 10 | 13 | 0.018829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-11_0_5_line_13 |  | 11 | 14 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1061-11_0_5_line_14 |  | 12 | 15 | 0.011067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-11_0_5_line_15 |  | 14 | 16 | 0.008563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1061-11_0_5_line_16 |  | 14 | 17 | 0.0049719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1061-11_0_5_line_17 |  | 16 | 21 | 0.011057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1061-11_0_5_line_18 |  | 17 | 19 | 0.010675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1061-11_0_5_line_19 |  | 18 | 19 | 0.0090748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1061-11_0_5_line_20 |  | 18 | 20 | 0.013626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-11_0_5_line_21 |  | 21 | 29 | 0.013279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1061-11_0_5_line_22 |  | 22 | 23 | 0.0062732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-11_0_5_line_23 |  | 22 | 24 | 0.0051123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-11_0_5_line_24 |  | 23 | 25 | 0.0032049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-11_0_5_line_25 |  | 24 | 26 | 0.0047546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-11_0_5_line_26 |  | 25 | 27 | 0.0069011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-11_0_5_line_27 |  | 26 | 28 | 0.0062704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-11_0_5_line_28 |  | 27 | 29 | 0.010791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1061-11_0_5_line_29 |  | 28 | 30 | 0.0018971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-11_0_5_line_30 |  | 29 | 33 | 0.16991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-11_0_5_line_31 |  | 31 | 32 | 0.011172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-11_0_5_line_32 |  | 31 | 33 | 0.016094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-11_0_5_trafo_10 | 0.63 MVA 20/0.4 kV | 34 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2666064.8179 | 1211636.9755 | 2666061.1567 | 1211643.7057
1 | 2666044.285 | 1211625.4188 | 2666061.2169 | 1211634.8454 | 2666063.0888 | 1211635.9779 | 2666064.8179 | 1211636.9755
2 | 2666044.285 | 1211625.4188 | 2666044.8889 | 1211624.4138 | 2666046.1713 | 1211622.3956
3 | 2666051.2593 | 1211613.8778 | 2666047.2321 | 1211620.7263 | 2666046.1713 | 1211622.3956
4 | 2666066.025 | 1211624.7257 | 2666054.8731 | 1211617.5979 | 2666051.2593 | 1211613.8778
5 | 2666066.025 | 1211624.7257 | 2666066.9676 | 1211623.3242 | 2666068.1141 | 1211621.3468 | 2666069.669 | 1211618.1731 | 2666013.6734 | 1211536.9118
6 | 2666051.2593 | 1211613.8778 | 2666048.9076 | 1211611.4614 | 2666033.1135 | 1211603.2782
7 | 2666024.6179 | 1211598.8765 | 2666033.1135 | 1211603.2782
8 | 2665981.3862 | 1211597.3457 | 2665981.3766 | 1211597.3844
9 | 2665986.9539 | 1211582.0578 | 2665982.2088 | 1211594.0461 | 2665981.3862 | 1211597.3457
10 | 2665981.3766 | 1211597.3844 | 2665981.2686 | 1211597.8175
11 | 2665986.9539 | 1211582.0578 | 2666004.5273 | 1211588.4672 | 2666014.7915 | 1211593.7853
12 | 2665986.9539 | 1211582.0578 | 2665969.4364 | 1211575.1536
13 | 2665977.7564 | 1211611.8634 | 2665978.5272 | 1211608.8145 | 2665981.2686 | 1211597.8175
14 | 2666014.7915 | 1211593.7853 | 2666024.6179 | 1211598.8765
15 | 2665977.7564 | 1211611.8634 | 2665969.4603 | 1211609.6481
16 | 2665977.7564 | 1211611.8634 | 2665982.6511 | 1211612.7363
17 | 2665969.4603 | 1211609.6481 | 2665968.9633 | 1211611.2992 | 2665966.6492 | 1211619.2229 | 2665966.3485 | 1211620.2579
18 | 2665982.6511 | 1211612.7363 | 2665993.1602 | 1211614.6104
19 | 2666002.094 | 1211616.2036 | 2665993.1602 | 1211614.6104
20 | 2666002.094 | 1211616.2036 | 2666009.6612 | 1211617.5531 | 2666015.1755 | 1211619.7594
21 | 2665962.6442 | 1211633.0094 | 2665965.725 | 1211622.4035 | 2665966.3485 | 1211620.2579
22 | 2665982.4539 | 1211639.6582 | 2665988.3043 | 1211641.9223
23 | 2665993.072 | 1211643.7675 | 2665988.3043 | 1211641.9223
24 | 2665982.4539 | 1211639.6582 | 2665981.6165 | 1211639.3341 | 2665979.4279 | 1211638.6045
25 | 2665993.072 | 1211643.7675 | 2665997.5061 | 1211645.4835
26 | 2665979.4279 | 1211638.6045 | 2665972.881 | 1211636.422
27 | 2666003.3538 | 1211647.7466 | 2665997.5061 | 1211645.4835
28 | 2665962.6442 | 1211633.0094 | 2665972.881 | 1211636.422
29 | 2666003.3538 | 1211647.7466 | 2666005.1231 | 1211648.4314
30 | 2665962.6442 | 1211633.0094 | 2665959.2753 | 1211631.8825 | 2665951.2577 | 1211629.2145 | 2665936.661 | 1211622.9938 | 2665926.553 | 1211651.3329 | 2665919.0749 | 1211669.984 | 2665930.461 | 1211676.5583 | 2665952.3676 | 1211688.9525 | 2665974.6373 | 1211699.4162 | 2665981.3326 | 1211700.7133 | 2665985.7355 | 1211699.728 | 2665992.583 | 1211696.8687 | 2666000.7131 | 1211690.7326
31 | 2666014.508 | 1211667.5295 | 2666009.5827 | 1211677.5573
32 | 2666000.7131 | 1211690.7326 | 2666005.4231 | 1211686.0262 | 2666009.5827 | 1211677.5573

## bus_geodata
| x | y | coords
0 | 2666061.1567 | 1211643.7058
1 | 2666064.8179 | 1211636.9755
2 | 2666044.285 | 1211625.4188
3 | 2666046.1713 | 1211622.3956
4 | 2666066.025 | 1211624.7257
5 | 2666051.2593 | 1211613.8778
6 | 2666013.6734 | 1211536.9118
7 | 2666033.1135 | 1211603.2782
8 | 2665981.3863 | 1211597.3457
9 | 2665981.3766 | 1211597.3844
10 | 2665986.9539 | 1211582.0578
11 | 2665981.2686 | 1211597.8175
12 | 2666014.7915 | 1211593.7853
13 | 2665969.4364 | 1211575.1536
14 | 2665977.7564 | 1211611.8634
15 | 2666024.6179 | 1211598.8765
16 | 2665969.4603 | 1211609.6481
17 | 2665982.6511 | 1211612.7363
18 | 2666002.094 | 1211616.2036
19 | 2665993.1602 | 1211614.6104
20 | 2666015.1755 | 1211619.7594
21 | 2665966.3485 | 1211620.2579
22 | 2665988.3043 | 1211641.9223
23 | 2665982.4539 | 1211639.6582
24 | 2665993.072 | 1211643.7675
25 | 2665979.4279 | 1211638.6045
26 | 2665997.5061 | 1211645.4835
27 | 2665972.881 | 1211636.422
28 | 2666003.3538 | 1211647.7466
29 | 2665962.6442 | 1211633.0094
30 | 2666005.1231 | 1211648.4314
31 | 2666009.5827 | 1211677.5573
32 | 2666014.508 | 1211667.5295
33 | 2666000.7131 | 1211690.7326
34 | 2666020.835 | 1211622.0239

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98774 | -0.23589 | 0.042079 | 0.010546
1 | 0.98803 | -0.23014 | 0 | 0
2 | 0.98894 | -0.21249 | 0 | 0
3 | 0.98908 | -0.20982 | 0.015987 | 0.0040067
4 | 0.98887 | -0.21393 | 0 | 0
5 | 0.98961 | -0.19956 | 0 | 0
6 | 0.98457 | -0.2974 | 0.043904 | 0.011003
7 | 0.99159 | -0.16123 | 0.016882 | 0.0042311
8 | 0.99667 | -0.063766 | 0.0074124 | 0.0018577
9 | 0.99667 | -0.063737 | 0.059436 | 0.014896
10 | 0.99608 | -0.075036 | 0 | 0
11 | 0.99669 | -0.063297 | 0.010678 | 0.0026761
12 | 0.99396 | -0.11567 | 0.022501 | 0.0056393
13 | 0.99599 | -0.07671 | 0.0050609 | 0.0012684
14 | 0.99747 | -0.048377 | 0 | 0
15 | 0.99264 | -0.14109 | 0.011167 | 0.0027988
16 | 0.99708 | -0.055861 | 0 | 0
17 | 0.99796 | -0.038919 | 0.012166 | 0.0030491
18 | 1 | 0 | -0.47237 | -0.11922
19 | 0.99905 | -0.018075 | 0.0099082 | 0.0024832
20 | 0.99987 | -0.0025726 | 0.010831 | 0.0027144
21 | 0.99657 | -0.065533 | 0.021712 | 0.0054414
22 | 0.9931 | -0.13254 | 0.016115 | 0.0040389
23 | 0.99362 | -0.12247 | 0.023905 | 0.0059912
24 | 0.99275 | -0.1393 | 0.013402 | 0.0033589
25 | 0.99396 | -0.11598 | 0.018494 | 0.004635
26 | 0.99248 | -0.14446 | 0.01057 | 0.002649
27 | 0.9948 | -0.099767 | 0.0088683 | 0.0022226
28 | 0.99219 | -0.1501 | 0.014938 | 0.0037438
29 | 0.9955 | -0.086268 | 0 | 0
30 | 0.99213 | -0.15131 | 0.035861 | 0.0089875
31 | 0.98942 | -0.20348 | 0.011395 | 0.0028558
32 | 0.98918 | -0.20829 | 0.024212 | 0.006068
33 | 0.98995 | -0.19328 | 0 | 0
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.042079 | -0.010546 | 0.042091 | 0.010553 | 1.1546e-05 | 7.2912e-06 | 0.063392 | 0.063392 | 0.063392 | 0.98774 | -0.23589 | 0.98803 | -0.23014 | 17.4154
1 | -0.042091 | -0.010553 | 0.042126 | 0.010576 | 3.543e-05 | 2.2374e-05 | 0.063392 | 0.063392 | 0.063392 | 0.98803 | -0.23014 | 0.98894 | -0.21249 | 17.4154
2 | -0.042126 | -0.010576 | 0.042132 | 0.010579 | 5.3703e-06 | 3.3912e-06 | 0.063392 | 0.063392 | 0.063392 | 0.98894 | -0.21249 | 0.98908 | -0.20982 | 17.4154
3 | -0.058119 | -0.014586 | 0.058147 | 0.014604 | 2.8452e-05 | 1.8082e-05 | 0.087443 | 0.087443 | 0.087443 | 0.98908 | -0.20982 | 0.98961 | -0.19956 | 24.0229
4 | -0.044079 | -0.011114 | 0.044109 | 0.011133 | 3.0357e-05 | 1.9192e-05 | 0.066353 | 0.066353 | 0.066353 | 0.98887 | -0.21393 | 0.98961 | -0.19956 | 18.2287
5 | 0.044079 | 0.011114 | -0.043904 | -0.011003 | 0.00017533 | 0.00011085 | 0.066353 | 0.066353 | 0.066353 | 0.98887 | -0.21393 | 0.98457 | -0.2974 | 18.2289
6 | -0.10226 | -0.025737 | 0.10244 | 0.025857 | 0.00018769 | 0.00011985 | 0.1538 | 0.1538 | 0.1538 | 0.98961 | -0.19956 | 0.99159 | -0.16123 | 42.2516
7 | -0.11933 | -0.030088 | 0.11944 | 0.030162 | 0.00011513 | 7.3561e-05 | 0.17913 | 0.17913 | 0.17913 | 0.99159 | -0.16123 | 0.99264 | -0.14109 | 49.2115
8 | -0.16613 | -0.042072 | 0.16613 | 0.042073 | 2.3039e-07 | 1.4537e-07 | 0.24818 | 0.24818 | 0.24818 | 0.99667 | -0.063766 | 0.99667 | -0.063737 | 17.0455
9 | 0.15872 | 0.040215 | -0.15863 | -0.040161 | 8.5884e-05 | 5.4117e-05 | 0.23712 | 0.23712 | 0.23712 | 0.99667 | -0.063766 | 0.99608 | -0.075036 | 16.2854
10 | -0.22556 | -0.056969 | 0.22557 | 0.056972 | 4.7501e-06 | 3.0168e-06 | 0.33692 | 0.33692 | 0.33692 | 0.99667 | -0.063737 | 0.99669 | -0.063297 | 23.1401
11 | 0.15357 | 0.038892 | -0.15327 | -0.038702 | 0.00029904 | 0.0001906 | 0.22956 | 0.22956 | 0.22956 | 0.99608 | -0.075036 | 0.99396 | -0.11567 | 31.5323
12 | 0.0050613 | 0.0012684 | -0.0050609 | -0.0012684 | 4.0365e-07 | 1.3271e-08 | 0.0075609 | 0.007561 | 0.007561 | 0.99608 | -0.075036 | 0.99599 | -0.07671 | 2.0772
13 | -0.23625 | -0.059648 | 0.23642 | 0.059755 | 0.000169 | 0.00010741 | 0.35286 | 0.35286 | 0.35286 | 0.99669 | -0.063297 | 0.99747 | -0.048377 | 24.2349
14 | 0.13077 | 0.033062 | -0.13061 | -0.032961 | 0.00015922 | 0.00010176 | 0.19587 | 0.19587 | 0.19587 | 0.99396 | -0.11567 | 0.99264 | -0.14109 | 53.8105
15 | 0.20035 | 0.050548 | -0.20028 | -0.050503 | 7.1768e-05 | 4.5484e-05 | 0.299 | 0.299 | 0.299 | 0.99747 | -0.048377 | 0.99708 | -0.055861 | 20.5355
16 | -0.43676 | -0.1103 | 0.43696 | 0.11043 | 0.00019806 | 0.0001265 | 0.65186 | 0.65186 | 0.65186 | 0.99747 | -0.048377 | 0.99796 | -0.038919 | 44.7704
17 | 0.20028 | 0.050503 | -0.20018 | -0.050444 | 9.2668e-05 | 5.8731e-05 | 0.299 | 0.299 | 0.299 | 0.99708 | -0.055861 | 0.99657 | -0.065533 | 20.5355
18 | -0.44913 | -0.11348 | 0.44958 | 0.11377 | 0.00044924 | 0.00028696 | 0.67 | 0.67 | 0.67 | 0.99796 | -0.038919 | 0.99905 | -0.018075 | 46.0163
19 | 0.45988 | 0.1165 | -0.45948 | -0.11625 | 0.00039891 | 0.00025483 | 0.68475 | 0.68475 | 0.68475 | 1 | 0 | 0.99905 | -0.018075 | 47.0298
20 | 0.010832 | 0.0027151 | -0.010831 | -0.0027144 | 1.3275e-06 | 6.7086e-07 | 0.016118 | 0.016118 | 0.016118 | 1 | 0 | 0.99987 | -0.0025726 | 4.4281
21 | 0.17847 | 0.045003 | -0.17829 | -0.04489 | 0.00017693 | 0.00011289 | 0.26658 | 0.26658 | 0.26658 | 0.99657 | -0.065533 | 0.9955 | -0.086268 | 36.6179
22 | -0.090941 | -0.022813 | 0.090985 | 0.022841 | 4.3684e-05 | 2.7876e-05 | 0.13627 | 0.13627 | 0.13627 | 0.9931 | -0.13254 | 0.99362 | -0.12247 | 37.4367
23 | 0.074826 | 0.018774 | -0.074802 | -0.018759 | 2.4101e-05 | 1.5359e-05 | 0.11212 | 0.11212 | 0.11212 | 0.9931 | -0.13254 | 0.99275 | -0.1393 | 30.8031
24 | -0.11489 | -0.028832 | 0.11493 | 0.028855 | 3.5584e-05 | 2.2732e-05 | 0.17207 | 0.17207 | 0.17207 | 0.99362 | -0.12247 | 0.99396 | -0.11598 | 47.2717
25 | 0.061399 | 0.0154 | -0.061384 | -0.01539 | 1.5103e-05 | 9.6042e-06 | 0.092035 | 0.092035 | 0.092035 | 0.99275 | -0.1393 | 0.99248 | -0.14446 | 25.2843
26 | -0.13342 | -0.03349 | 0.13352 | 0.033556 | 0.00010326 | 6.6e-05 | 0.19976 | 0.19976 | 0.19976 | 0.99396 | -0.11598 | 0.9948 | -0.099767 | 54.878
27 | 0.050814 | 0.012741 | -0.050801 | -0.012733 | 1.3649e-05 | 8.6542e-06 | 0.076188 | 0.076188 | 0.076188 | 0.99248 | -0.14446 | 0.99219 | -0.1501 | 20.9307
28 | -0.14239 | -0.035779 | 0.14248 | 0.035837 | 9.1811e-05 | 5.8478e-05 | 0.21302 | 0.21302 | 0.21302 | 0.9948 | -0.099767 | 0.9955 | -0.086268 | 29.2611
29 | 0.035863 | 0.0089888 | -0.035861 | -0.0089875 | 2.058e-06 | 1.2926e-06 | 0.053785 | 0.053785 | 0.053785 | 0.99219 | -0.1501 | 0.99213 | -0.15131 | 14.776
30 | 0.035812 | 0.0090529 | -0.035629 | -0.0089381 | 0.00018277 | 0.00011478 | 0.053558 | 0.053558 | 0.053558 | 0.9955 | -0.086268 | 0.98995 | -0.19328 | 14.7138
31 | 0.024217 | 0.0060714 | -0.024212 | -0.006068 | 5.5575e-06 | 3.4134e-06 | 0.036422 | 0.036422 | 0.036422 | 0.98942 | -0.20348 | 0.98918 | -0.20829 | 10.006
32 | -0.035612 | -0.0089272 | 0.035629 | 0.0089381 | 1.7312e-05 | 1.0873e-05 | 0.053558 | 0.053558 | 0.053558 | 0.98942 | -0.20348 | 0.98995 | -0.19328 | 14.7138

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47875 | 0.12082

## res_load
| p_mw | q_mvar
0 | 0.042079 | 0.010546
1 | 0.015987 | 0.0040067
2 | 0.043904 | 0.011003
3 | 0.016882 | 0.0042311
4 | 0.0074124 | 0.0018577
5 | 0.059436 | 0.014896
6 | 0.010678 | 0.0026761
7 | 0.022501 | 0.0056393
8 | 0.0050609 | 0.0012684
9 | 0.011167 | 0.0027988
10 | 0.012166 | 0.0030491
11 | 0.0063826 | 0.0015996
12 | 0.0099082 | 0.0024832
13 | 0.010831 | 0.0027144
14 | 0.021712 | 0.0054414
15 | 0.016115 | 0.0040389
16 | 0.023905 | 0.0059912
17 | 0.013402 | 0.0033589
18 | 0.018494 | 0.004635
19 | 0.01057 | 0.002649
20 | 0.0088683 | 0.0022226
21 | 0.014938 | 0.0037438
22 | 0.035861 | 0.0089875
23 | 0.011395 | 0.0028558
24 | 0.024212 | 0.006068

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1