## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-121_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-121_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-121_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-121_0_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_1061-121_0_4_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_1061-121_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1061-121_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1061-121_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1061-121_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1061-121_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1061-121_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1061-121_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1061-121_0_4_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_1061-121_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1061-121_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1061-121_0_4_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1061-121_0_4_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1061-121_0_4_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_1061-121_0_4_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_1061-121_0_4_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1061-121_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1061-121_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1061-121_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1061-121_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1061-121_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1061-121_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1061-121_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1061-121_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1061-121_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1061-121_0_4_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_1061-121_0_4_node_28 | 0.4 | n |  | TRUE
31 | bus_MV_215_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-121_0_4_load_0 | 0 | 0.010092 | 0.0025292 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-121_0_4_load_1 | 1 | 0.013369 | 0.0033506 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-121_0_4_load_2 | 2 | 0.015653 | 0.0039229 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-121_0_4_load_15 | 4 | 0.031926 | 0.0080014 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-121_0_4_load_4 | 5 | 0.015396 | 0.0038586 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-121_0_4_load_3 | 6 | 0.016442 | 0.0041209 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-121_0_4_load_26 | 9 | 0.030551 | 0.0076569 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-121_0_4_load_27 | 12 | 0.012137 | 0.0030418 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-121_0_4_load_31 | 15 | 0.011844 | 0.0029684 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-121_0_4_load_33 | 17 | 0.025469 | 0.0063832 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-121_0_4_load_32 | 18 | 0.017304 | 0.0043369 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-121_0_4_load_29 | 19 | 0.017481 | 0.0043812 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-121_0_4_load_16 | 22 | 0.022037 | 0.005523 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-121_0_4_load_17 | 23 | 0.015813 | 0.0039632 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-121_0_4_load_20 | 24 | 0.020707 | 0.0051897 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-121_0_4_load_21 | 25 | 0.021046 | 0.0052746 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-121_0_4_load_34 | 29 | 0.038959 | 0.009764 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-121_0_4_load_28 | 30 | 0.035939 | 0.0090071 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-121_0_4_line_0 |  | 0 | 1 | 0.025109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-121_0_4_line_1 |  | 1 | 2 | 0.041915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-121_0_4_line_2 |  | 2 | 3 | 0.042172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-121_0_4_line_3 |  | 3 | 4 | 0.022382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-121_0_4_line_4 |  | 3 | 5 | 0.01387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-121_0_4_line_5 |  | 5 | 6 | 0.00086695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-121_0_4_line_6 |  | 6 | 7 | 0.019652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-121_0_4_line_7 |  | 7 | 8 | 0.044377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-121_0_4_line_8 |  | 8 | 9 | 0.0087001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-121_0_4_line_9 |  | 9 | 12 | 0.0074876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-121_0_4_line_10 |  | 10 | 11 | 0.019632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1061-121_0_4_line_11 |  | 10 | 12 | 0.011308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-121_0_4_line_12 |  | 11 | 16 | 0.05363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1061-121_0_4_line_13 |  | 11 | 17 | 0.031448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-121_0_4_line_14 |  | 11 | 13 | 0.020188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-121_0_4_line_15 |  | 13 | 14 | 0.074873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-121_0_4_line_16 |  | 13 | 15 | 0.014506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-121_0_4_line_17 |  | 14 | 18 | 0.010447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-121_0_4_line_18 |  | 16 | 19 | 0.041753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1061-121_0_4_line_19 |  | 19 | 20 | 0.015363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1061-121_0_4_line_20 |  | 20 | 21 | 0.003045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1061-121_0_4_line_21 |  | 21 | 24 | 0.009626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-121_0_4_line_22 |  | 21 | 23 | 0.024937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-121_0_4_line_23 |  | 22 | 23 | 0.017668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-121_0_4_line_24 |  | 24 | 25 | 0.018003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-121_0_4_line_25 |  | 25 | 26 | 0.022639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-121_0_4_line_26 |  | 26 | 27 | 0.048872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-121_0_4_line_27 |  | 26 | 28 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-121_0_4_line_28 |  | 27 | 29 | 0.009209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-121_0_4_line_29 |  | 28 | 30 | 0.0038225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-121_0_4_trafo_30 | 0.63 MVA 20/0.4 kV | 31 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2667616.7128 | 1209443.5743 | 2667592.51 | 1209436.8897
1 | 2667592.51 | 1209436.8897 | 2667586.7681 | 1209435.3039 | 2667558.467 | 1209431.3255 | 2667551.7511 | 1209434.3814
2 | 2667515.1886 | 1209454.4167 | 2667520.9655 | 1209448.3895 | 2667551.7511 | 1209434.3814
3 | 2667515.1886 | 1209454.4167 | 2667506.0394 | 1209433.9896
4 | 2667515.1886 | 1209454.4167 | 2667522.91 | 1209465.9389
5 | 2667523.3926 | 1209466.6591 | 2667522.91 | 1209465.9389
6 | 2667534.3326 | 1209482.9842 | 2667523.3926 | 1209466.6591
7 | 2667497.4212 | 1209507.7264 | 2667514.7039 | 1209495.2253 | 2667534.3326 | 1209482.9842
8 | 2667497.4212 | 1209507.7264 | 2667490.3733 | 1209512.8273
9 | 2667484.3077 | 1209517.2173 | 2667490.3733 | 1209512.8273
10 | 2667475.4561 | 1209524.2549 | 2667460.0692 | 1209536.4997
11 | 2667475.4561 | 1209524.2549 | 2667484.3077 | 1209517.2173
12 | 2667448.7488 | 1209492.9671 | 2667455.3964 | 1209500.6803 | 2667454.4089 | 1209515.4116 | 2667461.1756 | 1209524.0267 | 2667454.4609 | 1209528.965 | 2667460.0692 | 1209536.4997
13 | 2667460.0692 | 1209536.4997 | 2667458.2513 | 1209537.9467 | 2667436.7503 | 1209557.5917
14 | 2667460.0692 | 1209536.4997 | 2667462.4353 | 1209539.6728 | 2667458.4125 | 1209543.185 | 2667462.1511 | 1209547.3298 | 2667465.2263 | 1209551.6562
15 | 2667465.2263 | 1209551.6562 | 2667476.437 | 1209550.4377 | 2667484.8235 | 1209551.5888 | 2667491.4556 | 1209555.9664 | 2667508.4714 | 1209572.4134 | 2667512.3173 | 1209577.8158 | 2667515.0859 | 1209585.7298 | 2667515.5966 | 1209594.3297
16 | 2667465.2263 | 1209551.6562 | 2667465.7502 | 1209552.3848 | 2667466.1129 | 1209559.2931 | 2667463.6426 | 1209565.5113
17 | 2667515.5966 | 1209594.3297 | 2667508.769 | 1209602.2373
18 | 2667448.7488 | 1209492.9671 | 2667430.1327 | 1209508.4441 | 2667425.4015 | 1209513.4271 | 2667422.2334 | 1209517.983 | 2667420.0031 | 1209522.5952
19 | 2667411.2463 | 1209532.3789 | 2667414.2057 | 1209532.8348 | 2667415.0859 | 1209532.967 | 2667419.6026 | 1209523.4233 | 2667420.0031 | 1209522.5952
20 | 2667411.2463 | 1209532.3789 | 2667408.9394 | 1209532.0304 | 2667408.2261 | 1209531.9223
21 | 2667408.2261 | 1209531.9223 | 2667409.2938 | 1209528.2432 | 2667409.9232 | 1209522.4823
22 | 2667408.2261 | 1209531.9223 | 2667407.5696 | 1209534.1829 | 2667402.0073 | 1209547.4727 | 2667398.6584 | 1209554.931
23 | 2667398.6584 | 1209554.931 | 2667392.3617 | 1209568.9548 | 2667391.7646 | 1209571.1708
24 | 2667409.9232 | 1209522.4823 | 2667410.0569 | 1209521.2586 | 2667409.4809 | 1209506.3096 | 2667409.4929 | 1209504.498
25 | 2667414.3756 | 1209486.1858 | 2667412.0257 | 1209485.6033 | 2667411.0858 | 1209485.3703 | 2667409.5567 | 1209494.8923 | 2667409.4929 | 1209504.498
26 | 2667404.6047 | 1209448.1076 | 2667407.9179 | 1209448.2006 | 2667410.2777 | 1209448.5719 | 2667415.6339 | 1209450.8449 | 2667419.3732 | 1209455.6123 | 2667420.2626 | 1209460.9923 | 2667414.3756 | 1209486.1858
27 | 2667428.054 | 1209483.194 | 2667426.267 | 1209481.2393 | 2667419.5493 | 1209485.7662 | 2667417.9298 | 1209486.4705 | 2667417.7942 | 1209487.036 | 2667416.915 | 1209486.8148 | 2667414.3756 | 1209486.1858
28 | 2667395.7424 | 1209450.698 | 2667404.6047 | 1209448.1076
29 | 2667428.054 | 1209483.194 | 2667429.469 | 1209481.7535 | 2667429.9826 | 1209480.0249

## bus_geodata
| x | y | coords
0 | 2667616.7128 | 1209443.5743
1 | 2667592.51 | 1209436.8897
2 | 2667551.7511 | 1209434.3814
3 | 2667515.1886 | 1209454.4167
4 | 2667506.0394 | 1209433.9896
5 | 2667522.91 | 1209465.9389
6 | 2667523.3926 | 1209466.6591
7 | 2667534.3326 | 1209482.9842
8 | 2667497.4212 | 1209507.7264
9 | 2667490.3733 | 1209512.8273
10 | 2667475.4561 | 1209524.2549
11 | 2667460.0692 | 1209536.4997
12 | 2667484.3077 | 1209517.2173
13 | 2667465.2263 | 1209551.6562
14 | 2667515.5966 | 1209594.3297
15 | 2667463.6426 | 1209565.5113
16 | 2667448.7488 | 1209492.9671
17 | 2667436.7503 | 1209557.5917
18 | 2667508.769 | 1209602.2373
19 | 2667420.0031 | 1209522.5952
20 | 2667411.2463 | 1209532.3789
21 | 2667408.2261 | 1209531.9223
22 | 2667391.7646 | 1209571.1708
23 | 2667398.6584 | 1209554.931
24 | 2667409.9232 | 1209522.4823
25 | 2667409.4929 | 1209504.498
26 | 2667414.3756 | 1209486.1858
27 | 2667404.6047 | 1209448.1076
28 | 2667428.054 | 1209483.194
29 | 2667395.7424 | 1209450.698
30 | 2667429.9826 | 1209480.0249
31 | 2667458.7246 | 1209484.6636

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98153 | -0.356 | 0.010092 | 0.0025292
1 | 0.98177 | -0.35142 | 0.013369 | 0.0033506
2 | 0.98268 | -0.33365 | 0.015653 | 0.0039229
3 | 0.9842 | -0.30393 | 0 | 0
4 | 0.98354 | -0.31679 | 0.031926 | 0.0080014
5 | 0.98511 | -0.28621 | 0.015396 | 0.0038586
6 | 0.98518 | -0.28487 | 0.016442 | 0.0041209
7 | 0.98704 | -0.24863 | 0 | 0
8 | 0.99125 | -0.1673 | 0 | 0
9 | 0.99208 | -0.15143 | 0.030551 | 0.0076569
10 | 0.99376 | -0.11922 | 0 | 0
11 | 0.99507 | -0.09403 | 0 | 0
12 | 0.993 | -0.13375 | 0.012137 | 0.0030418
13 | 0.99453 | -0.10439 | 0 | 0
14 | 0.99335 | -0.12726 | 0 | 0
15 | 0.99438 | -0.10742 | 0.011844 | 0.0029684
16 | 1 | 0 | -0.3772 | -0.095429
17 | 0.99434 | -0.10814 | 0.025469 | 0.0063832
18 | 0.99319 | -0.13045 | 0.017304 | 0.0043369
19 | 0.99672 | -0.062787 | 0.017481 | 0.0043812
20 | 0.99563 | -0.083632 | 0 | 0
21 | 0.99542 | -0.087769 | 0 | 0
22 | 0.9942 | -0.11125 | 0.022037 | 0.005523
23 | 0.99456 | -0.10439 | 0.015813 | 0.0039632
24 | 0.99439 | -0.10754 | 0.020707 | 0.0051897
25 | 0.99281 | -0.13804 | 0.021046 | 0.0052746
26 | 0.99126 | -0.16807 | 0 | 0
27 | 0.98951 | -0.2019 | 0 | 0
28 | 0.99071 | -0.17867 | 0 | 0
29 | 0.98918 | -0.20829 | 0.038959 | 0.009764
30 | 0.99058 | -0.18111 | 0.035939 | 0.0090071
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010092 | -0.0025292 | 0.010094 | 0.0025303 | 2.2038e-06 | 1.093e-06 | 0.015299 | 0.015299 | 0.015299 | 0.98153 | -0.356 | 0.98177 | -0.35142 | 4.203
1 | -0.023463 | -0.0058808 | 0.023483 | 0.005893 | 1.9877e-05 | 1.2191e-05 | 0.035561 | 0.035561 | 0.035561 | 0.98177 | -0.35142 | 0.98268 | -0.33365 | 9.7696
2 | -0.039135 | -0.0098159 | 0.039191 | 0.0098509 | 5.5541e-05 | 3.5011e-05 | 0.059263 | 0.059263 | 0.059263 | 0.98268 | -0.33365 | 0.9842 | -0.30393 | 16.281
3 | 0.031945 | 0.0080136 | -0.031926 | -0.0080014 | 1.9582e-05 | 1.2248e-05 | 0.048301 | 0.048301 | 0.048301 | 0.9842 | -0.30393 | 0.98354 | -0.31679 | 13.2696
4 | -0.071136 | -0.017865 | 0.071196 | 0.017903 | 6.0179e-05 | 3.8338e-05 | 0.10756 | 0.10756 | 0.10756 | 0.9842 | -0.30393 | 0.98511 | -0.28621 | 29.5505
5 | -0.086592 | -0.021761 | 0.086598 | 0.021765 | 5.5638e-06 | 3.5498e-06 | 0.13082 | 0.13082 | 0.13082 | 0.98511 | -0.28621 | 0.98518 | -0.28487 | 35.9394
6 | -0.10304 | -0.025886 | 0.10322 | 0.026 | 0.00017855 | 0.00011402 | 0.15565 | 0.15565 | 0.15565 | 0.98518 | -0.28487 | 0.98704 | -0.24863 | 42.7621
7 | -0.10322 | -0.026 | 0.10362 | 0.026257 | 0.00040319 | 0.00025747 | 0.15565 | 0.15565 | 0.15565 | 0.98704 | -0.24863 | 0.99125 | -0.1673 | 42.7621
8 | -0.10362 | -0.026257 | 0.1037 | 0.026308 | 7.9045e-05 | 5.0477e-05 | 0.15565 | 0.15565 | 0.15565 | 0.99125 | -0.1673 | 0.99208 | -0.15143 | 42.7621
9 | -0.13425 | -0.033965 | 0.13437 | 0.034038 | 0.00011398 | 7.285e-05 | 0.20148 | 0.20148 | 0.20148 | 0.99208 | -0.15143 | 0.993 | -0.13375 | 55.3509
10 | -0.14661 | -0.037145 | 0.14678 | 0.037258 | 0.00017762 | 0.00011317 | 0.21966 | 0.21966 | 0.21966 | 0.99376 | -0.11922 | 0.99507 | -0.09403 | 30.1737
11 | 0.14661 | 0.037145 | -0.1465 | -0.037079 | 0.00010231 | 6.5186e-05 | 0.21966 | 0.21966 | 0.21966 | 0.99376 | -0.11922 | 0.993 | -0.13375 | 30.1738
12 | -0.20146 | -0.050979 | 0.20237 | 0.051563 | 0.00091363 | 0.00058332 | 0.30143 | 0.30143 | 0.30143 | 0.99507 | -0.09403 | 1 | 0 | 41.4049
13 | 0.025486 | 0.0063937 | -0.025469 | -0.0063832 | 1.7131e-05 | 1.0556e-05 | 0.038114 | 0.038114 | 0.038114 | 0.99507 | -0.09403 | 0.99434 | -0.10814 | 10.471
14 | 0.029186 | 0.0073278 | -0.029171 | -0.0073188 | 1.4424e-05 | 8.9691e-06 | 0.043649 | 0.043649 | 0.043649 | 0.99507 | -0.09403 | 0.99453 | -0.10439 | 11.9915
15 | 0.017326 | 0.0043495 | -0.017307 | -0.0043384 | 1.8872e-05 | 1.1108e-05 | 0.025925 | 0.025926 | 0.025926 | 0.99453 | -0.10439 | 0.99335 | -0.12726 | 7.1225
16 | 0.011846 | 0.0029693 | -0.011844 | -0.0029684 | 1.7088e-06 | 9.0541e-07 | 0.017723 | 0.017724 | 0.017724 | 0.99453 | -0.10439 | 0.99438 | -0.10742 | 4.8691
17 | 0.017307 | 0.0043384 | -0.017304 | -0.0043369 | 2.6333e-06 | 1.5501e-06 | 0.025926 | 0.025926 | 0.025926 | 0.99335 | -0.12726 | 0.99319 | -0.13045 | 7.1225
18 | 0.17318 | 0.043866 | -0.17266 | -0.043534 | 0.00052054 | 0.00033205 | 0.25786 | 0.25786 | 0.25786 | 1 | 0 | 0.99672 | -0.062787 | 35.4203
19 | 0.15518 | 0.039153 | -0.15502 | -0.039054 | 0.00015472 | 9.8623e-05 | 0.23176 | 0.23176 | 0.23176 | 0.99672 | -0.062787 | 0.99563 | -0.083632 | 31.8354
20 | 0.15502 | 0.039054 | -0.15499 | -0.039035 | 3.0667e-05 | 1.9548e-05 | 0.23176 | 0.23176 | 0.23176 | 0.99563 | -0.083632 | 0.99542 | -0.087769 | 31.8354
21 | 0.11711 | 0.029525 | -0.117 | -0.029455 | 0.0001107 | 7.0723e-05 | 0.17512 | 0.17512 | 0.17512 | 0.99542 | -0.087769 | 0.99439 | -0.10754 | 48.1099
22 | 0.037888 | 0.0095095 | -0.037858 | -0.0094906 | 3.0001e-05 | 1.8877e-05 | 0.056642 | 0.056642 | 0.056642 | 0.99542 | -0.087769 | 0.99456 | -0.10439 | 15.561
23 | -0.022037 | -0.005523 | 0.022044 | 0.0055274 | 7.2074e-06 | 4.3836e-06 | 0.032983 | 0.032983 | 0.032983 | 0.9942 | -0.11125 | 0.99456 | -0.10439 | 9.0612
24 | 0.096288 | 0.024265 | -0.096148 | -0.024175 | 0.00014025 | 8.9527e-05 | 0.14413 | 0.14413 | 0.14413 | 0.99439 | -0.10754 | 0.99281 | -0.13804 | 39.5972
25 | 0.075102 | 0.018901 | -0.074995 | -0.018832 | 0.00010762 | 6.8585e-05 | 0.11259 | 0.11259 | 0.11259 | 0.99281 | -0.13804 | 0.99126 | -0.16807 | 30.9315
26 | 0.039034 | 0.0098111 | -0.038971 | -0.0097714 | 6.2945e-05 | 3.9656e-05 | 0.058605 | 0.058605 | 0.058605 | 0.99126 | -0.16807 | 0.98951 | -0.2019 | 16.1003
27 | 0.035961 | 0.0090211 | -0.035943 | -0.0090097 | 1.8164e-05 | 1.1411e-05 | 0.053986 | 0.053986 | 0.053986 | 0.99126 | -0.16807 | 0.99071 | -0.17867 | 14.8312
28 | 0.038971 | 0.0097714 | -0.038959 | -0.009764 | 1.1861e-05 | 7.4727e-06 | 0.058605 | 0.058605 | 0.058605 | 0.98951 | -0.2019 | 0.98918 | -0.20829 | 16.1003
29 | 0.035943 | 0.0090097 | -0.035939 | -0.0090071 | 4.1776e-06 | 2.6245e-06 | 0.053986 | 0.053986 | 0.053986 | 0.99071 | -0.17867 | 0.99058 | -0.18111 | 14.8312

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3772 | 0.095429

## res_load
| p_mw | q_mvar
0 | 0.010092 | 0.0025292
1 | 0.013369 | 0.0033506
2 | 0.015653 | 0.0039229
3 | 0.031926 | 0.0080014
4 | 0.015396 | 0.0038586
5 | 0.016442 | 0.0041209
6 | 0.030551 | 0.0076569
7 | 0.012137 | 0.0030418
8 | 0.011844 | 0.0029684
9 | 0.025469 | 0.0063832
10 | 0.017304 | 0.0043369
11 | 0.017481 | 0.0043812
12 | 0.022037 | 0.005523
13 | 0.015813 | 0.0039632
14 | 0.020707 | 0.0051897
15 | 0.021046 | 0.0052746
16 | 0.038959 | 0.009764
17 | 0.035939 | 0.0090071

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1