## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-127_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-127_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-127_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-127_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-127_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-127_0_6_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_1061-127_0_6_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1061-127_0_6_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1061-127_0_6_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1061-127_0_6_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_1061-127_0_6_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1061-127_0_6_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1061-127_0_6_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1061-127_0_6_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1061-127_0_6_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1061-127_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1061-127_0_6_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_1061-127_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1061-127_0_6_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1061-127_0_6_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1061-127_0_6_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1061-127_0_6_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1061-127_0_6_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_1061-127_0_6_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1061-127_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1061-127_0_6_node_5 | 0.4 | n |  | TRUE
26 | bus_LV_1061-127_0_6_node_6 | 0.4 | n |  | TRUE
27 | bus_LV_1061-127_0_6_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1061-127_0_6_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1061-127_0_6_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1061-127_0_6_node_28 | 0.4 | n |  | TRUE
31 | bus_MV_216_0_node_96 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-127_0_6_load_0 | 0 | 0.050254 | 0.012595 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-127_0_6_load_1 | 1 | 0.0083206 | 0.0020853 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-127_0_6_load_2 | 2 | 0.047652 | 0.011943 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-127_0_6_load_4 | 4 | 0.073912 | 0.018524 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-127_0_6_load_21 | 5 | 0.0076527 | 0.0019179 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-127_0_6_load_23 | 6 | 0.032354 | 0.0081088 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-127_0_6_load_8 | 7 | 0.0059198 | 0.0014836 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-127_0_6_load_24 | 9 | 0.0028348 | 0.00071048 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-127_0_6_load_22 | 10 | 0.034302 | 0.0085968 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-127_0_6_load_31 | 12 | 0.040149 | 0.010062 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-127_0_6_load_29 | 16 | 0.035101 | 0.0087971 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-127_0_6_load_19 | 18 | 0.0019306 | 0.00048384 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-127_0_6_load_25 | 20 | 0.060996 | 0.015287 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-127_0_6_load_32 | 22 | 0.059668 | 0.014954 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-127_0_6_load_20 | 23 | 0.003051 | 0.00076466 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-127_0_6_load_18 | 24 | 0.010482 | 0.0026271 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-127_0_6_load_5 | 25 | 0.018596 | 0.0046606 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-127_0_6_load_6 | 26 | 0.0073641 | 0.0018456 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-127_0_6_load_30 | 28 | 0.009491 | 0.0023787 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-127_0_6_load_27 | 29 | 0.0050958 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-127_0_6_load_28 | 30 | 0.0084729 | 0.0021235 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-127_0_6_line_0 |  | 0 | 1 | 0.021094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-127_0_6_line_1 |  | 0 | 2 | 0.00040718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-127_0_6_line_2 |  | 1 | 3 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-127_0_6_line_3 |  | 2 | 4 | 0.0015824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1061-127_0_6_line_4 |  | 3 | 5 | 0.029952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-127_0_6_line_5 |  | 4 | 6 | 0.03487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1061-127_0_6_line_6 |  | 5 | 7 | 0.021176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-127_0_6_line_7 |  | 6 | 10 | 0.002036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1061-127_0_6_line_8 |  | 7 | 26 | 0.0013074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-127_0_6_line_9 |  | 8 | 9 | 0.026464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1061-127_0_6_line_10 |  | 8 | 10 | 0.020795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1061-127_0_6_line_11 |  | 9 | 17 | 0.0094278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1061-127_0_6_line_12 |  | 11 | 12 | 0.026326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-127_0_6_line_13 |  | 11 | 13 | 0.092599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-127_0_6_line_14 |  | 13 | 22 | 0.017964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-127_0_6_line_15 |  | 13 | 21 | 0.062924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-127_0_6_line_16 |  | 14 | 15 | 0.11743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1061-127_0_6_line_17 |  | 14 | 16 | 0.044629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1061-127_0_6_line_18 |  | 15 | 23 | 0.017972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-127_0_6_line_19 |  | 15 | 24 | 0.037768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1061-127_0_6_line_20 |  | 16 | 21 | 0.098368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1061-127_0_6_line_21 |  | 17 | 18 | 0.0024209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1061-127_0_6_line_22 |  | 18 | 24 | 0.018109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1061-127_0_6_line_23 |  | 19 | 20 | 0.030401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-127_0_6_line_24 |  | 19 | 21 | 0.1302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-127_0_6_line_25 |  | 20 | 27 | 0.034664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-127_0_6_line_26 |  | 23 | 28 | 0.0099168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-127_0_6_line_27 |  | 25 | 26 | 0.025553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-127_0_6_line_28 |  | 27 | 29 | 0.038103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-127_0_6_line_29 |  | 29 | 30 | 0.019261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-127_0_6_trafo_11 | 0.63 MVA 20/0.4 kV | 31 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2665592.6543 | 1210033.9922 | 2665613.4679 | 1210037.422
1 | 2665592.2526 | 1210033.9259 | 2665592.6543 | 1210033.9922
2 | 2665625.6214 | 1210039.4248 | 2665613.4679 | 1210037.422
3 | 2665590.6913 | 1210033.6687 | 2665592.2526 | 1210033.9259
4 | 2665625.6214 | 1210039.4248 | 2665627.3414 | 1210029.5487 | 2665630.5585 | 1210009.8825
5 | 2665590.6913 | 1210033.6687 | 2665571.0408 | 1210030.4305 | 2665556.2856 | 1210027.9979
6 | 2665630.5585 | 1210009.8825 | 2665632.3448 | 1209998.9627 | 2665633.9262 | 1209988.9756
7 | 2665556.2856 | 1210027.9979 | 2665554.2767 | 1210027.6667
8 | 2665633.9262 | 1209988.9756 | 2665634.1306 | 1209987.6843
9 | 2665533.7584 | 1210024.2839 | 2665534.0564 | 1210000.6171 | 2665534.1705 | 1209997.824
10 | 2665533.7584 | 1210024.2839 | 2665554.2767 | 1210027.6667
11 | 2665534.5554 | 1209988.404 | 2665534.1705 | 1209997.824
12 | 2665335.1514 | 1209685.6104 | 2665331.5669 | 1209711.6871
13 | 2665331.5669 | 1209711.6871 | 2665349.4996 | 1209714.3183 | 2665378.1934 | 1209718.5129 | 2665395.5645 | 1209721.0603 | 2665423.1881 | 1209725.1099
14 | 2665425.7091 | 1209707.3267 | 2665423.1881 | 1209725.1099
15 | 2665423.1881 | 1209725.1099 | 2665449.1725 | 1209728.9193 | 2665469.0175 | 1209731.8276 | 2665485.4475 | 1209734.2315
16 | 2665493.3013 | 1209875.9823 | 2665495.288 | 1209884.0313 | 2665502.4875 | 1209905.3567 | 2665507.8025 | 1209921.1024 | 2665516.6507 | 1209939.711 | 2665524.4779 | 1209950.9371 | 2665532.0451 | 1209952.6101 | 2665535.9388 | 1209929.5943 | 2665540.4899 | 1209930.4448
17 | 2665493.3013 | 1209875.9823 | 2665487.6331 | 1209852.9505 | 2665484.927 | 1209832.2163
18 | 2665540.4899 | 1209930.4448 | 2665544.5526 | 1209930.7896 | 2665552.0473 | 1209930.0715 | 2665554.5628 | 1209928.7205 | 2665556.3971 | 1209925.7277 | 2665556.3971 | 1209925.7277
19 | 2665540.4899 | 1209930.4448 | 2665539.3124 | 1209938.0031 | 2665537.3595 | 1209953.1688 | 2665535.9348 | 1209967.9281
20 | 2665485.4475 | 1209734.2315 | 2665481.5712 | 1209764.6743 | 2665482.3327 | 1209790.165 | 2665483.1879 | 1209818.8919 | 2665484.927 | 1209832.2163
21 | 2665534.5554 | 1209988.404 | 2665534.654 | 1209985.9851
22 | 2665535.9348 | 1209967.9281 | 2665534.9923 | 1209977.6911 | 2665534.654 | 1209985.9851
23 | 2665491.1353 | 1209605.2483 | 2665489.4761 | 1209574.893
24 | 2665485.4475 | 1209734.2315 | 2665485.6683 | 1209732.8109 | 2665489.853 | 1209705.4289 | 2665497.158 | 1209650.7089 | 2665491.1353 | 1209605.2483
25 | 2665487.5841 | 1209540.2807 | 2665489.4761 | 1209574.893
26 | 2665556.3971 | 1209925.7277 | 2665557.7641 | 1209917.5377 | 2665558.2535 | 1209916.0002
27 | 2665638.2199 | 1209962.4606 | 2665635.4325 | 1209979.4625 | 2665634.1306 | 1209987.6843
28 | 2665487.5841 | 1209540.2807 | 2665449.5614 | 1209542.7588
29 | 2665449.5614 | 1209542.7588 | 2665430.3416 | 1209544.0114

## bus_geodata
| x | y | coords
0 | 2665592.6543 | 1210033.9922
1 | 2665613.4679 | 1210037.422
2 | 2665592.2526 | 1210033.9259
3 | 2665625.6214 | 1210039.4247
4 | 2665590.6913 | 1210033.6687
5 | 2665630.5585 | 1210009.8825
6 | 2665556.2856 | 1210027.9979
7 | 2665633.9262 | 1209988.9756
8 | 2665533.7584 | 1210024.2839
9 | 2665534.1705 | 1209997.824
10 | 2665554.2767 | 1210027.6667
11 | 2665331.5669 | 1209711.6871
12 | 2665335.1514 | 1209685.6104
13 | 2665423.1881 | 1209725.1099
14 | 2665493.3013 | 1209875.9823
15 | 2665540.4899 | 1209930.4448
16 | 2665484.9269 | 1209832.2163
17 | 2665534.5554 | 1209988.404
18 | 2665534.654 | 1209985.9851
19 | 2665491.1353 | 1209605.2483
20 | 2665489.4761 | 1209574.893
21 | 2665485.4475 | 1209734.2315
22 | 2665425.7091 | 1209707.3267
23 | 2665556.3971 | 1209925.7277
24 | 2665535.9348 | 1209967.9281
25 | 2665638.2199 | 1209962.4606
26 | 2665634.1306 | 1209987.6843
27 | 2665487.5841 | 1209540.2807
28 | 2665558.2535 | 1209916.0002
29 | 2665449.5614 | 1209542.7588
30 | 2665430.3416 | 1209544.0114
31 | 2665502.4875 | 1209905.3567

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97546 | -0.47141 | 0.050254 | 0.012595
1 | 0.97452 | -0.48992 | 0.0083206 | 0.0020853
2 | 0.9755 | -0.47068 | 0.047652 | 0.011943
3 | 0.97407 | -0.49886 | 0 | 0
4 | 0.97561 | -0.46857 | 0.073912 | 0.018524
5 | 0.97297 | -0.52064 | 0.0076527 | 0.0019179
6 | 0.97798 | -0.42192 | 0.032354 | 0.0081088
7 | 0.97234 | -0.53308 | 0.0059198 | 0.0014836
8 | 0.97999 | -0.38272 | 0 | 0
9 | 0.98234 | -0.33699 | 0.0028348 | 0.00071048
10 | 0.97814 | -0.41881 | 0.034302 | 0.0085968
11 | 0.97992 | -0.38585 | 0 | 0
12 | 0.97894 | -0.40506 | 0.040149 | 0.010062
13 | 0.98336 | -0.3186 | 0 | 0
14 | 1 | 0 | -0.53555 | -0.1378
15 | 0.98856 | -0.2168 | 0 | 0
16 | 0.99712 | -0.054479 | 0.035101 | 0.0087971
17 | 0.98318 | -0.32059 | 0 | 0
18 | 0.9834 | -0.31638 | 0.0019306 | 0.00048384
19 | 0.98016 | -0.3806 | 0 | 0
20 | 0.97806 | -0.42181 | 0.060996 | 0.015287
21 | 0.98917 | -0.20606 | 0 | 0
22 | 0.98237 | -0.33794 | 0.059668 | 0.014954
23 | 0.98836 | -0.22082 | 0.003051 | 0.00076466
24 | 0.98503 | -0.28476 | 0.010482 | 0.0026271
25 | 0.97186 | -0.54247 | 0.018596 | 0.0046606
26 | 0.9723 | -0.5337 | 0.0073641 | 0.0018456
27 | 0.97763 | -0.43039 | 0 | 0
28 | 0.98827 | -0.2225 | 0.009491 | 0.0023787
29 | 0.97715 | -0.43982 | 0.0050958 | 0.0012771
30 | 0.97699 | -0.4428 | 0.0084729 | 0.0021235
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.047981 | 0.012074 | -0.047939 | -0.012047 | 4.2397e-05 | 2.6871e-05 | 0.07321 | 0.07321 | 0.07321 | 0.97546 | -0.47141 | 0.97452 | -0.48992 | 20.1126
1 | -0.098235 | -0.024668 | 0.098238 | 0.024671 | 3.4296e-06 | 2.1898e-06 | 0.14987 | 0.14987 | 0.14987 | 0.97546 | -0.47141 | 0.9755 | -0.47068 | 41.1728
2 | 0.039618 | 0.0099614 | -0.039601 | -0.0099507 | 1.691e-05 | 1.0669e-05 | 0.060505 | 0.060505 | 0.060505 | 0.97452 | -0.48992 | 0.97407 | -0.49886 | 16.6223
3 | -0.14589 | -0.036613 | 0.1459 | 0.036623 | 1.4695e-05 | 9.3656e-06 | 0.22256 | 0.22256 | 0.22256 | 0.9755 | -0.47068 | 0.97561 | -0.46857 | 30.5709
4 | 0.039601 | 0.0099507 | -0.03956 | -0.0099248 | 4.1119e-05 | 2.5944e-05 | 0.060505 | 0.060505 | 0.060505 | 0.97407 | -0.49886 | 0.97297 | -0.52064 | 16.6223
5 | -0.21982 | -0.055147 | 0.22031 | 0.055459 | 0.00049 | 0.00031229 | 0.33529 | 0.33529 | 0.33529 | 0.97561 | -0.46857 | 0.97798 | -0.42192 | 30.704
6 | 0.031907 | 0.0080068 | -0.031888 | -0.007995 | 1.8913e-05 | 1.1841e-05 | 0.048801 | 0.048802 | 0.048802 | 0.97297 | -0.52064 | 0.97234 | -0.53308 | 13.407
7 | -0.25266 | -0.063568 | 0.2527 | 0.063592 | 3.7629e-05 | 2.4006e-05 | 0.38451 | 0.38451 | 0.38451 | 0.97798 | -0.42192 | 0.97814 | -0.41881 | 35.212
8 | 0.025969 | 0.0065113 | -0.025968 | -0.0065108 | 7.7436e-07 | 4.7937e-07 | 0.039742 | 0.039742 | 0.039742 | 0.97234 | -0.53308 | 0.9723 | -0.5337 | 10.9182
9 | -0.2875 | -0.072505 | 0.28813 | 0.072908 | 0.00063085 | 0.00040274 | 0.4367 | 0.4367 | 0.4367 | 0.97999 | -0.38272 | 0.98234 | -0.33699 | 39.9905
10 | 0.2875 | 0.072505 | -0.287 | -0.072188 | 0.00049572 | 0.00031647 | 0.4367 | 0.4367 | 0.4367 | 0.97999 | -0.38272 | 0.97814 | -0.41881 | 39.9905
11 | -0.29096 | -0.073618 | 0.29119 | 0.073764 | 0.00022918 | 0.00014632 | 0.44099 | 0.44099 | 0.44099 | 0.98234 | -0.33699 | 0.98318 | -0.32059 | 40.3837
12 | 0.040186 | 0.010085 | -0.040149 | -0.010062 | 3.6768e-05 | 2.32e-05 | 0.061028 | 0.061028 | 0.061028 | 0.97992 | -0.38585 | 0.97894 | -0.40506 | 16.7658
13 | -0.040186 | -0.010085 | 0.040315 | 0.010167 | 0.00012933 | 8.1598e-05 | 0.061028 | 0.061027 | 0.061028 | 0.97992 | -0.38585 | 0.98336 | -0.3186 | 16.7658
14 | 0.059723 | 0.014989 | -0.059668 | -0.014954 | 5.5027e-05 | 3.499e-05 | 0.09038 | 0.09038 | 0.09038 | 0.98336 | -0.3186 | 0.98237 | -0.33794 | 24.8297
15 | -0.10004 | -0.025156 | 0.10058 | 0.025502 | 0.00054093 | 0.00034539 | 0.15141 | 0.15141 | 0.15141 | 0.98336 | -0.3186 | 0.98917 | -0.20606 | 41.5953
16 | 0.32101 | 0.083128 | -0.31765 | -0.08098 | 0.0033627 | 0.0021475 | 0.47863 | 0.47863 | 0.47863 | 1 | 0 | 0.98856 | -0.2168 | 43.8305
17 | 0.21289 | 0.054671 | -0.21233 | -0.054313 | 0.00056147 | 0.00035759 | 0.31725 | 0.31725 | 0.31725 | 1 | 0 | 0.99712 | -0.054479 | 29.0521
18 | 0.012545 | 0.003145 | -0.012543 | -0.0031437 | 2.4033e-06 | 1.3077e-06 | 0.018884 | 0.018884 | 0.018884 | 0.98856 | -0.2168 | 0.98836 | -0.22082 | 5.1878
19 | 0.30511 | 0.077835 | -0.30411 | -0.077198 | 0.00099787 | 0.00063719 | 0.45975 | 0.45975 | 0.45975 | 0.98856 | -0.2168 | 0.98503 | -0.28476 | 42.1013
20 | 0.17723 | 0.045516 | -0.17593 | -0.044691 | 0.0012939 | 0.00082558 | 0.26487 | 0.26487 | 0.26487 | 0.99712 | -0.054479 | 0.98917 | -0.20606 | 36.3831
21 | -0.29119 | -0.073764 | 0.29125 | 0.073802 | 5.8851e-05 | 3.7572e-05 | 0.44099 | 0.44099 | 0.44099 | 0.98318 | -0.32059 | 0.9834 | -0.31638 | 40.3837
22 | -0.29318 | -0.074286 | 0.29363 | 0.074571 | 0.00044607 | 0.00028479 | 0.44391 | 0.44391 | 0.44391 | 0.9834 | -0.31638 | 0.98503 | -0.28476 | 40.6512
23 | 0.074724 | 0.018788 | -0.074578 | -0.018695 | 0.00014677 | 9.3547e-05 | 0.11346 | 0.11346 | 0.11346 | 0.98016 | -0.3806 | 0.97806 | -0.42181 | 31.1712
24 | -0.074724 | -0.018788 | 0.075353 | 0.019189 | 0.00062857 | 0.00040063 | 0.11346 | 0.11346 | 0.11346 | 0.98016 | -0.3806 | 0.98917 | -0.20606 | 31.1712
25 | 0.013582 | 0.0034077 | -0.013576 | -0.0034046 | 5.5508e-06 | 3.1177e-06 | 0.020664 | 0.020664 | 0.020664 | 0.97806 | -0.42181 | 0.97763 | -0.43039 | 5.677
26 | 0.0094917 | 0.002379 | -0.009491 | -0.0023787 | 7.5943e-07 | 3.5896e-07 | 0.01429 | 0.01429 | 0.01429 | 0.98836 | -0.22082 | 0.98827 | -0.2225 | 3.9259
27 | -0.018596 | -0.0046606 | 0.018604 | 0.0046652 | 7.7681e-06 | 4.6548e-06 | 0.028472 | 0.028472 | 0.028472 | 0.97186 | -0.54247 | 0.9723 | -0.5337 | 7.822
28 | 0.013576 | 0.0034046 | -0.01357 | -0.0034012 | 6.1016e-06 | 3.4275e-06 | 0.020664 | 0.020665 | 0.020665 | 0.97763 | -0.43039 | 0.97715 | -0.43982 | 5.6771
29 | 0.0084741 | 0.002124 | -0.0084729 | -0.0021235 | 1.2028e-06 | 5.2857e-07 | 0.012905 | 0.012905 | 0.012905 | 0.97715 | -0.43982 | 0.97699 | -0.4428 | 3.5453

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53555 | 0.1378

## res_load
| p_mw | q_mvar
0 | 0.050254 | 0.012595
1 | 0.0083206 | 0.0020853
2 | 0.047652 | 0.011943
3 | 0.073912 | 0.018524
4 | 0.0076527 | 0.0019179
5 | 0.032354 | 0.0081088
6 | 0.0059198 | 0.0014836
7 | 0.0028348 | 0.00071048
8 | 0.034302 | 0.0085968
9 | 0.040149 | 0.010062
10 | 0.035101 | 0.0087971
11 | 0.0019306 | 0.00048384
12 | 0.060996 | 0.015287
13 | 0.059668 | 0.014954
14 | 0.003051 | 0.00076466
15 | 0.010482 | 0.0026271
16 | 0.018596 | 0.0046606
17 | 0.0073641 | 0.0018456
18 | 0.009491 | 0.0023787
19 | 0.0050958 | 0.0012771
20 | 0.0084729 | 0.0021235

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1