## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-129_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-129_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-129_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-129_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1061-129_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1061-129_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1061-129_0_3_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1061-129_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1061-129_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1061-129_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1061-129_0_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1061-129_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1061-129_0_3_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1061-129_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1061-129_0_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1061-129_0_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1061-129_0_3_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_1061-129_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1061-129_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1061-129_0_3_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1061-129_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1061-129_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_MV_216_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-129_0_3_load_0 | 0 | 0.0098485 | 0.0024683 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-129_0_3_load_1 | 1 | 0.0075778 | 0.0018992 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-129_0_3_load_5 | 4 | 0.00899 | 0.0022531 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-129_0_3_load_18 | 6 | 0.007464 | 0.0018707 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-129_0_3_load_17 | 7 | 0.0071162 | 0.0017835 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-129_0_3_load_15 | 9 | 0.044819 | 0.011233 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-129_0_3_load_14 | 10 | 0.007012 | 0.0017574 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-129_0_3_load_24 | 12 | 0.010645 | 0.0026679 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-129_0_3_load_20 | 15 | 0.012112 | 0.0030355 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-129_0_3_load_26 | 16 | 0.014752 | 0.0036971 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-129_0_3_load_19 | 17 | 0.0060043 | 0.0015048 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-129_0_3_load_16 | 18 | 0.0070192 | 0.0017592 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-129_0_3_load_23 | 19 | 0.085404 | 0.021404 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-129_0_3_load_21 | 20 | 0.014088 | 0.0035308 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-129_0_3_load_22 | 21 | 0.08268 | 0.020721 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-129_0_3_line_0 |  | 0 | 1 | 0.0031088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-129_0_3_line_1 |  | 0 | 2 | 0.034791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-129_0_3_line_2 |  | 2 | 3 | 0.0083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-129_0_3_line_3 |  | 2 | 4 | 0.018784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-129_0_3_line_4 |  | 3 | 5 | 0.010262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-129_0_3_line_5 |  | 3 | 6 | 0.0046322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-129_0_3_line_6 |  | 4 | 7 | 0.020228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-129_0_3_line_7 |  | 5 | 11 | 0.011696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-129_0_3_line_8 |  | 5 | 12 | 0.020149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-129_0_3_line_9 |  | 6 | 17 | 0.018809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-129_0_3_line_10 |  | 7 | 18 | 0.040738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-129_0_3_line_11 |  | 8 | 9 | 0.086107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-129_0_3_line_12 |  | 8 | 10 | 0.080784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-129_0_3_line_13 |  | 10 | 11 | 0.012319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-129_0_3_line_14 |  | 12 | 21 | 0.026128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1061-129_0_3_line_15 |  | 13 | 14 | 0.040943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-129_0_3_line_16 |  | 13 | 15 | 0.01866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-129_0_3_line_17 |  | 14 | 16 | 0.0029971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-129_0_3_line_18 |  | 15 | 17 | 0.022611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-129_0_3_line_19 |  | 19 | 20 | 0.035477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-129_0_3_line_20 |  | 20 | 21 | 0.0018367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-129_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 22 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2665666.7426 | 1210066.2626 | 2665669.8103 | 1210066.7665
1 | 2665632.4112 | 1210060.6235 | 2665666.7426 | 1210066.2626
2 | 2665632.4112 | 1210060.6235 | 2665633.2699 | 1210055.8078 | 2665633.8238 | 1210052.4451
3 | 2665632.4112 | 1210060.6235 | 2665629.1102 | 1210079.1151
4 | 2665623.6704 | 1210050.9548 | 2665624.361 | 1210051.0514 | 2665627.8593 | 1210051.5679 | 2665628.861 | 1210051.7123 | 2665629.5136 | 1210051.8085 | 2665633.0649 | 1210052.3367 | 2665633.8238 | 1210052.4451
5 | 2665633.8238 | 1210052.4451 | 2665634.5738 | 1210047.8741
6 | 2665629.1102 | 1210079.1151 | 2665628.2317 | 1210084.0364 | 2665625.6792 | 1210099.0497
7 | 2665623.6704 | 1210050.9548 | 2665624.7127 | 1210044.6513 | 2665625.6214 | 1210039.4248
8 | 2665623.6704 | 1210050.9548 | 2665620.8131 | 1210068.1784 | 2665620.3482 | 1210070.828
9 | 2665637.6006 | 1210029.3107 | 2665637.1233 | 1210032.3358 | 2665634.5738 | 1210047.8741
10 | 2665625.5529 | 1210136.1611 | 2665621.3002 | 1210134.4466 | 2665620.2893 | 1210133.068 | 2665620.784 | 1210129.5491 | 2665625.4281 | 1210100.5268 | 2665625.6792 | 1210099.0497
11 | 2665533.7584 | 1210024.2839 | 2665533.6679 | 1210031.1316 | 2665533.6325 | 1210058.5702 | 2665533.5899 | 1210062.4499 | 2665533.5221 | 1210068.6196 | 2665533.3297 | 1210100.6594 | 2665533.1494 | 1210110.3878
12 | 2665533.7584 | 1210024.2839 | 2665571.0408 | 1210030.4305 | 2665613.4668 | 1210037.4218
13 | 2665625.6214 | 1210039.4248 | 2665613.4668 | 1210037.4218
14 | 2665620.3482 | 1210070.828 | 2665615.8328 | 1210096.5627
15 | 2665684.6748 | 1209995.6252 | 2665644.2251 | 1209988.5759
16 | 2665644.2251 | 1209988.5759 | 2665641.6498 | 1210003.6457 | 2665641.1244 | 1210006.9761
17 | 2665684.6748 | 1209995.6252 | 2665684.4443 | 1209998.6134
18 | 2665637.6006 | 1210029.3107 | 2665641.1244 | 1210006.9761
19 | 2665615.5154 | 1210098.3717 | 2665615.5017 | 1210098.4497 | 2665611.9242 | 1210120.346 | 2665609.8701 | 1210133.3966
20 | 2665615.5154 | 1210098.3717 | 2665615.8328 | 1210096.5627

## bus_geodata
| x | y | coords
0 | 2665666.7426 | 1210066.2626
1 | 2665669.8103 | 1210066.7665
2 | 2665632.4112 | 1210060.6235
3 | 2665633.8238 | 1210052.4451
4 | 2665629.1102 | 1210079.1151
5 | 2665623.6704 | 1210050.9548
6 | 2665634.5738 | 1210047.8741
7 | 2665625.6792 | 1210099.0497
8 | 2665533.7584 | 1210024.2839
9 | 2665533.1494 | 1210110.3878
10 | 2665613.4668 | 1210037.4218
11 | 2665625.6214 | 1210039.4247
12 | 2665620.3482 | 1210070.828
13 | 2665644.2251 | 1209988.5759
14 | 2665684.6748 | 1209995.6252
15 | 2665641.1244 | 1210006.9761
16 | 2665684.4443 | 1209998.6134
17 | 2665637.6006 | 1210029.3107
18 | 2665625.5529 | 1210136.1611
19 | 2665609.8701 | 1210133.3966
20 | 2665615.5154 | 1210098.3717
21 | 2665615.8328 | 1210096.5627
22 | 2665623.6704 | 1210050.9548

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99423 | -0.1108 | 0.0098485 | 0.0024683
1 | 0.9942 | -0.11122 | 0.0075778 | 0.0018992
2 | 0.99478 | -0.10012 | 0 | 0
3 | 0.99509 | -0.09419 | 0 | 0
4 | 0.99438 | -0.10777 | 0.00899 | 0.0022531
5 | 0.99584 | -0.079589 | 0 | 0
6 | 0.99492 | -0.097479 | 0.007464 | 0.0018707
7 | 0.99412 | -0.11281 | 0.0071162 | 0.0017835
8 | 0.99138 | -0.16549 | 0 | 0
9 | 0.98783 | -0.23418 | 0.044819 | 0.011233
10 | 0.9947 | -0.10149 | 0.007012 | 0.0017574
11 | 0.99529 | -0.090251 | 0 | 0
12 | 0.99829 | -0.032702 | 0.010645 | 0.0026679
13 | 0.99355 | -0.12395 | 0 | 0
14 | 0.99299 | -0.13462 | 0 | 0
15 | 0.9938 | -0.11909 | 0.012112 | 0.0030355
16 | 0.99295 | -0.1354 | 0.014752 | 0.0036971
17 | 0.99435 | -0.10837 | 0.0060043 | 0.0015048
18 | 0.99386 | -0.11786 | 0.0070192 | 0.0017592
19 | 0.99708 | -0.056158 | 0.085404 | 0.021404
20 | 0.99983 | -0.0031855 | 0.014088 | 0.0035308
21 | 1 | 0 | -0.24574 | -0.061648
22 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.007578 | 0.0018992 | -0.0075778 | -0.0018992 | 1.4996e-07 | 5.566e-08 | 0.011342 | 0.011342 | 0.011342 | 0.99423 | -0.1108 | 0.9942 | -0.11122 | 3.1158
1 | -0.017426 | -0.0043675 | 0.017435 | 0.0043727 | 8.8749e-06 | 5.2285e-06 | 0.026081 | 0.026081 | 0.026081 | 0.99423 | -0.1108 | 0.99478 | -0.10012 | 7.1652
2 | -0.040574 | -0.010176 | 0.040586 | 0.010183 | 1.1466e-05 | 7.2304e-06 | 0.060695 | 0.060695 | 0.060695 | 0.99478 | -0.10012 | 0.99509 | -0.09419 | 16.6744
3 | 0.023139 | 0.0058034 | -0.023131 | -0.0057982 | 8.4393e-06 | 5.1574e-06 | 0.034613 | 0.034613 | 0.034613 | 0.99478 | -0.10012 | 0.99438 | -0.10777 | 9.5092
4 | -0.080966 | -0.020321 | 0.081022 | 0.020357 | 5.6421e-05 | 3.5976e-05 | 0.12108 | 0.12108 | 0.12108 | 0.99509 | -0.09419 | 0.99584 | -0.079589 | 33.2648
5 | 0.04038 | 0.010138 | -0.040374 | -0.010134 | 6.3349e-06 | 3.9941e-06 | 0.060389 | 0.060389 | 0.060389 | 0.99509 | -0.09419 | 0.99492 | -0.097479 | 16.5905
6 | 0.014141 | 0.0035451 | -0.014137 | -0.0035432 | 3.3966e-06 | 1.9115e-06 | 0.021161 | 0.021161 | 0.021161 | 0.99438 | -0.10777 | 0.99412 | -0.11281 | 5.8134
7 | 0.052171 | 0.013205 | -0.052144 | -0.013188 | 2.6685e-05 | 1.6926e-05 | 0.078001 | 0.078001 | 0.078001 | 0.99584 | -0.079589 | 0.99529 | -0.090251 | 21.4289
8 | -0.13319 | -0.033562 | 0.13349 | 0.033754 | 0.00029948 | 0.0001914 | 0.19908 | 0.19908 | 0.19908 | 0.99584 | -0.079589 | 0.99829 | -0.032702 | 54.6937
9 | 0.03291 | 0.0082631 | -0.032893 | -0.0082524 | 1.7091e-05 | 1.0694e-05 | 0.049226 | 0.049226 | 0.049226 | 0.99492 | -0.097479 | 0.99435 | -0.10837 | 13.5237
10 | 0.0070209 | 0.0017597 | -0.0070192 | -0.0017592 | 1.6872e-06 | 5.5176e-07 | 0.010509 | 0.010509 | 0.010509 | 0.99412 | -0.11281 | 0.99386 | -0.11786 | 2.8872
11 | 0.044966 | 0.011326 | -0.044819 | -0.011233 | 0.00014718 | 9.3086e-05 | 0.067512 | 0.067512 | 0.067512 | 0.99138 | -0.16549 | 0.98783 | -0.23418 | 18.5474
12 | -0.044966 | -0.011326 | 0.045104 | 0.011413 | 0.00013808 | 8.7323e-05 | 0.067512 | 0.067512 | 0.067512 | 0.99138 | -0.16549 | 0.9947 | -0.10149 | 18.5473
13 | -0.052116 | -0.01317 | 0.052144 | 0.013188 | 2.8106e-05 | 1.7828e-05 | 0.078001 | 0.078001 | 0.078001 | 0.9947 | -0.10149 | 0.99529 | -0.090251 | 21.4289
14 | -0.14414 | -0.036422 | 0.14436 | 0.036566 | 0.00022635 | 0.00014418 | 0.21495 | 0.21495 | 0.21495 | 0.99829 | -0.032702 | 1 | 0 | 29.5264
15 | 0.01476 | 0.0037017 | -0.014752 | -0.0036974 | 7.5031e-06 | 4.2721e-06 | 0.022106 | 0.022106 | 0.022106 | 0.99355 | -0.12395 | 0.99299 | -0.13462 | 6.0732
16 | -0.01476 | -0.0037017 | 0.014763 | 0.0037036 | 3.4195e-06 | 1.9468e-06 | 0.022106 | 0.022106 | 0.022106 | 0.99355 | -0.12395 | 0.9938 | -0.11909 | 6.0731
17 | 0.014752 | 0.0036974 | -0.014752 | -0.0036971 | 5.4924e-07 | 3.1275e-07 | 0.022106 | 0.022106 | 0.022106 | 0.99299 | -0.13462 | 0.99295 | -0.1354 | 6.0732
18 | -0.026875 | -0.0067391 | 0.026889 | 0.0067476 | 1.3731e-05 | 8.4944e-06 | 0.040241 | 0.040241 | 0.040241 | 0.9938 | -0.11909 | 0.99435 | -0.10837 | 11.0552
19 | -0.085404 | -0.021404 | 0.08562 | 0.021542 | 0.00021612 | 0.00013785 | 0.12745 | 0.12745 | 0.12745 | 0.99708 | -0.056158 | 0.99983 | -0.0031855 | 35.0149
20 | -0.099708 | -0.025073 | 0.099723 | 0.025083 | 1.5172e-05 | 9.6862e-06 | 0.14842 | 0.14842 | 0.14842 | 0.99983 | -0.0031855 | 1 | 0 | 40.775

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32842 | 0.08237

## res_load
| p_mw | q_mvar
0 | 0.0098485 | 0.0024683
1 | 0.0075778 | 0.0018992
2 | 0.00899 | 0.0022531
3 | 0.007464 | 0.0018707
4 | 0.0071162 | 0.0017835
5 | 0.044819 | 0.011233
6 | 0.007012 | 0.0017574
7 | 0.010645 | 0.0026679
8 | 0.012112 | 0.0030355
9 | 0.014752 | 0.0036971
10 | 0.0060043 | 0.0015048
11 | 0.0070192 | 0.0017592
12 | 0.085404 | 0.021404
13 | 0.014088 | 0.0035308
14 | 0.08268 | 0.020721

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1