## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-137_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-137_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1061-137_0_3_node_15 | 0.4 | n |  | TRUE
3 | bus_LV_1061-137_0_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_1061-137_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-137_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1061-137_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1061-137_0_3_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1061-137_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1061-137_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1061-137_0_3_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1061-137_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1061-137_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1061-137_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1061-137_0_3_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_1061-137_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1061-137_0_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1061-137_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1061-137_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1061-137_0_3_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_1061-137_0_3_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1061-137_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1061-137_0_3_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_1061-137_0_3_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1061-137_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1061-137_0_3_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1061-137_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1061-137_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1061-137_0_3_node_30 | 0.4 | n |  | TRUE
29 | bus_MV_215_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-137_0_3_load_0 | 0 | 0.002726 | 0.00068319 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-137_0_3_load_15 | 2 | 0.0029894 | 0.00074921 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-137_0_3_load_23 | 6 | 0.028996 | 0.007267 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-137_0_3_load_27 | 7 | 0.011541 | 0.0028925 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-137_0_3_load_18 | 9 | 0.0015464 | 0.00038755 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-137_0_3_load_16 | 11 | 0.0047021 | 0.0011784 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-137_0_3_load_28 | 14 | 0.017399 | 0.0043605 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-137_0_3_load_22 | 17 | 0.0057396 | 0.0014385 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-137_0_3_load_34 | 18 | 0.024487 | 0.0061371 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-137_0_3_load_32 | 19 | 0.026113 | 0.0065446 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-137_0_3_load_21 | 21 | 0.009848 | 0.0024682 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-137_0_3_load_25 | 22 | 0.021971 | 0.0055063 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-137_0_3_load_26 | 23 | 0.018943 | 0.0047475 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-137_0_3_load_19 | 24 | 0.0015715 | 0.00039385 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-137_0_3_load_33 | 25 | 0.0251 | 0.0062906 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-137_0_3_load_29 | 26 | 0.030887 | 0.0077409 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-137_0_3_load_20 | 27 | 0.010174 | 0.0025499 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-137_0_3_load_30 | 28 | 0.025885 | 0.0064873 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-137_0_3_line_0 |  | 0 | 1 | 0.041512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-137_0_3_line_1 |  | 1 | 2 | 0.03397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-137_0_3_line_2 |  | 1 | 3 | 0.053406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-137_0_3_line_3 |  | 3 | 10 | 0.035428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-137_0_3_line_4 |  | 3 | 11 | 0.07343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-137_0_3_line_5 |  | 3 | 8 | 0.052221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-137_0_3_line_6 |  | 4 | 5 | 0.045071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-137_0_3_line_7 |  | 4 | 6 | 0.041412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-137_0_3_line_8 |  | 5 | 7 | 0.013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-137_0_3_line_9 |  | 6 | 21 | 0.019919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-137_0_3_line_10 |  | 7 | 23 | 0.015579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-137_0_3_line_11 |  | 8 | 9 | 0.030637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-137_0_3_line_12 |  | 9 | 24 | 0.020727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-137_0_3_line_13 |  | 10 | 25 | 0.034451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-137_0_3_line_14 |  | 12 | 13 | 0.097394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-137_0_3_line_15 |  | 12 | 14 | 0.072043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-137_0_3_line_16 |  | 13 | 18 | 0.0099462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-137_0_3_line_17 |  | 13 | 15 | 0.039143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-137_0_3_line_18 |  | 15 | 16 | 0.022302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-137_0_3_line_19 |  | 15 | 17 | 0.048079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-137_0_3_line_20 |  | 16 | 26 | 0.069008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1061-137_0_3_line_21 |  | 17 | 21 | 0.020867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-137_0_3_line_22 |  | 19 | 20 | 0.012629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-137_0_3_line_23 |  | 20 | 25 | 0.030293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-137_0_3_line_24 |  | 20 | 28 | 0.013839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-137_0_3_line_25 |  | 22 | 23 | 0.022046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-137_0_3_line_26 |  | 24 | 27 | 0.012347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-137_0_3_line_27 |  | 26 | 28 | 0.02172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-137_0_3_trafo_29 | 0.63 MVA 20/0.4 kV | 29 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2667741.7776 | 1210121.4731 | 2667744.6613 | 1210134.5917 | 2667755.7835 | 1210159.8002 | 2667756.017 | 1210160.2723
1 | 2667772.1343 | 1210136.8939 | 2667741.7776 | 1210121.4731
2 | 2667695.2501 | 1210095.0177 | 2667741.7776 | 1210121.4731
3 | 2667695.2501 | 1210095.0177 | 2667665.8482 | 1210075.1276
4 | 2667695.2501 | 1210095.0177 | 2667696.9792 | 1210116.7952 | 2667702.5308 | 1210130.5778 | 2667714.5592 | 1210150.9713 | 2667718.9063 | 1210163.2749
5 | 2667695.2501 | 1210095.0177 | 2667695.8061 | 1210088.2199 | 2667700.1392 | 1210085.4784 | 2667708.9776 | 1210076.8845 | 2667713.1276 | 1210076.8871 | 2667736.9112 | 1210076.1343
6 | 2667470.4803 | 1210119.3877 | 2667503.4423 | 1210119.5716 | 2667503.459 | 1210122.796 | 2667512.4653 | 1210122.8424
7 | 2667512.4653 | 1210122.8424 | 2667512.6679 | 1210096.8842 | 2667528.1204 | 1210096.9095
8 | 2667470.4803 | 1210119.3877 | 2667470.3505 | 1210105.8163
9 | 2667545.979 | 1210089.7344 | 2667534.4814 | 1210096.9199 | 2667528.1204 | 1210096.9095
10 | 2667470.3505 | 1210105.8163 | 2667470.2015 | 1210090.2381
11 | 2667736.9112 | 1210076.1343 | 2667735.7563 | 1210045.5189
12 | 2667735.7563 | 1210045.5189 | 2667735.6844 | 1210043.6114 | 2667736.9923 | 1210024.8384
13 | 2667665.8482 | 1210075.1276 | 2667661.2953 | 1210094.5658 | 2667653.4045 | 1210106.7152
14 | 2667650.6948 | 1209993.1497 | 2667649.376 | 1209994.8358 | 2667642.7059 | 1210003.2432 | 2667609.4306 | 1210003.155 | 2667558.1846 | 1210003.2637
15 | 2667650.6948 | 1209993.1497 | 2667661.1218 | 1209993.268 | 2667661.1443 | 1209931.6524
16 | 2667558.1846 | 1210003.2637 | 2667550.6864 | 1209996.7289
17 | 2667558.1846 | 1210003.2637 | 2667572.2667 | 1210014.8636 | 2667575.071 | 1210021.6106 | 2667574.5152 | 1210025.718 | 2667572.3221 | 1210030.1069 | 2667575.1857 | 1210033.6304
18 | 2667575.1857 | 1210033.6304 | 2667577.1344 | 1210034.0416 | 2667597.2636 | 1210037.1937
19 | 2667575.1857 | 1210033.6304 | 2667546.3118 | 1210059.6752 | 2667546.2101 | 1210068.8687
20 | 2667597.2636 | 1210037.1937 | 2667597.1509 | 1210042.4401 | 2667597.785 | 1210048.8624 | 2667596.7175 | 1210053.8534 | 2667596.5085 | 1210072.2957 | 2667599.1724 | 1210077.3401 | 2667609.4143 | 1210078.3568 | 2667615.1093 | 1210081.5232 | 2667620.5696 | 1210087.2998 | 2667621.8127 | 1210090.3546
21 | 2667545.979 | 1210089.7344 | 2667545.979 | 1210089.7344 | 2667546.2101 | 1210068.8687
22 | 2667629.4115 | 1210124.6341 | 2667620.2126 | 1210133.2863
23 | 2667629.4115 | 1210124.6341 | 2667642.3284 | 1210117.6317 | 2667652.4069 | 1210108.2513 | 2667653.4045 | 1210106.7152
24 | 2667629.4115 | 1210124.6341 | 2667626.3639 | 1210117.9065 | 2667624.6178 | 1210111.694
25 | 2667469.9907 | 1210068.1932 | 2667470.2015 | 1210090.2381
26 | 2667739.2501 | 1210012.7693 | 2667737.3825 | 1210019.2379 | 2667736.9923 | 1210024.8384
27 | 2667621.8127 | 1210090.3546 | 2667623.6014 | 1210094.7498 | 2667624.6178 | 1210111.694

## bus_geodata
| x | y | coords
0 | 2667756.017 | 1210160.2723
1 | 2667741.7776 | 1210121.4731
2 | 2667772.1343 | 1210136.8939
3 | 2667695.2501 | 1210095.0177
4 | 2667512.4653 | 1210122.8424
5 | 2667470.4803 | 1210119.3877
6 | 2667528.1204 | 1210096.9095
7 | 2667470.3505 | 1210105.8163
8 | 2667736.9112 | 1210076.1343
9 | 2667735.7563 | 1210045.5189
10 | 2667665.8482 | 1210075.1276
11 | 2667718.9063 | 1210163.2749
12 | 2667650.6948 | 1209993.1497
13 | 2667558.1846 | 1210003.2637
14 | 2667661.1443 | 1209931.6524
15 | 2667575.1857 | 1210033.6304
16 | 2667597.2636 | 1210037.1937
17 | 2667546.2101 | 1210068.8687
18 | 2667550.6864 | 1209996.7289
19 | 2667620.2126 | 1210133.2863
20 | 2667629.4115 | 1210124.6341
21 | 2667545.979 | 1210089.7344
22 | 2667469.9907 | 1210068.1932
23 | 2667470.2015 | 1210090.2381
24 | 2667736.9923 | 1210024.8384
25 | 2667653.4045 | 1210106.7152
26 | 2667621.8127 | 1210090.3546
27 | 2667739.2501 | 1210012.7693
28 | 2667624.6178 | 1210111.694
29 | 2667629.4115 | 1210124.6341

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99382 | -0.11894 | 0.002726 | 0.00068319
1 | 0.99392 | -0.11695 | 0 | 0
2 | 0.99383 | -0.11874 | 0.0029894 | 0.00074921
3 | 0.9942 | -0.11156 | 0 | 0
4 | 0.98315 | -0.32369 | 0 | 0
5 | 0.98096 | -0.36642 | 0 | 0
6 | 0.98516 | -0.28459 | 0.028996 | 0.007267
7 | 0.9803 | -0.37932 | 0.011541 | 0.0028925
8 | 0.99357 | -0.12381 | 0 | 0
9 | 0.9932 | -0.131 | 0.0015464 | 0.00038755
10 | 0.99497 | -0.096751 | 0 | 0
11 | 0.99389 | -0.11765 | 0.0047021 | 0.0011784
12 | 0.98967 | -0.19773 | 0 | 0
13 | 0.99122 | -0.16762 | 0 | 0
14 | 0.98852 | -0.22006 | 0.017399 | 0.0043605
15 | 0.99273 | -0.13857 | 0 | 0
16 | 0.99558 | -0.083928 | 0 | 0
17 | 0.98842 | -0.22145 | 0.0057396 | 0.0014385
18 | 0.991 | -0.17194 | 0.024487 | 0.0061371
19 | 0.99676 | -0.062192 | 0.026113 | 0.0065446
20 | 0.99706 | -0.056409 | 0 | 0
21 | 0.98666 | -0.2555 | 0.009848 | 0.0024682
22 | 0.97926 | -0.39969 | 0.021971 | 0.0055063
23 | 0.97971 | -0.39089 | 0.018943 | 0.0047475
24 | 0.99297 | -0.13531 | 0.0015715 | 0.00039385
25 | 0.99571 | -0.082374 | 0.0251 | 0.0062906
26 | 1 | 0 | -0.24372 | -0.061565
27 | 0.99286 | -0.13753 | 0.010174 | 0.0025499
28 | 0.99801 | -0.038244 | 0.025885 | 0.0064873
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.002726 | -0.00068319 | 0.0027262 | 0.00068282 | 2.5931e-07 | -3.7199e-07 | 0.0040815 | 0.0040813 | 0.0040815 | 0.99382 | -0.11894 | 0.99392 | -0.11695 | 1.1213
1 | 0.0029896 | 0.00074893 | -0.0029894 | -0.00074921 | 2.5519e-07 | -2.769e-07 | 0.0044757 | 0.0044758 | 0.0044758 | 0.99392 | -0.11695 | 0.99383 | -0.11874 | 1.2296
2 | -0.0057159 | -0.0014318 | 0.0057173 | 0.001432 | 1.4664e-06 | 2.4614e-07 | 0.008557 | 0.0085568 | 0.008557 | 0.99392 | -0.11695 | 0.9942 | -0.11156 | 2.3508
3 | -0.023729 | -0.0059503 | 0.023745 | 0.0059606 | 1.6758e-05 | 1.0265e-05 | 0.035516 | 0.035516 | 0.035516 | 0.9942 | -0.11156 | 0.99497 | -0.096751 | 9.7571
4 | 0.0047034 | 0.0011784 | -0.0047021 | -0.0011784 | 1.3646e-06 | -7.8574e-08 | 0.0070394 | 0.0070398 | 0.0070398 | 0.9942 | -0.11156 | 0.99389 | -0.11765 | 1.934
5 | 0.013308 | 0.0033399 | -0.0133 | -0.0033356 | 7.7703e-06 | 4.2963e-06 | 0.019919 | 0.01992 | 0.01992 | 0.9942 | -0.11156 | 0.99357 | -0.12381 | 5.4724
6 | 0.052626 | 0.013255 | -0.052519 | -0.013187 | 0.00010729 | 6.8096e-05 | 0.079674 | 0.079675 | 0.079675 | 0.98315 | -0.32369 | 0.98096 | -0.36642 | 21.8886
7 | -0.052626 | -0.013255 | 0.052725 | 0.013317 | 9.858e-05 | 6.2565e-05 | 0.079674 | 0.079674 | 0.079674 | 0.98315 | -0.32369 | 0.98516 | -0.28459 | 21.8886
8 | 0.052519 | 0.013187 | -0.052487 | -0.013166 | 3.2308e-05 | 2.0506e-05 | 0.079675 | 0.079675 | 0.079675 | 0.98096 | -0.36642 | 0.9803 | -0.37932 | 21.8886
9 | -0.08172 | -0.020584 | 0.081834 | 0.020657 | 0.00011387 | 7.2626e-05 | 0.12347 | 0.12347 | 0.12347 | 0.98516 | -0.28459 | 0.98666 | -0.2555 | 33.9203
10 | 0.040945 | 0.010274 | -0.040923 | -0.010259 | 2.257e-05 | 1.4248e-05 | 0.062156 | 0.062156 | 0.062156 | 0.9803 | -0.37932 | 0.97971 | -0.39089 | 17.0758
11 | 0.0133 | 0.0033356 | -0.013296 | -0.0033331 | 4.5588e-06 | 2.521e-06 | 0.01992 | 0.01992 | 0.01992 | 0.99357 | -0.12381 | 0.9932 | -0.131 | 5.4725
12 | 0.011749 | 0.0029456 | -0.011747 | -0.0029443 | 2.4086e-06 | 1.2733e-06 | 0.017603 | 0.017603 | 0.017603 | 0.9932 | -0.131 | 0.99297 | -0.13531 | 4.836
13 | -0.023745 | -0.0059606 | 0.023762 | 0.0059705 | 1.6296e-05 | 9.9814e-06 | 0.035516 | 0.035515 | 0.035516 | 0.99497 | -0.096751 | 0.99571 | -0.082374 | 9.757
14 | -0.017417 | -0.0043714 | 0.017442 | 0.0043862 | 2.5051e-05 | 1.4779e-05 | 0.02619 | 0.026189 | 0.02619 | 0.98967 | -0.19773 | 0.99122 | -0.16762 | 7.195
15 | 0.017417 | 0.0043714 | -0.017399 | -0.0043605 | 1.8531e-05 | 1.0935e-05 | 0.02619 | 0.02619 | 0.02619 | 0.98967 | -0.19773 | 0.98852 | -0.22006 | 7.1951
16 | 0.024492 | 0.0061402 | -0.024487 | -0.0061371 | 5.0423e-06 | 3.0989e-06 | 0.036768 | 0.036768 | 0.036768 | 0.99122 | -0.16762 | 0.991 | -0.17194 | 10.1012
17 | -0.041934 | -0.010526 | 0.041993 | 0.010563 | 5.818e-05 | 3.673e-05 | 0.062957 | 0.062957 | 0.062957 | 0.99122 | -0.16762 | 0.99273 | -0.13857 | 17.296
18 | -0.13995 | -0.035471 | 0.14032 | 0.035707 | 0.00036854 | 0.00023557 | 0.20992 | 0.20992 | 0.20992 | 0.99273 | -0.13857 | 0.99558 | -0.083928 | 57.6702
19 | 0.097961 | 0.024908 | -0.097572 | -0.024659 | 0.0003894 | 0.0002486 | 0.14696 | 0.14696 | 0.14696 | 0.99273 | -0.13857 | 0.98842 | -0.22145 | 40.3744
20 | -0.14032 | -0.035707 | 0.14089 | 0.03607 | 0.00057017 | 0.00036311 | 0.20992 | 0.20992 | 0.20992 | 0.99558 | -0.083928 | 1 | 0 | 28.8351
21 | 0.091832 | 0.023221 | -0.091682 | -0.023125 | 0.00014972 | 9.5553e-05 | 0.13832 | 0.13832 | 0.13832 | 0.98842 | -0.22145 | 0.98666 | -0.2555 | 38.0006
22 | -0.026113 | -0.0065446 | 0.026121 | 0.0065491 | 7.1969e-06 | 4.4414e-06 | 0.038983 | 0.038983 | 0.038983 | 0.99676 | -0.062192 | 0.99706 | -0.056409 | 10.7097
23 | 0.048922 | 0.0123 | -0.048861 | -0.012261 | 6.0578e-05 | 3.8375e-05 | 0.073025 | 0.073025 | 0.073025 | 0.99706 | -0.056409 | 0.99571 | -0.082374 | 20.0618
24 | -0.075043 | -0.018849 | 0.075108 | 0.01889 | 6.5108e-05 | 4.1488e-05 | 0.11201 | 0.11201 | 0.11201 | 0.99706 | -0.056409 | 0.99801 | -0.038244 | 30.7715
25 | -0.021971 | -0.0055063 | 0.02198 | 0.005512 | 9.2142e-06 | 5.6196e-06 | 0.033385 | 0.033385 | 0.033385 | 0.97926 | -0.39969 | 0.97971 | -0.39089 | 9.1717
26 | 0.010175 | 0.0025504 | -0.010174 | -0.0025499 | 1.0765e-06 | 5.2929e-07 | 0.015248 | 0.015248 | 0.015248 | 0.99297 | -0.13531 | 0.99286 | -0.13753 | 4.1891
27 | 0.10118 | 0.025495 | -0.10099 | -0.025377 | 0.00018474 | 0.00011795 | 0.1506 | 0.1506 | 0.1506 | 1 | 0 | 0.99801 | -0.038244 | 41.3742

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27461 | 0.069306

## res_load
| p_mw | q_mvar
0 | 0.002726 | 0.00068319
1 | 0.0029894 | 0.00074921
2 | 0.028996 | 0.007267
3 | 0.011541 | 0.0028925
4 | 0.0015464 | 0.00038755
5 | 0.0047021 | 0.0011784
6 | 0.017399 | 0.0043605
7 | 0.0057396 | 0.0014385
8 | 0.024487 | 0.0061371
9 | 0.026113 | 0.0065446
10 | 0.009848 | 0.0024682
11 | 0.021971 | 0.0055063
12 | 0.018943 | 0.0047475
13 | 0.0015715 | 0.00039385
14 | 0.0251 | 0.0062906
15 | 0.030887 | 0.0077409
16 | 0.010174 | 0.0025499
17 | 0.025885 | 0.0064873

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1