## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-143_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-143_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-143_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1061-143_0_5_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_1061-143_0_5_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_1061-143_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1061-143_0_5_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1061-143_0_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1061-143_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1061-143_0_5_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1061-143_0_5_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_1061-143_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1061-143_0_5_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1061-143_0_5_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_1061-143_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1061-143_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1061-143_0_5_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1061-143_0_5_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_1061-143_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1061-143_0_5_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_1061-143_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1061-143_0_5_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1061-143_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1061-143_0_5_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1061-143_0_5_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1061-143_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1061-143_0_5_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_1061-143_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1061-143_0_5_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1061-143_0_5_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1061-143_0_5_node_47 | 0.4 | n |  | TRUE
31 | bus_LV_1061-143_0_5_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1061-143_0_5_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1061-143_0_5_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1061-143_0_5_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1061-143_0_5_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_1061-143_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1061-143_0_5_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_1061-143_0_5_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1061-143_0_5_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_1061-143_0_5_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1061-143_0_5_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1061-143_0_5_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_1061-143_0_5_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1061-143_0_5_node_42 | 0.4 | n |  | TRUE
45 | bus_MV_215_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-143_0_5_load_0 | 0 | 0.024193 | 0.0060632 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-143_0_5_load_17 | 4 | 0.06412 | 0.01607 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-143_0_5_load_19 | 7 | 0.0709 | 0.017769 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-143_0_5_load_23 | 9 | 0.03443 | 0.0086291 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-143_0_5_load_21 | 10 | 0.0078489 | 0.0019671 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-143_0_5_load_34 | 13 | 0.02085 | 0.0052255 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-143_0_5_load_32 | 16 | 0.0067801 | 0.0016993 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-143_0_5_load_44 | 17 | 0.0081737 | 0.0020485 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-143_0_5_load_18 | 21 | 0.0062464 | 0.0015655 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-143_0_5_load_38 | 24 | 0.0088937 | 0.002229 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-143_0_5_load_16 | 25 | 0.011294 | 0.0028306 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-143_0_5_load_22 | 27 | 0.0085773 | 0.0021497 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-143_0_5_load_24 | 28 | 0.0092133 | 0.0023091 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-143_0_5_load_47 | 30 | 0.026281 | 0.0065866 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-143_0_5_load_30 | 31 | 0.0015908 | 0.00039869 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-143_0_5_load_37 | 32 | 0.063944 | 0.016026 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-143_0_5_load_25 | 33 | 0.051146 | 0.012818 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-143_0_5_load_43 | 34 | 0.02999 | 0.0075161 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-143_0_5_load_39 | 35 | 0.045326 | 0.01136 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-143_0_5_load_28 | 36 | 0.0087196 | 0.0021853 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-143_0_5_load_27 | 37 | 0.023 | 0.0057643 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-143_0_5_load_29 | 38 | 0.015868 | 0.0039768 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-143_0_5_load_46 | 39 | 0.0051585 | 0.0012928 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-143_0_5_load_31 | 40 | 0.013285 | 0.0033294 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-143_0_5_load_35 | 41 | 0.0020945 | 0.00052494 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-143_0_5_load_36 | 42 | 0.020579 | 0.0051576 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-143_0_5_load_41 | 43 | 0.0020935 | 0.00052467 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-143_0_5_load_42 | 44 | 0.0066304 | 0.0016617 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-143_0_5_line_0 |  | 0 | 1 | 0.017768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-143_0_5_line_1 |  | 1 | 2 | 0.035332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1061-143_0_5_line_2 |  | 1 | 3 | 0.036492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-143_0_5_line_3 |  | 2 | 4 | 0.028756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_1061-143_0_5_line_4 |  | 3 | 10 | 0.02741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-143_0_5_line_5 |  | 3 | 8 | 0.004846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-143_0_5_line_6 |  | 4 | 20 | 0.0085928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1061-143_0_5_line_7 |  | 5 | 6 | 0.013402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-143_0_5_line_8 |  | 5 | 7 | 0.022448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-143_0_5_line_9 |  | 6 | 9 | 0.020607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-143_0_5_line_10 |  | 8 | 9 | 0.015247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-143_0_5_line_11 |  | 10 | 27 | 0.024042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-143_0_5_line_12 |  | 11 | 12 | 0.006722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-143_0_5_line_13 |  | 11 | 13 | 0.029815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-143_0_5_line_14 |  | 12 | 28 | 0.050436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-143_0_5_line_15 |  | 12 | 23 | 0.060741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-143_0_5_line_16 |  | 13 | 14 | 0.079723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1061-143_0_5_line_17 |  | 14 | 15 | 0.017258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-143_0_5_line_18 |  | 14 | 16 | 0.013976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1061-143_0_5_line_19 |  | 15 | 17 | 0.0082482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-143_0_5_line_20 |  | 16 | 29 | 0.0042572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1061-143_0_5_line_21 |  | 17 | 18 | 0.096735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-143_0_5_line_22 |  | 18 | 19 | 0.036132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-143_0_5_line_23 |  | 19 | 30 | 0.10028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-143_0_5_line_24 |  | 20 | 21 | 0.01061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_1061-143_0_5_line_25 |  | 21 | 31 | 0.012432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1061-143_0_5_line_26 |  | 22 | 23 | 0.030213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-143_0_5_line_27 |  | 22 | 24 | 0.018608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-143_0_5_line_28 |  | 24 | 32 | 0.030376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-143_0_5_line_29 |  | 25 | 26 | 0.028489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1061-143_0_5_line_30 |  | 26 | 34 | 0.018946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1061-143_0_5_line_31 |  | 26 | 35 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1061-143_0_5_line_32 |  | 28 | 33 | 0.077807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-143_0_5_line_33 |  | 29 | 41 | 0.029874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_1061-143_0_5_line_34 |  | 29 | 42 | 0.019987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1061-143_0_5_line_35 |  | 31 | 36 | 0.0053215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_1061-143_0_5_line_36 |  | 34 | 40 | 0.015321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_1061-143_0_5_line_37 |  | 35 | 41 | 0.041292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1061-143_0_5_line_38 |  | 36 | 37 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_1061-143_0_5_line_39 |  | 37 | 38 | 0.015791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_1061-143_0_5_line_40 |  | 37 | 39 | 0.10276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1061-143_0_5_line_41 |  | 38 | 40 | 0.0078481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_1061-143_0_5_line_42 |  | 42 | 43 | 0.00017861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1061-143_0_5_line_43 |  | 43 | 44 | 0.011736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-143_0_5_trafo_16 | 0.63 MVA 20/0.4 kV | 45 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2666297.695 | 1210728.4536 | 2666313.642 | 1210720.6172
1 | 2666297.695 | 1210728.4536 | 2666296.9802 | 1210733.2819 | 2666276.3351 | 1210753.4651 | 2666276.9803 | 1210754.9065
2 | 2666286.4429 | 1210693.974 | 2666290.8481 | 1210712.6789 | 2666295.6645 | 1210721.738 | 2666297.695 | 1210728.4536
3 | 2666276.9803 | 1210754.9065 | 2666289.5893 | 1210780.7502
4 | 2666286.4429 | 1210693.974 | 2666280.1665 | 1210667.2923
5 | 2666290.8655 | 1210691.9664 | 2666286.4429 | 1210693.974
6 | 2666290.0759 | 1210788.9951 | 2666290.8605 | 1210783.3559 | 2666289.5893 | 1210780.7502
7 | 2666330.4096 | 1210671.9823 | 2666317.1574 | 1210669.7448
8 | 2666330.4096 | 1210671.9823 | 2666330.8748 | 1210669.7861 | 2666332.543 | 1210665.3464 | 2666334.815 | 1210650.0541
9 | 2666317.1574 | 1210669.7448 | 2666315.9879 | 1210675.1351 | 2666311.5147 | 1210678.9544 | 2666303.87 | 1210684.0894
10 | 2666290.8655 | 1210691.9664 | 2666294.7763 | 1210690.1976 | 2666303.87 | 1210684.0894
11 | 2666274.6613 | 1210643.8889 | 2666280.1665 | 1210667.2923
12 | 2666464.3524 | 1210760.4937 | 2666468.6508 | 1210755.3161
13 | 2666468.6508 | 1210755.3161 | 2666479.9329 | 1210782.9144
14 | 2666464.3524 | 1210760.4937 | 2666461.3578 | 1210765.9748 | 2666460.2397 | 1210772.1995 | 2666465.3687 | 1210785.9095 | 2666464.3483 | 1210790.1897 | 2666447.0464 | 1210797.6134
15 | 2666464.3524 | 1210760.4937 | 2666448.6364 | 1210739.9949 | 2666437.3602 | 1210709.7952 | 2666436.5682 | 1210707.207
16 | 2666483.7461 | 1210828.7629 | 2666450.4638 | 1210815.3951 | 2666479.9329 | 1210782.9144
17 | 2666495.7058 | 1210841.2371 | 2666483.7461 | 1210828.7629
18 | 2666483.7461 | 1210828.7629 | 2666473.0893 | 1210837.8053
19 | 2666495.7058 | 1210841.2371 | 2666502.4831 | 1210845.9382
20 | 2666468.8534 | 1210837.3801 | 2666473.0893 | 1210837.8053
21 | 2666576.1683 | 1210908.2533 | 2666565.0761 | 1210901.1474 | 2666532.5829 | 1210870.922 | 2666512.5985 | 1210852.9548 | 2666502.4831 | 1210845.9382
22 | 2666568.1342 | 1210940.3724 | 2666577.7809 | 1210930.5851 | 2666576.1683 | 1210908.2533
23 | 2666568.1342 | 1210940.3724 | 2666559.2534 | 1210930.5562 | 2666555.9441 | 1210904.9924 | 2666509.6713 | 1210864.6628
24 | 2666290.0759 | 1210788.9951 | 2666297.5334 | 1210796.5423
25 | 2666297.5334 | 1210796.5423 | 2666306.2712 | 1210805.3851
26 | 2666436.5682 | 1210707.207 | 2666426.452 | 1210682.0345 | 2666423.5962 | 1210683.2368
27 | 2666423.5962 | 1210683.2368 | 2666406.4708 | 1210690.5159
28 | 2666406.4708 | 1210690.5159 | 2666378.5153 | 1210702.3984
29 | 2666376.4943 | 1210786.821 | 2666364.8039 | 1210760.8414
30 | 2666376.4943 | 1210786.821 | 2666357.7386 | 1210789.5029
31 | 2666376.4943 | 1210786.821 | 2666407.1527 | 1210802.898
32 | 2666447.0464 | 1210797.6134 | 2666432.8792 | 1210803.6921 | 2666429.5639 | 1210802.4878 | 2666399.4141 | 1210785.564 | 2666389.9748 | 1210763.1851
33 | 2666468.8534 | 1210837.3801 | 2666464.4733 | 1210836.9421 | 2666450.2897 | 1210827.6118 | 2666443.2673 | 1210822.8326
34 | 2666468.8534 | 1210837.3801 | 2666453.1604 | 1210849.757
35 | 2666311.3603 | 1210806.9406 | 2666306.2712 | 1210805.3851 | 2666306.2712 | 1210805.3851
36 | 2666345.0929 | 1210798.153 | 2666357.7386 | 1210789.5029
37 | 2666443.2673 | 1210822.8326 | 2666436.8866 | 1210818.4903 | 2666407.1527 | 1210802.898
38 | 2666311.3603 | 1210806.9406 | 2666320.3892 | 1210809.7002 | 2666325.1246 | 1210809.8193
39 | 2666338.6608 | 1210802.6443 | 2666332.9624 | 1210807.3607 | 2666327.5233 | 1210809.8796 | 2666325.1246 | 1210809.8193
40 | 2666325.1246 | 1210809.8193 | 2666352.1462 | 1210908.9588
41 | 2666345.0929 | 1210798.153 | 2666339.2981 | 1210802.1168 | 2666338.6608 | 1210802.6443
42 | 2666453.0202 | 1210849.8676 | 2666453.1604 | 1210849.757
43 | 2666443.8051 | 1210857.1355 | 2666453.0202 | 1210849.8676

## bus_geodata
| x | y | coords
0 | 2666313.642 | 1210720.6172
1 | 2666297.695 | 1210728.4536
2 | 2666276.9803 | 1210754.9065
3 | 2666286.4429 | 1210693.974
4 | 2666289.5893 | 1210780.7502
5 | 2666330.4096 | 1210671.9823
6 | 2666317.1574 | 1210669.7448
7 | 2666334.815 | 1210650.0541
8 | 2666290.8655 | 1210691.9664
9 | 2666303.87 | 1210684.0894
10 | 2666280.1665 | 1210667.2923
11 | 2666468.6508 | 1210755.3161
12 | 2666464.3524 | 1210760.4937
13 | 2666479.9329 | 1210782.9144
14 | 2666483.7461 | 1210828.7629
15 | 2666495.7058 | 1210841.2371
16 | 2666473.0893 | 1210837.8053
17 | 2666502.4831 | 1210845.9382
18 | 2666576.1683 | 1210908.2533
19 | 2666568.1342 | 1210940.3724
20 | 2666290.0759 | 1210788.9951
21 | 2666297.5334 | 1210796.5423
22 | 2666423.5962 | 1210683.2368
23 | 2666436.5682 | 1210707.207
24 | 2666406.4708 | 1210690.5159
25 | 2666364.8039 | 1210760.8414
26 | 2666376.4943 | 1210786.821
27 | 2666274.6613 | 1210643.8889
28 | 2666447.0464 | 1210797.6134
29 | 2666468.8534 | 1210837.3801
30 | 2666509.6713 | 1210864.6628
31 | 2666306.2712 | 1210805.3851
32 | 2666378.5153 | 1210702.3984
33 | 2666389.9748 | 1210763.1851
34 | 2666357.7386 | 1210789.5029
35 | 2666407.1527 | 1210802.898
36 | 2666311.3603 | 1210806.9406
37 | 2666325.1246 | 1210809.8193
38 | 2666338.6608 | 1210802.6443
39 | 2666352.1462 | 1210908.9588
40 | 2666345.0929 | 1210798.153
41 | 2666443.2673 | 1210822.8326
42 | 2666453.1604 | 1210849.757
43 | 2666453.0202 | 1210849.8676
44 | 2666443.8051 | 1210857.1355
45 | 2666376.4943 | 1210786.821

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9883 | -0.22389 | 0.024193 | 0.0060632
1 | 0.9887 | -0.21622 | 0 | 0
2 | 0.99108 | -0.17036 | 0 | 0
3 | 0.98459 | -0.29578 | 0 | 0
4 | 0.99186 | -0.15548 | 0.06412 | 0.01607
5 | 0.9804 | -0.37753 | 0 | 0
6 | 0.98128 | -0.36032 | 0 | 0
7 | 0.97892 | -0.40644 | 0.0709 | 0.017769
8 | 0.98412 | -0.30496 | 0 | 0
9 | 0.98263 | -0.33391 | 0.03443 | 0.0086291
10 | 0.98417 | -0.30388 | 0.0078489 | 0.0019671
11 | 0.98214 | -0.34147 | 0 | 0
12 | 0.98131 | -0.35767 | 0 | 0
13 | 0.98584 | -0.26998 | 0.02085 | 0.0052255
14 | 0.99156 | -0.16048 | 0 | 0
15 | 0.99101 | -0.17103 | 0 | 0
16 | 0.99205 | -0.15115 | 0.0067801 | 0.0016993
17 | 0.99075 | -0.17608 | 0.0081737 | 0.0020485
18 | 0.98841 | -0.22134 | 0 | 0
19 | 0.98754 | -0.2383 | 0 | 0
20 | 0.99219 | -0.14908 | 0 | 0
21 | 0.9926 | -0.14119 | 0.0062464 | 0.0015655
22 | 0.97513 | -0.47834 | 0 | 0
23 | 0.97718 | -0.43809 | 0 | 0
24 | 0.97386 | -0.50322 | 0.0088937 | 0.002229
25 | 1 | 0 | -0.59554 | -0.15191
26 | 0.99692 | -0.058375 | 0 | 0
27 | 0.98398 | -0.30759 | 0.0085773 | 0.0021497
28 | 0.97848 | -0.41293 | 0.0092133 | 0.0023091
29 | 0.9922 | -0.1482 | 0 | 0
30 | 0.98511 | -0.28552 | 0.026281 | 0.0065866
31 | 0.9931 | -0.13168 | 0.0015908 | 0.00039869
32 | 0.97205 | -0.53898 | 0.063944 | 0.016026
33 | 0.97478 | -0.48565 | 0.051146 | 0.012818
34 | 0.99583 | -0.079262 | 0.02999 | 0.0075161
35 | 0.99518 | -0.091465 | 0.045326 | 0.01136
36 | 0.99331 | -0.12758 | 0.0087196 | 0.0021853
37 | 0.9939 | -0.11624 | 0.023 | 0.0057643
38 | 0.99464 | -0.10205 | 0.015868 | 0.0039768
39 | 0.99342 | -0.1256 | 0.0051585 | 0.0012928
40 | 0.99503 | -0.094568 | 0.013285 | 0.0033294
41 | 0.99345 | -0.12447 | 0.0020945 | 0.00052494
42 | 0.99167 | -0.15858 | 0.020579 | 0.0051576
43 | 0.99167 | -0.1586 | 0.0020935 | 0.00052467
44 | 0.9916 | -0.15998 | 0.0066304 | 0.0016617
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.024193 | -0.0060632 | 0.024201 | 0.0060686 | 8.8404e-06 | 5.4301e-06 | 0.036425 | 0.036425 | 0.036425 | 0.9883 | -0.22389 | 0.9887 | -0.21622 | 10.0068
1 | -0.14687 | -0.037166 | 0.1472 | 0.037373 | 0.00032406 | 0.00020649 | 0.22117 | 0.22117 | 0.22117 | 0.9887 | -0.21622 | 0.99108 | -0.17036 | 30.3809
2 | 0.12267 | 0.031098 | -0.1222 | -0.030799 | 0.00046708 | 0.00029847 | 0.18475 | 0.18475 | 0.18475 | 0.9887 | -0.21622 | 0.98459 | -0.29578 | 50.755
3 | -0.1472 | -0.037373 | 0.1473 | 0.037439 | 0.0001055 | 6.5665e-05 | 0.22117 | 0.22117 | 0.22117 | 0.99108 | -0.17036 | 0.99186 | -0.15548 | 12.1523
4 | 0.016434 | 0.0041212 | -0.016428 | -0.0041175 | 6.3412e-06 | 3.7099e-06 | 0.024838 | 0.024838 | 0.024838 | 0.98459 | -0.29578 | 0.98417 | -0.30388 | 6.8236
5 | 0.10577 | 0.026678 | -0.10572 | -0.026648 | 4.647e-05 | 2.9679e-05 | 0.15991 | 0.15991 | 0.15991 | 0.98459 | -0.29578 | 0.98412 | -0.30496 | 43.9314
6 | -0.21142 | -0.053509 | 0.21149 | 0.05355 | 6.4911e-05 | 4.0988e-05 | 0.31737 | 0.31737 | 0.31737 | 0.99186 | -0.15548 | 0.99219 | -0.14908 | 17.4377
7 | -0.070998 | -0.017832 | 0.071056 | 0.017869 | 5.8373e-05 | 3.719e-05 | 0.10777 | 0.10777 | 0.10777 | 0.9804 | -0.37753 | 0.98128 | -0.36032 | 29.6077
8 | 0.070998 | 0.017832 | -0.0709 | -0.017769 | 9.7773e-05 | 6.2292e-05 | 0.10777 | 0.10777 | 0.10777 | 0.9804 | -0.37753 | 0.97892 | -0.40644 | 29.6077
9 | -0.071056 | -0.017869 | 0.071146 | 0.017926 | 8.9754e-05 | 5.7182e-05 | 0.10777 | 0.10777 | 0.10777 | 0.98128 | -0.36032 | 0.98263 | -0.33391 | 29.6077
10 | 0.10572 | 0.026648 | -0.10558 | -0.026555 | 0.00014621 | 9.3379e-05 | 0.15991 | 0.15991 | 0.15991 | 0.98412 | -0.30496 | 0.98263 | -0.33391 | 43.9315
11 | 0.0085789 | 0.0021504 | -0.0085773 | -0.0021497 | 1.5169e-06 | 6.6534e-07 | 0.012971 | 0.012971 | 0.012971 | 0.98417 | -0.30388 | 0.98398 | -0.30759 | 3.5635
12 | 0.13426 | 0.034059 | -0.13416 | -0.033992 | 0.00010445 | 6.6764e-05 | 0.20356 | 0.20356 | 0.20356 | 0.98214 | -0.34147 | 0.98131 | -0.35767 | 55.9233
13 | -0.13426 | -0.034059 | 0.13472 | 0.034355 | 0.00046329 | 0.00029613 | 0.20356 | 0.20356 | 0.20356 | 0.98214 | -0.34147 | 0.98584 | -0.26998 | 55.9233
14 | 0.060698 | 0.015342 | -0.060537 | -0.01524 | 0.00016038 | 0.00010201 | 0.092086 | 0.092087 | 0.092087 | 0.98131 | -0.35767 | 0.97848 | -0.41293 | 25.2985
15 | 0.073458 | 0.01865 | -0.073175 | -0.018469 | 0.00028305 | 0.00018039 | 0.11147 | 0.11147 | 0.11147 | 0.98131 | -0.35767 | 0.97718 | -0.43809 | 30.6249
16 | -0.15557 | -0.039581 | 0.1564 | 0.040107 | 0.00082573 | 0.00052642 | 0.23503 | 0.23503 | 0.23503 | 0.98584 | -0.26998 | 0.99156 | -0.16048 | 32.2845
17 | 0.034618 | 0.0087365 | -0.034601 | -0.0087255 | 1.7481e-05 | 1.0965e-05 | 0.051972 | 0.051972 | 0.051972 | 0.99156 | -0.16048 | 0.99101 | -0.17103 | 14.2781
18 | -0.19102 | -0.048844 | 0.1911 | 0.048898 | 8.6341e-05 | 5.4357e-05 | 0.287 | 0.287 | 0.287 | 0.99156 | -0.16048 | 0.99205 | -0.15115 | 15.7694
19 | 0.034601 | 0.0087255 | -0.034592 | -0.0087203 | 8.3547e-06 | 5.2408e-06 | 0.051972 | 0.051972 | 0.051972 | 0.99101 | -0.17103 | 0.99075 | -0.17608 | 14.2781
20 | -0.19788 | -0.050597 | 0.19791 | 0.050615 | 2.8197e-05 | 1.7771e-05 | 0.29717 | 0.29717 | 0.29717 | 0.99205 | -0.15115 | 0.9922 | -0.1482 | 16.3281
21 | 0.026419 | 0.0066718 | -0.026361 | -0.0066364 | 5.7163e-05 | 3.5342e-05 | 0.039696 | 0.039697 | 0.039697 | 0.99075 | -0.17608 | 0.98841 | -0.22134 | 10.9057
22 | 0.026361 | 0.0066364 | -0.02634 | -0.0066232 | 2.1352e-05 | 1.3202e-05 | 0.039697 | 0.039697 | 0.039697 | 0.98841 | -0.22134 | 0.98754 | -0.2383 | 10.9057
23 | 0.02634 | 0.0066232 | -0.026281 | -0.0065866 | 5.9263e-05 | 3.6648e-05 | 0.039697 | 0.039697 | 0.039697 | 0.98754 | -0.2383 | 0.98511 | -0.28552 | 10.9058
24 | -0.21149 | -0.05355 | 0.21157 | 0.0536 | 8.015e-05 | 5.0611e-05 | 0.31737 | 0.31737 | 0.31737 | 0.99219 | -0.14908 | 0.9926 | -0.14119 | 17.4377
25 | -0.21781 | -0.055166 | 0.21791 | 0.055229 | 9.9533e-05 | 6.2897e-05 | 0.32673 | 0.32673 | 0.32673 | 0.9926 | -0.14119 | 0.9931 | -0.13168 | 17.9522
26 | -0.073034 | -0.01838 | 0.073175 | 0.018469 | 0.00014079 | 8.9729e-05 | 0.11147 | 0.11147 | 0.11147 | 0.97513 | -0.47834 | 0.97718 | -0.43809 | 30.6249
27 | 0.073034 | 0.01838 | -0.072947 | -0.018324 | 8.6714e-05 | 5.5265e-05 | 0.11147 | 0.11147 | 0.11147 | 0.97513 | -0.47834 | 0.97386 | -0.50322 | 30.6249
28 | 0.064053 | 0.016095 | -0.063944 | -0.016026 | 0.00010914 | 6.9475e-05 | 0.097886 | 0.097886 | 0.097886 | 0.97386 | -0.50322 | 0.97205 | -0.53898 | 26.8917
29 | 0.59389 | 0.15191 | -0.59221 | -0.15084 | 0.0016727 | 0.0010687 | 0.8848 | 0.8848 | 0.8848 | 1 | 0 | 0.99692 | -0.058375 | 48.6153
30 | 0.31649 | 0.080307 | -0.31618 | -0.080105 | 0.00031758 | 0.00020202 | 0.47275 | 0.47275 | 0.47275 | 0.99692 | -0.058375 | 0.99583 | -0.079262 | 25.9754
31 | 0.27572 | 0.07053 | -0.27528 | -0.07025 | 0.00044082 | 0.00027987 | 0.41205 | 0.41205 | 0.41205 | 0.99692 | -0.058375 | 0.99518 | -0.091465 | 22.64
32 | 0.051324 | 0.012931 | -0.051146 | -0.012818 | 0.00017786 | 0.00011286 | 0.078076 | 0.078076 | 0.078076 | 0.97848 | -0.41293 | 0.97478 | -0.48565 | 21.4494
33 | -0.22723 | -0.057968 | 0.22749 | 0.058133 | 0.00026075 | 0.00016495 | 0.34114 | 0.34114 | 0.34114 | 0.9922 | -0.1482 | 0.99345 | -0.12447 | 18.744
34 | 0.029318 | 0.0073531 | -0.029303 | -0.0073441 | 1.449e-05 | 9.0158e-06 | 0.04397 | 0.04397 | 0.04397 | 0.9922 | -0.1482 | 0.99167 | -0.15858 | 12.0797
35 | -0.2195 | -0.055627 | 0.21955 | 0.055655 | 4.323e-05 | 2.7323e-05 | 0.32911 | 0.32911 | 0.32911 | 0.9931 | -0.13168 | 0.99331 | -0.12758 | 18.0832
36 | 0.28619 | 0.072589 | -0.28598 | -0.072455 | 0.00021044 | 0.00013368 | 0.42794 | 0.42794 | 0.42794 | 0.99583 | -0.079262 | 0.99503 | -0.094568 | 23.5132
37 | 0.22995 | 0.05889 | -0.22958 | -0.058658 | 0.00036707 | 0.00023225 | 0.34428 | 0.34428 | 0.34428 | 0.99518 | -0.091465 | 0.99345 | -0.12447 | 18.9163
38 | -0.22827 | -0.05784 | 0.22839 | 0.057919 | 0.0001245 | 7.8764e-05 | 0.34218 | 0.34218 | 0.34218 | 0.99331 | -0.12758 | 0.9939 | -0.11624 | 18.8009
39 | -0.25655 | -0.064976 | 0.25673 | 0.065087 | 0.00017494 | 0.00011094 | 0.38434 | 0.38434 | 0.38434 | 0.9939 | -0.11624 | 0.99464 | -0.10205 | 21.1174
40 | 0.0051608 | 0.001293 | -0.0051585 | -0.0012928 | 2.3005e-06 | 1.4124e-07 | 0.0077263 | 0.0077268 | 0.0077268 | 0.9939 | -0.11624 | 0.99342 | -0.1256 | 2.1228
41 | -0.27259 | -0.069064 | 0.27269 | 0.069126 | 9.8017e-05 | 6.2221e-05 | 0.40807 | 0.40807 | 0.40807 | 0.99464 | -0.10205 | 0.99503 | -0.094568 | 22.4217
42 | 0.0087243 | 0.0021865 | -0.0087243 | -0.0021865 | 1.1479e-08 | 5.0426e-09 | 0.013091 | 0.013091 | 0.013091 | 0.99167 | -0.15858 | 0.99167 | -0.1586 | 3.5964
43 | 0.0066308 | 0.0016619 | -0.0066304 | -0.0016617 | 4.357e-07 | 1.2744e-07 | 0.0099497 | 0.0099498 | 0.0099498 | 0.99167 | -0.1586 | 0.9916 | -0.15998 | 2.7334

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60683 | 0.15474

## res_load
| p_mw | q_mvar
0 | 0.024193 | 0.0060632
1 | 0.06412 | 0.01607
2 | 0.0709 | 0.017769
3 | 0.03443 | 0.0086291
4 | 0.0078489 | 0.0019671
5 | 0.02085 | 0.0052255
6 | 0.0067801 | 0.0016993
7 | 0.0081737 | 0.0020485
8 | 0.0062464 | 0.0015655
9 | 0.0088937 | 0.002229
10 | 0.011294 | 0.0028306
11 | 0.0085773 | 0.0021497
12 | 0.0092133 | 0.0023091
13 | 0.026281 | 0.0065866
14 | 0.0015908 | 0.00039869
15 | 0.063944 | 0.016026
16 | 0.051146 | 0.012818
17 | 0.02999 | 0.0075161
18 | 0.045326 | 0.01136
19 | 0.0087196 | 0.0021853
20 | 0.023 | 0.0057643
21 | 0.015868 | 0.0039768
22 | 0.0051585 | 0.0012928
23 | 0.013285 | 0.0033294
24 | 0.0020945 | 0.00052494
25 | 0.020579 | 0.0051576
26 | 0.0020935 | 0.00052467
27 | 0.0066304 | 0.0016617

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1