## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-14_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-14_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-14_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-14_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-14_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-14_0_6_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1061-14_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1061-14_0_6_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1061-14_0_6_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1061-14_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1061-14_0_6_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_1061-14_0_6_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1061-14_0_6_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1061-14_0_6_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1061-14_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1061-14_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1061-14_0_6_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1061-14_0_6_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1061-14_0_6_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1061-14_0_6_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1061-14_0_6_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1061-14_0_6_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1061-14_0_6_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1061-14_0_6_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_1061-14_0_6_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_1061-14_0_6_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1061-14_0_6_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1061-14_0_6_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1061-14_0_6_node_25 | 0.4 | n |  | TRUE
29 | bus_MV_220_0_node_141 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-14_0_6_load_0 | 0 | 0.042216 | 0.01058 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-14_0_6_load_3 | 3 | 0.093325 | 0.023389 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-14_0_6_load_23 | 8 | 0.024124 | 0.006046 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-14_0_6_load_18 | 11 | 0.068326 | 0.017124 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-14_0_6_load_26 | 12 | 0.052341 | 0.013118 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-14_0_6_load_27 | 16 | 0.0043213 | 0.001083 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-14_0_6_load_19 | 19 | 0.051309 | 0.012859 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-14_0_6_load_21 | 20 | 0.021426 | 0.0053698 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-14_0_6_load_20 | 21 | 0.036141 | 0.0090577 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-14_0_6_load_28 | 23 | 0.0048336 | 0.0012114 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-14_0_6_load_30 | 24 | 0.00080651 | 0.00020213 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-14_0_6_load_22 | 26 | 0.015324 | 0.0038405 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-14_0_6_load_29 | 27 | 0.0020732 | 0.00051959 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-14_0_6_load_25 | 28 | 0.079207 | 0.019851 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-14_0_6_line_0 |  | 0 | 1 | 0.057011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-14_0_6_line_1 |  | 0 | 2 | 0.075031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-14_0_6_line_2 |  | 1 | 3 | 0.1304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-14_0_6_line_3 |  | 1 | 4 | 0.054487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-14_0_6_line_4 |  | 2 | 5 | 0.034398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-14_0_6_line_5 |  | 3 | 6 | 0.034296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1061-14_0_6_line_6 |  | 4 | 7 | 0.008289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-14_0_6_line_7 |  | 4 | 8 | 0.051277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-14_0_6_line_8 |  | 5 | 25 | 0.075857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-14_0_6_line_9 |  | 6 | 12 | 0.020629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-14_0_6_line_10 |  | 6 | 13 | 0.21227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1061-14_0_6_line_11 |  | 7 | 27 | 0.047968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-14_0_6_line_12 |  | 9 | 10 | 0.072433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-14_0_6_line_13 |  | 9 | 11 | 0.016001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-14_0_6_line_14 |  | 10 | 26 | 0.014599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-14_0_6_line_15 |  | 11 | 19 | 0.01652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-14_0_6_line_16 |  | 13 | 21 | 0.040491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1061-14_0_6_line_17 |  | 14 | 15 | 0.15073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-14_0_6_line_18 |  | 14 | 16 | 0.0075088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-14_0_6_line_19 |  | 15 | 24 | 0.016144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-14_0_6_line_20 |  | 15 | 22 | 0.15453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-14_0_6_line_21 |  | 17 | 18 | 0.037368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1061-14_0_6_line_22 |  | 17 | 19 | 0.033128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1061-14_0_6_line_23 |  | 18 | 20 | 0.0097292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-14_0_6_line_24 |  | 18 | 21 | 0.011206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1061-14_0_6_line_25 |  | 20 | 28 | 0.020637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-14_0_6_line_26 |  | 22 | 23 | 0.0071525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-14_0_6_line_27 |  | 24 | 25 | 0.016254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-14_0_6_trafo_6 | 0.63 MVA 20/0.4 kV | 29 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2666500.1477 | 1211221.221 | 2666471.4662 | 1211270.4925
1 | 2666439.65 | 1211334.4726 | 2666445.901 | 1211332.6966 | 2666448.6034 | 1211309.7681 | 2666471.4662 | 1211270.4925
2 | 2666500.1477 | 1211221.221 | 2666467.111 | 1211216.7057 | 2666370.713 | 1211205.3881
3 | 2666500.1477 | 1211221.221 | 2666539.0808 | 1211225.1018 | 2666539.1986 | 1211224.0803 | 2666539.988 | 1211224.1669 | 2666539.886 | 1211225.133 | 2666540.6836 | 1211225.1642 | 2666540.378 | 1211229.3967 | 2666544.8625 | 1211235.4393
4 | 2666439.65 | 1211334.4726 | 2666437.4685 | 1211351.5811 | 2666437.4269 | 1211351.903 | 2666436.6677 | 1211357.9761 | 2666442.5814 | 1211357.8307 | 2666447.0536 | 1211356.1128
5 | 2666336.6505 | 1211201.389 | 2666370.713 | 1211205.3881
6 | 2666544.8625 | 1211235.4393 | 2666540.1056 | 1211242.2349
7 | 2666544.8625 | 1211235.4393 | 2666548.9378 | 1211233.2056 | 2666582.8491 | 1211202.9319 | 2666583.7229 | 1211202.1524
8 | 2666426.3161 | 1211416.119 | 2666436.2886 | 1211393.3715 | 2666437.7155 | 1211390.1187 | 2666443.5405 | 1211367.9143 | 2666442.4014 | 1211365.1221 | 2666436.5368 | 1211362.2217 | 2666436.6677 | 1211357.9761 | 2666442.5814 | 1211357.8307 | 2666447.0536 | 1211356.1128
9 | 2666336.6505 | 1211201.389 | 2666350.67 | 1211186.2561
10 | 2666178.5955 | 1211132.0581 | 2666179.4016 | 1211121.7385 | 2666179.7918 | 1211113.282 | 2666175.6489 | 1211110.6567 | 2666176.8145 | 1211113.1378 | 2666197.0545 | 1211127.9381 | 2666210.6596 | 1211136.6277 | 2666226.8907 | 1211146.992 | 2666242.7897 | 1211157.1414 | 2666259.3995 | 1211167.61 | 2666275.9533 | 1211178.3226 | 2666292.3274 | 1211188.7887 | 2666303.5932 | 1211195.9739 | 2666306.6307 | 1211196.1744 | 2666307.1394 | 1211196.2134 | 2666307.1214 | 1211197.1471 | 2666308.3736 | 1211197.2945 | 2666323.1058 | 1211199.5929 | 2666336.6505 | 1211201.389
11 | 2666540.1056 | 1211242.2349 | 2666541.2428 | 1211252.0092 | 2666539.4232 | 1211255.0352 | 2666530.4178 | 1211270.0552 | 2666521.6442 | 1211284.7139
12 | 2666054.2712 | 1211151.2036 | 2666056.8043 | 1211155.7789 | 2666062.7032 | 1211153.554 | 2666069.5826 | 1211154.0526 | 2666075.7269 | 1211156.4333 | 2666081.2677 | 1211160.4638 | 2666097.6998 | 1211175.3327 | 2666112.0719 | 1211186.8212
13 | 2666112.0719 | 1211186.8212 | 2666125.8035 | 1211195.0351
14 | 2666054.2712 | 1211151.2036 | 2666051.8109 | 1211151.0318 | 2666041.2547 | 1211145.0515
15 | 2666125.8035 | 1211195.0351 | 2666139.9811 | 1211203.5157
16 | 2666178.5955 | 1211132.0581 | 2666176.7491 | 1211151.9054 | 2666174.1036 | 1211172.2923
17 | 2666279.1483 | 1211456.3185 | 2666283.3563 | 1211456.4764 | 2666286.3998 | 1211453.3861 | 2666292.1511 | 1211454.1727 | 2666295.5053 | 1211454.5769 | 2666303.0943 | 1211455.4729 | 2666306.8052 | 1211455.9144 | 2666311.5787 | 1211456.4789 | 2666313.3165 | 1211456.6872 | 2666316.4134 | 1211456.9996 | 2666320.1099 | 1211457.3743 | 2666404.5224 | 1211467.2858 | 2666406.5661 | 1211461.1825 | 2666413.3105 | 1211445.7925
18 | 2666279.1483 | 1211456.3185 | 2666271.6809 | 1211455.5302
19 | 2666413.3105 | 1211445.7925 | 2666419.7912 | 1211431.0062
20 | 2666300.3392 | 1211503.0161 | 2666315.1757 | 1211504.0705 | 2666316.3956 | 1211492.7659 | 2666378.9491 | 1211500.3217 | 2666395.7625 | 1211480.7855 | 2666401.3979 | 1211474.2331 | 2666404.5224 | 1211467.2858 | 2666406.5661 | 1211461.1825 | 2666413.3105 | 1211445.7925
21 | 2666168.4113 | 1211220.5219 | 2666171.4699 | 1211192.105 | 2666172.6303 | 1211183.4014
22 | 2666168.4113 | 1211220.5219 | 2666139.9811 | 1211203.5157
23 | 2666172.6303 | 1211183.4014 | 2666162.9826 | 1211182.1449
24 | 2666172.6303 | 1211183.4014 | 2666173.7741 | 1211174.831 | 2666174.1036 | 1211172.2923
25 | 2666153.8193 | 1211169.5535 | 2666150.6033 | 1211174.8853 | 2666162.2723 | 1211182.0524 | 2666162.9826 | 1211182.1449
26 | 2666300.3392 | 1211503.0161 | 2666300.0629 | 1211505.3144 | 2666299.3501 | 1211510.0992
27 | 2666426.3161 | 1211416.119 | 2666419.7912 | 1211431.0062

## bus_geodata
| x | y | coords
0 | 2666471.4662 | 1211270.4925
1 | 2666500.1477 | 1211221.221
2 | 2666439.65 | 1211334.4726
3 | 2666370.713 | 1211205.3881
4 | 2666544.8625 | 1211235.4393
5 | 2666447.0536 | 1211356.1128
6 | 2666336.6505 | 1211201.389
7 | 2666540.1056 | 1211242.2349
8 | 2666583.7229 | 1211202.1524
9 | 2666112.0719 | 1211186.8212
10 | 2666054.2712 | 1211151.2036
11 | 2666125.8035 | 1211195.0351
12 | 2666350.67 | 1211186.2561
13 | 2666178.5955 | 1211132.0581
14 | 2666279.1483 | 1211456.3185
15 | 2666413.3105 | 1211445.7925
16 | 2666271.6809 | 1211455.5302
17 | 2666168.4113 | 1211220.5219
18 | 2666172.6303 | 1211183.4014
19 | 2666139.9811 | 1211203.5157
20 | 2666162.9826 | 1211182.1449
21 | 2666174.1036 | 1211172.2923
22 | 2666300.3392 | 1211503.0161
23 | 2666299.3501 | 1211510.0992
24 | 2666419.7912 | 1211431.0062
25 | 2666426.3161 | 1211416.119
26 | 2666041.2547 | 1211145.0515
27 | 2666521.6442 | 1211284.7139
28 | 2666153.8193 | 1211169.5535
29 | 2666332.4515 | 1211211.3374

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98515 | -0.28563 | 0.042216 | 0.01058
1 | 0.98789 | -0.23233 | 0 | 0
2 | 0.98446 | -0.29908 | 0 | 0
3 | 0.99731 | -0.051466 | 0.093325 | 0.023389
4 | 0.98658 | -0.25786 | 0 | 0
5 | 0.98415 | -0.30525 | 0 | 0
6 | 1 | 0 | -0.5052 | -0.1292
7 | 0.98656 | -0.25817 | 0 | 0
8 | 0.98544 | -0.28004 | 0.024124 | 0.006046
9 | 0.97269 | -0.52539 | 0 | 0
10 | 0.97165 | -0.54586 | 0 | 0
11 | 0.97292 | -0.52087 | 0.068326 | 0.017124
12 | 0.99902 | -0.018838 | 0.052341 | 0.013118
13 | 0.98209 | -0.34126 | 0 | 0
14 | 0.98256 | -0.33623 | 0 | 0
15 | 0.98316 | -0.32447 | 0 | 0
16 | 0.98253 | -0.33681 | 0.0043213 | 0.001083
17 | 0.97629 | -0.45449 | 0 | 0
18 | 0.97786 | -0.4238 | 0 | 0
19 | 0.97421 | -0.49546 | 0.051309 | 0.012859
20 | 0.97695 | -0.44166 | 0.021426 | 0.0053698
21 | 0.97868 | -0.40777 | 0.036141 | 0.0090577
22 | 0.98247 | -0.33795 | 0 | 0
23 | 0.98244 | -0.33858 | 0.0048336 | 0.0012114
24 | 0.9833 | -0.3218 | 0.00080651 | 0.00020213
25 | 0.98345 | -0.31888 | 0 | 0
26 | 0.97145 | -0.54999 | 0.015324 | 0.0038405
27 | 0.98647 | -0.25995 | 0.0020732 | 0.00051959
28 | 0.97543 | -0.47156 | 0.079207 | 0.019851
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.052202 | -0.013086 | 0.052335 | 0.01317 | 0.00013292 | 8.4339e-05 | 0.078849 | 0.078849 | 0.078849 | 0.98515 | -0.28563 | 0.98789 | -0.23233 | 21.6618
1 | 0.0099855 | 0.0025052 | -0.0099791 | -0.0025021 | 6.4016e-06 | 3.1423e-06 | 0.015084 | 0.015084 | 0.015084 | 0.98515 | -0.28563 | 0.98446 | -0.29908 | 4.1439
2 | -0.078589 | -0.01977 | 0.079275 | 0.020207 | 0.00068555 | 0.00043706 | 0.1184 | 0.1184 | 0.1184 | 0.98789 | -0.23233 | 0.99731 | -0.051466 | 32.528
3 | 0.026255 | 0.0066004 | -0.026223 | -0.0065806 | 3.1966e-05 | 1.9762e-05 | 0.039553 | 0.039554 | 0.039554 | 0.98789 | -0.23233 | 0.98658 | -0.25786 | 10.8663
4 | 0.0099791 | 0.0025021 | -0.0099762 | -0.0025006 | 2.9349e-06 | 1.4411e-06 | 0.015084 | 0.015084 | 0.015084 | 0.98446 | -0.29908 | 0.98415 | -0.30525 | 4.144
5 | -0.1726 | -0.043597 | 0.17303 | 0.043869 | 0.00042687 | 0.0002723 | 0.25764 | 0.25764 | 0.25764 | 0.99731 | -0.051466 | 1 | 0 | 35.3908
6 | 0.0020734 | 0.00051901 | -0.0020734 | -0.00051909 | 3.0394e-08 | -8.6392e-08 | 0.003127 | 0.003127 | 0.003127 | 0.98658 | -0.25786 | 0.98656 | -0.25817 | 0.85908
7 | 0.024149 | 0.0060616 | -0.024124 | -0.006046 | 2.5515e-05 | 1.5675e-05 | 0.036427 | 0.036427 | 0.036427 | 0.98658 | -0.25786 | 0.98544 | -0.28004 | 10.0073
8 | 0.0099762 | 0.0025006 | -0.0099697 | -0.0024974 | 6.4725e-06 | 3.1792e-06 | 0.015084 | 0.015084 | 0.015084 | 0.98415 | -0.30525 | 0.98345 | -0.31888 | 4.1441
9 | 0.052388 | 0.013148 | -0.052341 | -0.013118 | 4.7017e-05 | 2.982e-05 | 0.07796 | 0.07796 | 0.07796 | 1 | 0 | 0.99902 | -0.018838 | 21.4177
10 | 0.27813 | 0.072185 | -0.27357 | -0.069272 | 0.0045643 | 0.002913 | 0.41475 | 0.41475 | 0.41475 | 1 | 0 | 0.98209 | -0.34126 | 37.9812
11 | 0.0020734 | 0.00051909 | -0.0020732 | -0.00051959 | 1.759e-07 | -4.9987e-07 | 0.003127 | 0.0031273 | 0.0031273 | 0.98656 | -0.25817 | 0.98647 | -0.25995 | 0.85914
12 | 0.015342 | 0.0038509 | -0.015327 | -0.0038422 | 1.4965e-05 | 8.6792e-06 | 0.023472 | 0.023472 | 0.023472 | 0.97269 | -0.52539 | 0.97165 | -0.54586 | 6.4484
13 | -0.015342 | -0.0038509 | 0.015345 | 0.0038528 | 3.3057e-06 | 1.917e-06 | 0.023472 | 0.023472 | 0.023472 | 0.97269 | -0.52539 | 0.97292 | -0.52087 | 6.4483
14 | 0.015327 | 0.0038422 | -0.015324 | -0.0038405 | 3.0161e-06 | 1.7495e-06 | 0.023472 | 0.023472 | 0.023472 | 0.97165 | -0.54586 | 0.97145 | -0.54999 | 6.4484
15 | -0.083671 | -0.020977 | 0.083772 | 0.021042 | 0.00010146 | 6.4726e-05 | 0.12797 | 0.12797 | 0.12797 | 0.97292 | -0.52087 | 0.97421 | -0.49546 | 35.1569
16 | 0.27357 | 0.069272 | -0.2727 | -0.068716 | 0.00087066 | 0.00055569 | 0.41475 | 0.41475 | 0.41475 | 0.98209 | -0.34126 | 0.97868 | -0.40777 | 37.9812
17 | -0.0043214 | -0.001083 | 0.0043238 | 0.0010826 | 2.4206e-06 | -3.6107e-07 | 0.0065444 | 0.0065437 | 0.0065444 | 0.98256 | -0.33623 | 0.98316 | -0.32447 | 1.7979
18 | 0.0043214 | 0.001083 | -0.0043213 | -0.001083 | 1.206e-07 | -1.7918e-08 | 0.0065444 | 0.0065445 | 0.0065445 | 0.98256 | -0.33623 | 0.98253 | -0.33681 | 1.7979
19 | -0.0091607 | -0.0022941 | 0.0091618 | 0.0022946 | 1.1637e-06 | 5.3998e-07 | 0.013864 | 0.013864 | 0.013864 | 0.98316 | -0.32447 | 0.9833 | -0.3218 | 3.8088
20 | 0.0048368 | 0.0012114 | -0.0048337 | -0.0012114 | 3.1055e-06 | 2.9295e-08 | 0.0073203 | 0.007321 | 0.007321 | 0.98316 | -0.32447 | 0.98247 | -0.33795 | 2.0113
21 | -0.13535 | -0.034069 | 0.13554 | 0.034195 | 0.00019888 | 0.00012588 | 0.20634 | 0.20634 | 0.20634 | 0.97629 | -0.45449 | 0.97786 | -0.4238 | 18.8957
22 | 0.13535 | 0.034069 | -0.13508 | -0.033901 | 0.00026447 | 0.00016843 | 0.20634 | 0.20634 | 0.20634 | 0.97629 | -0.45449 | 0.97421 | -0.49546 | 28.3437
23 | 0.10083 | 0.025348 | -0.10075 | -0.025293 | 8.5926e-05 | 5.4871e-05 | 0.15346 | 0.15346 | 0.15346 | 0.97786 | -0.4238 | 0.97695 | -0.44166 | 42.1605
24 | -0.23638 | -0.059543 | 0.23656 | 0.059659 | 0.00018135 | 0.00011564 | 0.35981 | 0.35981 | 0.35981 | 0.97786 | -0.4238 | 0.97868 | -0.40777 | 32.9492
25 | 0.07932 | 0.019923 | -0.079207 | -0.019851 | 0.00011299 | 7.2054e-05 | 0.12083 | 0.12083 | 0.12083 | 0.97695 | -0.44166 | 0.97543 | -0.47156 | 33.1952
26 | 0.0048337 | 0.0012114 | -0.0048336 | -0.0012114 | 1.4376e-07 | 1.4317e-09 | 0.007321 | 0.007321 | 0.007321 | 0.98247 | -0.33795 | 0.98244 | -0.33858 | 2.0113
27 | -0.0099683 | -0.0024968 | 0.0099697 | 0.0024974 | 1.3869e-06 | 6.8142e-07 | 0.015084 | 0.015084 | 0.015084 | 0.9833 | -0.3218 | 0.98345 | -0.31888 | 4.1441

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5052 | 0.1292

## res_load
| p_mw | q_mvar
0 | 0.042216 | 0.01058
1 | 0.093325 | 0.023389
2 | 0.024124 | 0.006046
3 | 0.068326 | 0.017124
4 | 0.052341 | 0.013118
5 | 0.0043213 | 0.001083
6 | 0.051309 | 0.012859
7 | 0.021426 | 0.0053698
8 | 0.036141 | 0.0090577
9 | 0.0048336 | 0.0012114
10 | 0.00080651 | 0.00020213
11 | 0.015324 | 0.0038405
12 | 0.0020732 | 0.00051959
13 | 0.079207 | 0.019851

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1