## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-151_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-151_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-151_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-151_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1061-151_0_5_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1061-151_0_5_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1061-151_0_5_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1061-151_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1061-151_0_5_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1061-151_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1061-151_0_5_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1061-151_0_5_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1061-151_0_5_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1061-151_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1061-151_0_5_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1061-151_0_5_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1061-151_0_5_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1061-151_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1061-151_0_5_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_1061-151_0_5_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_1061-151_0_5_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_1061-151_0_5_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_1061-151_0_5_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1061-151_0_5_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1061-151_0_5_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1061-151_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1061-151_0_5_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1061-151_0_5_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1061-151_0_5_node_25 | 0.4 | n |  | TRUE
29 | bus_MV_215_0_node_52 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-151_0_5_load_0 | 0 | 0.039297 | 0.0098488 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-151_0_5_load_7 | 4 | 0.026847 | 0.0067284 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-151_0_5_load_3 | 5 | 0.031089 | 0.0077917 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-151_0_5_load_18 | 6 | 0.031081 | 0.0077897 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-151_0_5_load_11 | 8 | 0.017855 | 0.004475 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-151_0_5_load_8 | 9 | 0.054931 | 0.013767 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-151_0_5_load_13 | 10 | 0.047999 | 0.01203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-151_0_5_load_19 | 11 | 0.026866 | 0.0067333 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-151_0_5_load_9 | 13 | 0.0081794 | 0.0020499 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-151_0_5_load_16 | 15 | 0.078594 | 0.019698 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-151_0_5_load_20 | 16 | 0.026853 | 0.0067301 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-151_0_5_load_10 | 17 | 0.0081811 | 0.0020504 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-151_0_5_load_32 | 19 | 0.01429 | 0.0035814 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-151_0_5_load_30 | 20 | 0.011791 | 0.0029551 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-151_0_5_load_26 | 21 | 0.0081801 | 0.0020501 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-151_0_5_load_24 | 22 | 0.0279 | 0.0069924 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-151_0_5_load_22 | 23 | 0.011786 | 0.0029539 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-151_0_5_load_31 | 24 | 0.011776 | 0.0029513 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-151_0_5_load_21 | 25 | 0.011079 | 0.0027767 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-151_0_5_load_28 | 26 | 0.0072991 | 0.0018293 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-151_0_5_load_29 | 27 | 0.0032233 | 0.00080783 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-151_0_5_load_25 | 28 | 0.026113 | 0.0065444 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-151_0_5_line_0 |  | 0 | 1 | 0.022993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-151_0_5_line_1 |  | 0 | 2 | 0.038158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-151_0_5_line_2 |  | 1 | 3 | 0.045792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-151_0_5_line_3 |  | 2 | 4 | 0.015001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-151_0_5_line_4 |  | 3 | 10 | 0.054202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-151_0_5_line_5 |  | 4 | 11 | 0.022012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-151_0_5_line_6 |  | 5 | 6 | 0.025557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-151_0_5_line_7 |  | 6 | 12 | 0.03164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1061-151_0_5_line_8 |  | 7 | 8 | 0.019192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-151_0_5_line_9 |  | 7 | 9 | 0.024724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-151_0_5_line_10 |  | 9 | 13 | 5.9582e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-151_0_5_line_11 |  | 11 | 16 | 0.022012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-151_0_5_line_12 |  | 12 | 22 | 0.022025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1061-151_0_5_line_13 |  | 12 | 23 | 0.012452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-151_0_5_line_14 |  | 12 | 14 | 0.012938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-151_0_5_line_15 |  | 13 | 17 | 0.011814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-151_0_5_line_16 |  | 14 | 15 | 0.038744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-151_0_5_line_17 |  | 16 | 25 | 0.00065577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1061-151_0_5_line_18 |  | 17 | 18 | 0.025304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-151_0_5_line_19 |  | 18 | 19 | 0.018046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1061-151_0_5_line_20 |  | 18 | 20 | 0.027386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1061-151_0_5_line_21 |  | 18 | 21 | 0.013941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-151_0_5_line_22 |  | 19 | 27 | 0.022451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1061-151_0_5_line_23 |  | 20 | 24 | 0.012215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1061-151_0_5_line_24 |  | 21 | 28 | 0.0045942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-151_0_5_line_25 |  | 22 | 24 | 0.00091245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1061-151_0_5_line_26 |  | 25 | 26 | 0.01052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1061-151_0_5_line_27 |  | 26 | 27 | 0.0098534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-151_0_5_trafo_18 | 0.63 MVA 20/0.4 kV | 29 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2666597.5517 | 1210738.276 | 2666613.7961 | 1210722.0032
1 | 2666640.754 | 1210694.9982 | 2666613.7961 | 1210722.0032
2 | 2666585.0439 | 1210746.9862 | 2666586.4935 | 1210744.4453 | 2666587.2698 | 1210741.6189 | 2666587.3404 | 1210738.6956 | 2666586.2369 | 1210734.7476 | 2666583.8575 | 1210731.4078 | 2666580.804 | 1210729.2169 | 2666580.0315 | 1210728.9748 | 2666583.7742 | 1210725.2476 | 2666597.5517 | 1210738.276
3 | 2666640.754 | 1210694.9982 | 2666651.5708 | 1210705.3913
4 | 2666585.0439 | 1210746.9862 | 2666591.2929 | 1210752.9374 | 2666624.2964 | 1210784.3646
5 | 2666651.5708 | 1210705.3913 | 2666667.4438 | 1210720.6424
6 | 2666661.2283 | 1210800.886 | 2666643.0048 | 1210782.9677
7 | 2666683.7892 | 1210823.069 | 2666661.2283 | 1210800.886
8 | 2666771.1599 | 1210734.4579 | 2666784.8795 | 1210747.8782
9 | 2666771.1599 | 1210734.4579 | 2666753.7943 | 1210752.0572
10 | 2666753.7525 | 1210752.0997 | 2666753.7943 | 1210752.0572
11 | 2666683.3166 | 1210735.8935 | 2666667.4438 | 1210720.6424
12 | 2666683.7892 | 1210823.069 | 2666699.2477 | 1210807.3797
13 | 2666683.7892 | 1210823.069 | 2666692.4559 | 1210832.0094
14 | 2666683.7892 | 1210823.069 | 2666674.6955 | 1210832.2953
15 | 2666753.7525 | 1210752.0997 | 2666745.4547 | 1210760.5091
16 | 2666674.6955 | 1210832.2953 | 2666666.2171 | 1210840.8725 | 2666647.4882 | 1210859.8786
17 | 2666683.3166 | 1210735.8935 | 2666683.7895 | 1210736.3478
18 | 2666727.6821 | 1210778.521 | 2666745.4547 | 1210760.5091
19 | 2666727.6821 | 1210778.521 | 2666714.6696 | 1210766.0182
20 | 2666727.6821 | 1210778.521 | 2666708.4611 | 1210798.0289
21 | 2666727.6821 | 1210778.521 | 2666737.4424 | 1210788.4759
22 | 2666714.6696 | 1210766.0182 | 2666698.4805 | 1210750.4634
23 | 2666699.8881 | 1210806.7298 | 2666708.4611 | 1210798.0289
24 | 2666737.4424 | 1210788.4759 | 2666740.6588 | 1210791.7563
25 | 2666699.8881 | 1210806.7298 | 2666699.2477 | 1210807.3797
26 | 2666691.3754 | 1210743.6366 | 2666683.7895 | 1210736.3478
27 | 2666691.3754 | 1210743.6366 | 2666698.4805 | 1210750.4634

## bus_geodata
| x | y | coords
0 | 2666613.7961 | 1210722.0032
1 | 2666597.5517 | 1210738.276
2 | 2666640.754 | 1210694.9982
3 | 2666585.0439 | 1210746.9862
4 | 2666651.5708 | 1210705.3913
5 | 2666643.0048 | 1210782.9677
6 | 2666661.2283 | 1210800.886
7 | 2666771.1599 | 1210734.4579
8 | 2666784.8795 | 1210747.8782
9 | 2666753.7943 | 1210752.0572
10 | 2666624.2964 | 1210784.3646
11 | 2666667.4438 | 1210720.6424
12 | 2666683.7892 | 1210823.069
13 | 2666753.7525 | 1210752.0997
14 | 2666674.6955 | 1210832.2953
15 | 2666647.4882 | 1210859.8786
16 | 2666683.3166 | 1210735.8935
17 | 2666745.4547 | 1210760.5091
18 | 2666727.6821 | 1210778.521
19 | 2666714.6696 | 1210766.0182
20 | 2666708.4611 | 1210798.0289
21 | 2666737.4424 | 1210788.4759
22 | 2666699.2477 | 1210807.3797
23 | 2666692.4559 | 1210832.0094
24 | 2666699.8881 | 1210806.7298
25 | 2666683.7895 | 1210736.3478
26 | 2666691.3754 | 1210743.6366
27 | 2666698.4805 | 1210750.4634
28 | 2666740.6588 | 1210791.7563
29 | 2666683.7892 | 1210823.069

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98081 | -0.36955 | 0.039297 | 0.0098488
1 | 0.97978 | -0.38956 | 0 | 0
2 | 0.9839 | -0.30938 | 0 | 0
3 | 0.97774 | -0.42956 | 0 | 0
4 | 0.98511 | -0.28583 | 0.026847 | 0.0067284
5 | 0.99928 | -0.013859 | 0.031089 | 0.0077917
6 | 1 | 0 | -0.50696 | -0.12865
7 | 0.98823 | -0.22592 | 0 | 0
8 | 0.98792 | -0.23204 | 0.017855 | 0.004475
9 | 0.98864 | -0.21804 | 0.054931 | 0.013767
10 | 0.97532 | -0.47711 | 0.047999 | 0.01203
11 | 0.98744 | -0.24081 | 0.026866 | 0.0067333
12 | 0.99659 | -0.06489 | 0 | 0
13 | 0.98864 | -0.21796 | 0.0081794 | 0.0020499
14 | 0.99566 | -0.082752 | 0 | 0
15 | 0.99288 | -0.13644 | 0.078594 | 0.019698
16 | 0.98887 | -0.2131 | 0.026853 | 0.0067301
17 | 0.98952 | -0.20092 | 0.0081811 | 0.0020504
18 | 0.99159 | -0.16085 | 0 | 0
19 | 0.99074 | -0.17716 | 0.01429 | 0.0035814
20 | 0.99365 | -0.12122 | 0.011791 | 0.0029551
21 | 0.99115 | -0.16933 | 0.0081801 | 0.0020501
22 | 0.99468 | -0.10155 | 0.0279 | 0.0069924
23 | 0.99646 | -0.067466 | 0.011786 | 0.0029539
24 | 0.9946 | -0.10296 | 0.011776 | 0.0029513
25 | 0.9889 | -0.21261 | 0.011079 | 0.0027767
26 | 0.98933 | -0.20423 | 0.0072991 | 0.0018293
27 | 0.98976 | -0.19606 | 0.0032233 | 0.00080783
28 | 0.99104 | -0.17146 | 0.026113 | 0.0065444
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.048247 | 0.012187 | -0.0482 | -0.012157 | 4.624e-05 | 2.9304e-05 | 0.073231 | 0.073231 | 0.073231 | 0.98081 | -0.36955 | 0.97978 | -0.38956 | 20.1184
1 | -0.087544 | -0.022035 | 0.087796 | 0.022196 | 0.00025254 | 0.00016114 | 0.13285 | 0.13285 | 0.13285 | 0.98081 | -0.36955 | 0.9839 | -0.30938 | 36.4971
2 | 0.0482 | 0.012157 | -0.048108 | -0.012099 | 9.209e-05 | 5.8362e-05 | 0.073231 | 0.073231 | 0.073231 | 0.97978 | -0.38956 | 0.97774 | -0.42956 | 20.1184
3 | -0.087796 | -0.022196 | 0.087896 | 0.02226 | 9.9279e-05 | 6.3348e-05 | 0.13285 | 0.13285 | 0.13285 | 0.9839 | -0.30938 | 0.98511 | -0.28583 | 36.4971
4 | 0.048108 | 0.012099 | -0.047999 | -0.01203 | 0.000109 | 6.9084e-05 | 0.073231 | 0.073231 | 0.073231 | 0.97774 | -0.42956 | 0.97532 | -0.47711 | 20.1185
5 | -0.11474 | -0.028988 | 0.11499 | 0.029147 | 0.0002482 | 0.00015857 | 0.1734 | 0.1734 | 0.1734 | 0.98511 | -0.28583 | 0.98744 | -0.24081 | 47.6377
6 | -0.031089 | -0.0077917 | 0.03111 | 0.0078045 | 2.054e-05 | 1.2811e-05 | 0.046295 | 0.046295 | 0.046295 | 0.99928 | -0.013859 | 1 | 0 | 12.7183
7 | 0.4742 | 0.12084 | -0.47272 | -0.1199 | 0.0014798 | 0.00094544 | 0.70632 | 0.70632 | 0.70632 | 1 | 0 | 0.99659 | -0.06489 | 48.5112
8 | 0.017861 | 0.004478 | -0.017855 | -0.004475 | 5.2055e-06 | 3.0857e-06 | 0.026894 | 0.026894 | 0.026894 | 0.98823 | -0.22592 | 0.98792 | -0.23204 | 7.3884
9 | -0.017861 | -0.004478 | 0.017867 | 0.004482 | 6.706e-06 | 3.9749e-06 | 0.026894 | 0.026894 | 0.026894 | 0.98823 | -0.22592 | 0.98864 | -0.21804 | 7.3884
10 | -0.072798 | -0.018249 | 0.072799 | 0.018249 | 2.6825e-07 | 1.7092e-07 | 0.10957 | 0.10957 | 0.10957 | 0.98864 | -0.21804 | 0.98864 | -0.21796 | 30.1021
11 | -0.14186 | -0.03588 | 0.14205 | 0.036 | 0.00018881 | 0.00012028 | 0.21389 | 0.21389 | 0.21389 | 0.98744 | -0.24081 | 0.98887 | -0.2131 | 29.3801
12 | 0.38207 | 0.097072 | -0.3814 | -0.096642 | 0.00067308 | 0.00042963 | 0.57094 | 0.57094 | 0.57094 | 0.99659 | -0.06489 | 0.99468 | -0.10155 | 39.2126
13 | 0.011788 | 0.0029547 | -0.011786 | -0.0029539 | 1.4465e-06 | 7.6351e-07 | 0.0176 | 0.0176 | 0.0176 | 0.99659 | -0.06489 | 0.99646 | -0.067466 | 4.8353
14 | 0.078863 | 0.019869 | -0.078796 | -0.019826 | 6.7313e-05 | 4.2912e-05 | 0.11779 | 0.11779 | 0.11779 | 0.99659 | -0.06489 | 0.99566 | -0.082752 | 32.3593
15 | -0.080978 | -0.020299 | 0.081044 | 0.020341 | 6.5813e-05 | 4.1969e-05 | 0.12188 | 0.12188 | 0.12188 | 0.98864 | -0.21796 | 0.98952 | -0.20092 | 33.4842
16 | 0.078796 | 0.019826 | -0.078594 | -0.019698 | 0.00020157 | 0.00012851 | 0.11779 | 0.11779 | 0.11779 | 0.99566 | -0.082752 | 0.99288 | -0.13644 | 32.3594
17 | -0.1689 | -0.04273 | 0.1689 | 0.042733 | 3.9755e-06 | 2.5107e-06 | 0.25429 | 0.25429 | 0.25429 | 0.98887 | -0.2131 | 0.9889 | -0.21261 | 17.4653
18 | -0.089225 | -0.022392 | 0.089396 | 0.022501 | 0.00017086 | 0.00010902 | 0.13419 | 0.13419 | 0.13419 | 0.98952 | -0.20092 | 0.99159 | -0.16085 | 36.8641
19 | 0.20527 | 0.052032 | -0.20511 | -0.05193 | 0.00016075 | 0.00010195 | 0.30825 | 0.30825 | 0.30825 | 0.99159 | -0.16085 | 0.99074 | -0.17716 | 21.1711
20 | -0.32898 | -0.083138 | 0.32961 | 0.083537 | 0.00062636 | 0.00039945 | 0.49392 | 0.49392 | 0.49392 | 0.99159 | -0.16085 | 0.99365 | -0.12122 | 33.9233
21 | 0.034309 | 0.0086049 | -0.034295 | -0.0085962 | 1.386e-05 | 8.6904e-06 | 0.051488 | 0.051488 | 0.051488 | 0.99159 | -0.16085 | 0.99115 | -0.16933 | 14.1451
22 | 0.19082 | 0.048349 | -0.19065 | -0.048239 | 0.00017311 | 0.00010964 | 0.28679 | 0.28679 | 0.28679 | 0.99074 | -0.17716 | 0.98976 | -0.19606 | 19.6971
23 | -0.3414 | -0.086492 | 0.3417 | 0.086683 | 0.0002997 | 0.00019117 | 0.51158 | 0.51158 | 0.51158 | 0.99365 | -0.12122 | 0.9946 | -0.10296 | 35.136
24 | 0.026115 | 0.0065461 | -0.026113 | -0.0065444 | 2.6483e-06 | 1.6357e-06 | 0.039207 | 0.039207 | 0.039207 | 0.99115 | -0.16933 | 0.99104 | -0.17146 | 10.7712
25 | 0.3535 | 0.08965 | -0.35347 | -0.089635 | 2.3956e-05 | 1.5285e-05 | 0.5292 | 0.5292 | 0.5292 | 0.99468 | -0.10155 | 0.9946 | -0.10296 | 36.346
26 | -0.17998 | -0.04551 | 0.18005 | 0.045555 | 7.2413e-05 | 4.5804e-05 | 0.27097 | 0.27097 | 0.27097 | 0.9889 | -0.21261 | 0.98933 | -0.20423 | 18.6103
27 | -0.18735 | -0.047385 | 0.18743 | 0.047431 | 7.3431e-05 | 4.649e-05 | 0.28194 | 0.28194 | 0.28194 | 0.98933 | -0.20423 | 0.98976 | -0.19606 | 19.3643

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53804 | 0.13644

## res_load
| p_mw | q_mvar
0 | 0.039297 | 0.0098488
1 | 0.026847 | 0.0067284
2 | 0.031089 | 0.0077917
3 | 0.031081 | 0.0077897
4 | 0.017855 | 0.004475
5 | 0.054931 | 0.013767
6 | 0.047999 | 0.01203
7 | 0.026866 | 0.0067333
8 | 0.0081794 | 0.0020499
9 | 0.078594 | 0.019698
10 | 0.026853 | 0.0067301
11 | 0.0081811 | 0.0020504
12 | 0.01429 | 0.0035814
13 | 0.011791 | 0.0029551
14 | 0.0081801 | 0.0020501
15 | 0.0279 | 0.0069924
16 | 0.011786 | 0.0029539
17 | 0.011776 | 0.0029513
18 | 0.011079 | 0.0027767
19 | 0.0072991 | 0.0018293
20 | 0.0032233 | 0.00080783
21 | 0.026113 | 0.0065444

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1