## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-158_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-158_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-158_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-158_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-158_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-158_0_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1061-158_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1061-158_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1061-158_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_1061-158_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1061-158_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1061-158_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1061-158_0_4_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_1061-158_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_1061-158_0_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1061-158_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1061-158_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1061-158_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1061-158_0_4_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1061-158_0_4_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1061-158_0_4_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_1061-158_0_4_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1061-158_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_1061-158_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1061-158_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1061-158_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1061-158_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1061-158_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1061-158_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1061-158_0_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1061-158_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_MV_217_0_node_65 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-158_0_4_load_0 | 0 | 0.038168 | 0.0095657 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-158_0_4_load_1 | 1 | 0.020292 | 0.0050857 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-158_0_4_load_3 | 3 | 0.021572 | 0.0054065 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-158_0_4_load_13 | 5 | 0.0057596 | 0.0014435 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-158_0_4_load_12 | 6 | 0.043593 | 0.010926 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-158_0_4_load_14 | 8 | 0.0075049 | 0.0018809 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-158_0_4_load_25 | 12 | 0.057894 | 0.01451 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-158_0_4_load_26 | 13 | 0.0095976 | 0.0024054 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-158_0_4_load_19 | 15 | 0.015109 | 0.0037866 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-158_0_4_load_15 | 16 | 0.034769 | 0.0087138 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-158_0_4_load_31 | 19 | 0.0091328 | 0.0022889 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-158_0_4_load_27 | 21 | 0.007443 | 0.0018654 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-158_0_4_load_28 | 22 | 0.0090177 | 0.0022601 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-158_0_4_load_16 | 23 | 0.0266 | 0.0066665 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-158_0_4_load_24 | 24 | 0.017554 | 0.0043995 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-158_0_4_load_22 | 25 | 0.027788 | 0.0069643 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-158_0_4_load_20 | 26 | 0.02512 | 0.0062956 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-158_0_4_load_21 | 27 | 0.010021 | 0.0025114 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-158_0_4_load_32 | 29 | 0.014714 | 0.0036876 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-158_0_4_load_29 | 30 | 0.0072507 | 0.0018172 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-158_0_4_line_0 |  | 0 | 1 | 0.029082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-158_0_4_line_1 |  | 0 | 2 | 0.0088451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-158_0_4_line_2 |  | 1 | 3 | 0.023519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-158_0_4_line_3 |  | 2 | 4 | 0.020391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-158_0_4_line_4 |  | 4 | 5 | 0.017857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-158_0_4_line_5 |  | 4 | 6 | 0.0098766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-158_0_4_line_6 |  | 5 | 7 | 0.01052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-158_0_4_line_7 |  | 7 | 8 | 0.039928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-158_0_4_line_8 |  | 8 | 9 | 0.02046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-158_0_4_line_9 |  | 9 | 10 | 0.027485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1061-158_0_4_line_10 |  | 9 | 11 | 0.018654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-158_0_4_line_11 |  | 10 | 12 | 0.021517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-158_0_4_line_12 |  | 11 | 13 | 0.035794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-158_0_4_line_13 |  | 12 | 17 | 0.033419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1061-158_0_4_line_14 |  | 14 | 15 | 0.0093432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-158_0_4_line_15 |  | 14 | 16 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-158_0_4_line_16 |  | 16 | 23 | 0.011691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-158_0_4_line_17 |  | 17 | 24 | 0.021205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-158_0_4_line_18 |  | 17 | 23 | 0.008488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-158_0_4_line_19 |  | 18 | 19 | 0.072421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-158_0_4_line_20 |  | 18 | 20 | 0.06418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-158_0_4_line_21 |  | 19 | 30 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-158_0_4_line_22 |  | 20 | 29 | 0.06336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-158_0_4_line_23 |  | 21 | 22 | 0.015438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-158_0_4_line_24 |  | 22 | 30 | 0.018657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-158_0_4_line_25 |  | 24 | 25 | 0.019462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-158_0_4_line_26 |  | 25 | 26 | 0.01745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-158_0_4_line_27 |  | 26 | 27 | 0.012014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-158_0_4_line_28 |  | 27 | 28 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-158_0_4_line_29 |  | 28 | 29 | 0.0010742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-158_0_4_trafo_18 | 0.63 MVA 20/0.4 kV | 31 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2665399.1171 | 1211851.5044 | 2665393.7768 | 1211854.718 | 2665385.2278 | 1211853.4124 | 2665372.6924 | 1211860.0864
1 | 2665406.6958 | 1211846.9437 | 2665399.1171 | 1211851.5044
2 | 2665372.6924 | 1211860.0864 | 2665351.9328 | 1211871.1391
3 | 2665406.6958 | 1211846.9437 | 2665405.3481 | 1211867.2859
4 | 2665405.3481 | 1211867.2859 | 2665422.4184 | 1211862.044
5 | 2665405.3481 | 1211867.2859 | 2665405.5527 | 1211877.1605
6 | 2665432.4745 | 1211858.956 | 2665422.4184 | 1211862.044
7 | 2665432.4745 | 1211858.956 | 2665422.3182 | 1211820.3411
8 | 2665409.886 | 1211804.7861 | 2665414.446 | 1211808.1715 | 2665417.7166 | 1211811.3315 | 2665420.4348 | 1211814.9858 | 2665422.219 | 1211819.9639 | 2665422.3182 | 1211820.3411
9 | 2665386.7175 | 1211811.1027 | 2665392.9615 | 1211807.8135 | 2665394.9452 | 1211811.2263 | 2665398.4482 | 1211809.1411 | 2665406.7298 | 1211805.0516 | 2665409.886 | 1211804.7861
10 | 2665407.3342 | 1211789.4264 | 2665408.9811 | 1211792.3796 | 2665413.1181 | 1211794.8376 | 2665412.6071 | 1211796.3996 | 2665411.4354 | 1211800.0001 | 2665410.2715 | 1211803.5895 | 2665409.886 | 1211804.7861
11 | 2665386.7175 | 1211811.1027 | 2665368.0794 | 1211821.8546
12 | 2665407.3342 | 1211789.4264 | 2665406.054 | 1211784.9096 | 2665403.0104 | 1211779.0615 | 2665391.7045 | 1211757.3191
13 | 2665339.1316 | 1211838.5539 | 2665368.0794 | 1211821.8546
14 | 2665350.4182 | 1211804.3008 | 2665346.8199 | 1211795.6783
15 | 2665350.4182 | 1211804.3008 | 2665345.2714 | 1211814.951 | 2665342.7105 | 1211820.0421
16 | 2665337.4571 | 1211830.4862 | 2665342.7105 | 1211820.0421
17 | 2665339.1316 | 1211838.5539 | 2665320.7994 | 1211849.2121
18 | 2665339.1316 | 1211838.5539 | 2665338.2673 | 1211836.9879 | 2665337.283 | 1211834.5868 | 2665337.4571 | 1211830.4862
19 | 2665227.7781 | 1211970.428 | 2665238.7228 | 1211967.3569 | 2665248.3569 | 1211963.2263 | 2665270.28 | 1211951.9258 | 2665294.5604 | 1211942.8914
20 | 2665227.7781 | 1211970.428 | 2665224.8262 | 1211964.5254 | 2665207.8408 | 1211918.2668 | 2665204.482 | 1211910.6588
21 | 2665313.847 | 1211935.7151 | 2665294.5604 | 1211942.8914
22 | 2665204.482 | 1211910.6588 | 2665226.5773 | 1211903.0734 | 2665250.9786 | 1211889.5985 | 2665261.5415 | 1211883.6476
23 | 2665346.5156 | 1211928.846 | 2665346.5156 | 1211928.846 | 2665338.7719 | 1211927.5493 | 2665331.4944 | 1211929.6931
24 | 2665331.4944 | 1211929.6931 | 2665324.4714 | 1211931.7619 | 2665313.847 | 1211935.7151
25 | 2665303.9747 | 1211858.9939 | 2665320.7994 | 1211849.2121
26 | 2665303.9747 | 1211858.9939 | 2665288.8894 | 1211867.7645
27 | 2665278.503 | 1211873.8031 | 2665288.8894 | 1211867.7645
28 | 2665262.4774 | 1211883.1203 | 2665278.503 | 1211873.8031
29 | 2665262.4774 | 1211883.1203 | 2665261.5415 | 1211883.6476

## bus_geodata
| x | y | coords
0 | 2665399.1171 | 1211851.5044
1 | 2665372.6924 | 1211860.0864
2 | 2665406.6958 | 1211846.9437
3 | 2665351.9328 | 1211871.1391
4 | 2665405.3481 | 1211867.2859
5 | 2665422.4184 | 1211862.044
6 | 2665405.5527 | 1211877.1605
7 | 2665432.4745 | 1211858.956
8 | 2665422.3182 | 1211820.3411
9 | 2665409.886 | 1211804.7861
10 | 2665386.7175 | 1211811.1027
11 | 2665407.3342 | 1211789.4264
12 | 2665368.0794 | 1211821.8546
13 | 2665391.7045 | 1211757.3191
14 | 2665350.4182 | 1211804.3008
15 | 2665346.8199 | 1211795.6783
16 | 2665342.7105 | 1211820.0421
17 | 2665339.1316 | 1211838.5539
18 | 2665227.7781 | 1211970.428
19 | 2665294.5604 | 1211942.8914
20 | 2665204.482 | 1211910.6588
21 | 2665346.5156 | 1211928.846
22 | 2665331.4944 | 1211929.6931
23 | 2665337.4571 | 1211830.4862
24 | 2665320.7994 | 1211849.2121
25 | 2665303.9747 | 1211858.9939
26 | 2665288.8894 | 1211867.7645
27 | 2665278.503 | 1211873.8031
28 | 2665262.4774 | 1211883.1203
29 | 2665261.5415 | 1211883.6476
30 | 2665313.847 | 1211935.7151
31 | 2665350.4182 | 1211804.3008

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98071 | -0.37109 | 0.038168 | 0.0095657
1 | 0.97958 | -0.39318 | 0.020292 | 0.0050857
2 | 0.98136 | -0.35827 | 0 | 0
3 | 0.97911 | -0.4024 | 0.021572 | 0.0054065
4 | 0.98287 | -0.32878 | 0 | 0
5 | 0.98491 | -0.28903 | 0.0057596 | 0.0014435
6 | 0.98248 | -0.33655 | 0.043593 | 0.010926
7 | 0.98617 | -0.26461 | 0 | 0
8 | 0.99095 | -0.17246 | 0.0075049 | 0.0018809
9 | 0.99354 | -0.12288 | 0 | 0
10 | 0.9954 | -0.087399 | 0 | 0
11 | 0.99338 | -0.12604 | 0 | 0
12 | 0.99686 | -0.059715 | 0.057894 | 0.01451
13 | 0.99306 | -0.13211 | 0.0095976 | 0.0024054
14 | 0.99864 | -0.026129 | 0 | 0
15 | 0.99851 | -0.028597 | 0.015109 | 0.0037866
16 | 0.99888 | -0.021502 | 0.034769 | 0.0087138
17 | 1 | 0 | -0.41406 | -0.10472
18 | 0.98889 | -0.21368 | 0 | 0
19 | 0.9867 | -0.25617 | 0.0091328 | 0.0022889
20 | 0.99083 | -0.17617 | 0 | 0
21 | 0.98587 | -0.27247 | 0.007443 | 0.0018654
22 | 0.98597 | -0.27041 | 0.0090177 | 0.0022601
23 | 0.99941 | -0.011321 | 0.0266 | 0.0066665
24 | 0.99752 | -0.047445 | 0.017554 | 0.0043995
25 | 0.99555 | -0.085187 | 0.027788 | 0.0069643
26 | 0.99423 | -0.1106 | 0.02512 | 0.0062956
27 | 0.9936 | -0.12281 | 0.010021 | 0.0025114
28 | 0.99279 | -0.13839 | 0 | 0
29 | 0.99274 | -0.13929 | 0.014714 | 0.0036876
30 | 0.98625 | -0.26491 | 0.0072507 | 0.0018172
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.041918 | 0.010526 | -0.041874 | -0.010498 | 4.4127e-05 | 2.7874e-05 | 0.063609 | 0.06361 | 0.06361 | 0.98071 | -0.37109 | 0.97958 | -0.39318 | 17.4751
1 | -0.080086 | -0.020092 | 0.080135 | 0.020123 | 4.8982e-05 | 3.1237e-05 | 0.12152 | 0.12152 | 0.12152 | 0.98071 | -0.37109 | 0.98136 | -0.35827 | 33.3848
2 | 0.021582 | 0.0054123 | -0.021572 | -0.0054065 | 9.4796e-06 | 5.771e-06 | 0.032785 | 0.032785 | 0.032785 | 0.97958 | -0.39318 | 0.97911 | -0.4024 | 9.0068
3 | -0.080135 | -0.020123 | 0.080248 | 0.020195 | 0.00011292 | 7.2011e-05 | 0.12152 | 0.12152 | 0.12152 | 0.98136 | -0.35827 | 0.98287 | -0.32878 | 33.3848
4 | -0.12386 | -0.031131 | 0.12409 | 0.031281 | 0.00023553 | 0.00015051 | 0.18755 | 0.18755 | 0.18755 | 0.98287 | -0.32878 | 0.98491 | -0.28903 | 51.5235
5 | 0.04361 | 0.010936 | -0.043593 | -0.010926 | 1.6146e-05 | 1.0208e-05 | 0.066025 | 0.066025 | 0.066025 | 0.98287 | -0.32878 | 0.98248 | -0.33655 | 18.1387
6 | -0.12985 | -0.032725 | 0.13 | 0.032822 | 0.00015193 | 9.71e-05 | 0.19625 | 0.19625 | 0.19625 | 0.98491 | -0.28903 | 0.98617 | -0.26461 | 53.914
7 | -0.13 | -0.032822 | 0.13058 | 0.03319 | 0.00057665 | 0.00036855 | 0.19625 | 0.19625 | 0.19625 | 0.98617 | -0.26461 | 0.99095 | -0.17246 | 53.914
8 | -0.13809 | -0.035071 | 0.13842 | 0.035282 | 0.0003304 | 0.00021119 | 0.20752 | 0.20752 | 0.20752 | 0.99095 | -0.17246 | 0.99354 | -0.12288 | 57.0099
9 | -0.14802 | -0.03769 | 0.14827 | 0.037851 | 0.00025375 | 0.00016168 | 0.2219 | 0.2219 | 0.2219 | 0.99354 | -0.12288 | 0.9954 | -0.087399 | 30.4803
10 | 0.0096018 | 0.0024074 | -0.0096004 | -0.0024067 | 1.4467e-06 | 6.8434e-07 | 0.014381 | 0.014381 | 0.014381 | 0.99354 | -0.12288 | 0.99338 | -0.12604 | 3.9508
11 | -0.14827 | -0.037851 | 0.14847 | 0.037978 | 0.00019865 | 0.00012657 | 0.2219 | 0.2219 | 0.2219 | 0.9954 | -0.087399 | 0.99686 | -0.059715 | 30.4803
12 | 0.0096004 | 0.0024067 | -0.0095976 | -0.0024054 | 2.776e-06 | 1.3134e-06 | 0.014381 | 0.014381 | 0.014381 | 0.99338 | -0.12604 | 0.99306 | -0.13211 | 3.9509
13 | -0.20636 | -0.052488 | 0.20696 | 0.052868 | 0.00059564 | 0.00038034 | 0.30831 | 0.30831 | 0.30831 | 0.99686 | -0.059715 | 1 | 0 | 42.3508
14 | 0.015111 | 0.0037876 | -0.015109 | -0.0037866 | 1.7762e-06 | 1.0145e-06 | 0.022516 | 0.022516 | 0.022516 | 0.99864 | -0.026129 | 0.99851 | -0.028597 | 6.1856
15 | -0.015111 | -0.0037876 | 0.015114 | 0.0037895 | 3.3321e-06 | 1.9032e-06 | 0.022516 | 0.022515 | 0.022516 | 0.99864 | -0.026129 | 0.99888 | -0.021502 | 6.1856
16 | -0.049882 | -0.012503 | 0.049907 | 0.012519 | 2.4208e-05 | 1.534e-05 | 0.07431 | 0.07431 | 0.07431 | 0.99888 | -0.021502 | 0.99941 | -0.011321 | 20.4147
17 | 0.12891 | 0.032639 | -0.12861 | -0.032452 | 0.00029293 | 0.0001872 | 0.19193 | 0.19193 | 0.19193 | 1 | 0 | 0.99752 | -0.047445 | 52.7282
18 | 0.076548 | 0.019212 | -0.076506 | -0.019185 | 4.1304e-05 | 2.6323e-05 | 0.11391 | 0.11391 | 0.11391 | 1 | 0 | 0.99941 | -0.011321 | 31.295
19 | 0.032926 | 0.0082822 | -0.032859 | -0.0082404 | 6.6693e-05 | 4.1756e-05 | 0.049555 | 0.049556 | 0.049556 | 0.98889 | -0.21368 | 0.9867 | -0.25617 | 13.6142
20 | -0.032926 | -0.0082822 | 0.032985 | 0.0083192 | 5.9103e-05 | 3.7001e-05 | 0.049555 | 0.049555 | 0.049555 | 0.98889 | -0.21368 | 0.99083 | -0.17617 | 13.6141
21 | 0.023726 | 0.0059515 | -0.023717 | -0.0059454 | 9.8809e-06 | 6.0611e-06 | 0.035783 | 0.035783 | 0.035783 | 0.9867 | -0.25617 | 0.98625 | -0.26491 | 9.8305
22 | -0.032985 | -0.0083192 | 0.033043 | 0.0083557 | 5.8347e-05 | 3.6525e-05 | 0.049555 | 0.049555 | 0.049555 | 0.99083 | -0.17617 | 0.99274 | -0.13929 | 13.6141
23 | -0.007443 | -0.0018654 | 0.0074437 | 0.0018657 | 7.3063e-07 | 2.7073e-07 | 0.011234 | 0.011234 | 0.011234 | 0.98587 | -0.27247 | 0.98597 | -0.27041 | 3.0863
24 | -0.016461 | -0.0041257 | 0.016466 | 0.0041282 | 4.3182e-06 | 2.5256e-06 | 0.024843 | 0.024843 | 0.024843 | 0.98597 | -0.27041 | 0.98625 | -0.26491 | 6.8251
25 | 0.11106 | 0.028052 | -0.11086 | -0.027924 | 0.00020049 | 0.00012806 | 0.16574 | 0.16574 | 0.16574 | 0.99752 | -0.047445 | 0.99555 | -0.085187 | 45.5343
26 | 0.08307 | 0.02096 | -0.082969 | -0.020896 | 0.00010096 | 6.4387e-05 | 0.12421 | 0.12421 | 0.12421 | 0.99555 | -0.085187 | 0.99423 | -0.1106 | 34.1241
27 | 0.057849 | 0.0146 | -0.057815 | -0.014579 | 3.3801e-05 | 2.1477e-05 | 0.086616 | 0.086616 | 0.086616 | 0.99423 | -0.1106 | 0.9936 | -0.12281 | 23.7956
28 | 0.047795 | 0.012067 | -0.047759 | -0.012045 | 3.5646e-05 | 2.2574e-05 | 0.071609 | 0.071609 | 0.071609 | 0.9936 | -0.12281 | 0.99279 | -0.13839 | 19.6728
29 | 0.047759 | 0.012045 | -0.047757 | -0.012043 | 2.0657e-06 | 1.3082e-06 | 0.071609 | 0.071609 | 0.071609 | 0.99279 | -0.13839 | 0.99274 | -0.13929 | 19.6728

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41406 | 0.10472

## res_load
| p_mw | q_mvar
0 | 0.038168 | 0.0095657
1 | 0.020292 | 0.0050857
2 | 0.021572 | 0.0054065
3 | 0.0057596 | 0.0014435
4 | 0.043593 | 0.010926
5 | 0.0075049 | 0.0018809
6 | 0.057894 | 0.01451
7 | 0.0095976 | 0.0024054
8 | 0.015109 | 0.0037866
9 | 0.034769 | 0.0087138
10 | 0.0091328 | 0.0022889
11 | 0.007443 | 0.0018654
12 | 0.0090177 | 0.0022601
13 | 0.0266 | 0.0066665
14 | 0.017554 | 0.0043995
15 | 0.027788 | 0.0069643
16 | 0.02512 | 0.0062956
17 | 0.010021 | 0.0025114
18 | 0.014714 | 0.0036876
19 | 0.0072507 | 0.0018172

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1