## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-169_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-169_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-169_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-169_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-169_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-169_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1061-169_0_6_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_1061-169_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1061-169_0_6_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_1061-169_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1061-169_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1061-169_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1061-169_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1061-169_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1061-169_0_6_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_1061-169_0_6_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1061-169_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1061-169_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1061-169_0_6_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1061-169_0_6_node_42 | 0.4 | n |  | TRUE
20 | bus_LV_1061-169_0_6_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1061-169_0_6_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1061-169_0_6_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1061-169_0_6_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1061-169_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1061-169_0_6_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1061-169_0_6_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1061-169_0_6_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1061-169_0_6_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1061-169_0_6_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1061-169_0_6_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1061-169_0_6_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_1061-169_0_6_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_1061-169_0_6_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_1061-169_0_6_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1061-169_0_6_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1061-169_0_6_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_1061-169_0_6_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1061-169_0_6_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1061-169_0_6_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_1061-169_0_6_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1061-169_0_6_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1061-169_0_6_node_50 | 0.4 | n |  | TRUE
43 | bus_LV_1061-169_0_6_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_1061-169_0_6_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1061-169_0_6_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_1061-169_0_6_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_1061-169_0_6_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_1061-169_0_6_node_48 | 0.4 | n |  | TRUE
49 | bus_MV_213_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-169_0_6_load_0 | 0 | 0.0073086 | 0.0018317 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-169_0_6_load_1 | 1 | 0.0077647 | 0.001946 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-169_0_6_load_2 | 2 | 0.0054423 | 0.001364 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-169_0_6_load_3 | 3 | 0.0080216 | 0.0020104 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-169_0_6_load_4 | 4 | 0.0070282 | 0.0017614 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-169_0_6_load_8 | 5 | 0.0077183 | 0.0019344 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-169_0_6_load_25 | 6 | 0.0059365 | 0.0014878 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-169_0_6_load_26 | 8 | 0.0068414 | 0.0017146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-169_0_6_load_5 | 9 | 0.0064341 | 0.0016125 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-169_0_6_load_9 | 11 | 0.058981 | 0.014782 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-169_0_6_load_10 | 12 | 0.052703 | 0.013209 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-169_0_6_load_11 | 13 | 0.0086297 | 0.0021628 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-169_0_6_load_35 | 14 | 0.052721 | 0.013213 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-169_0_6_load_36 | 15 | 0.019306 | 0.0048386 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-169_0_6_load_12 | 16 | 0.017859 | 0.0044759 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-169_0_6_load_13 | 17 | 0.024197 | 0.0060642 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-169_0_6_load_15 | 18 | 0.0073564 | 0.0018437 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-169_0_6_load_42 | 19 | 0.029373 | 0.0073615 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-169_0_6_load_17 | 21 | 0.0021022 | 0.00052685 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-169_0_6_load_18 | 22 | 0.010689 | 0.0026789 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-169_0_6_load_19 | 23 | 0.0044023 | 0.0011033 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-169_0_6_load_20 | 24 | 0.019461 | 0.0048773 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-169_0_6_load_21 | 25 | 0.0043645 | 0.0010938 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-169_0_6_load_22 | 26 | 0.0029215 | 0.00073221 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-169_0_6_load_27 | 27 | 0.0058254 | 0.00146 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-169_0_6_load_23 | 28 | 0.002632 | 0.00065965 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-169_0_6_load_24 | 30 | 0.0020264 | 0.00050786 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-169_0_6_load_41 | 32 | 0.020378 | 0.0051071 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-169_0_6_load_38 | 33 | 0.017568 | 0.0044029 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-169_0_6_load_30 | 35 | 0.010611 | 0.0026595 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-169_0_6_load_32 | 36 | 0.015355 | 0.0038482 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-169_0_6_load_31 | 37 | 0.011369 | 0.0028494 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-169_0_6_load_33 | 38 | 0.0044056 | 0.0011042 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1061-169_0_6_load_47 | 39 | 0.013924 | 0.0034896 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1061-169_0_6_load_53 | 43 | 0.034098 | 0.0085459 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1061-169_0_6_load_43 | 44 | 0.012807 | 0.0032096 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1061-169_0_6_load_44 | 45 | 0.015067 | 0.0037762 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1061-169_0_6_load_46 | 46 | 0.015067 | 0.003776 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1061-169_0_6_load_48 | 48 | 0.0098675 | 0.002473 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-169_0_6_line_0 |  | 0 | 1 | 0.018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1061-169_0_6_line_1 |  | 0 | 2 | 0.009059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1061-169_0_6_line_2 |  | 1 | 3 | 0.0012721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1061-169_0_6_line_3 |  | 2 | 4 | 0.010616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1061-169_0_6_line_4 |  | 3 | 5 | 0.013852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1061-169_0_6_line_5 |  | 4 | 6 | 0.00033184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1061-169_0_6_line_6 |  | 5 | 7 | 0.012172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1061-169_0_6_line_7 |  | 6 | 8 | 0.023751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1061-169_0_6_line_8 |  | 7 | 11 | 0.015712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-169_0_6_line_9 |  | 7 | 9 | 0.01521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1061-169_0_6_line_10 |  | 8 | 31 | 0.01398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1061-169_0_6_line_11 |  | 9 | 10 | 0.015466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-169_0_6_line_12 |  | 10 | 12 | 0.02087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1061-169_0_6_line_13 |  | 10 | 13 | 0.041789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-169_0_6_line_14 |  | 12 | 14 | 0.031852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-169_0_6_line_15 |  | 14 | 15 | 0.025069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-169_0_6_line_16 |  | 15 | 41 | 0.037941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-169_0_6_line_17 |  | 16 | 17 | 0.032236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-169_0_6_line_18 |  | 17 | 18 | 0.0058517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-169_0_6_line_19 |  | 18 | 19 | 0.030173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-169_0_6_line_20 |  | 19 | 20 | 0.018342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-169_0_6_line_21 |  | 20 | 39 | 0.014824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1061-169_0_6_line_22 |  | 20 | 38 | 0.029171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1061-169_0_6_line_23 |  | 21 | 22 | 0.014174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-169_0_6_line_24 |  | 21 | 23 | 0.011335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1061-169_0_6_line_25 |  | 22 | 24 | 0.02372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-169_0_6_line_26 |  | 23 | 25 | 0.01535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1061-169_0_6_line_27 |  | 24 | 26 | 0.010305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-169_0_6_line_28 |  | 25 | 27 | 0.0087227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1061-169_0_6_line_29 |  | 26 | 28 | 0.030251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-169_0_6_line_30 |  | 27 | 29 | 0.0564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1061-169_0_6_line_31 |  | 28 | 30 | 0.0022967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-169_0_6_line_32 |  | 29 | 34 | 0.017247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1061-169_0_6_line_33 |  | 29 | 35 | 0.013601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1061-169_0_6_line_34 |  | 31 | 32 | 0.032444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1061-169_0_6_line_35 |  | 31 | 33 | 0.013276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1061-169_0_6_line_36 |  | 32 | 40 | 0.031196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1061-169_0_6_line_37 |  | 34 | 36 | 0.027896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1061-169_0_6_line_38 |  | 36 | 37 | 0.024349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1061-169_0_6_line_39 |  | 37 | 38 | 0.0071574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1061-169_0_6_line_40 |  | 39 | 40 | 0.028121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1061-169_0_6_line_41 |  | 40 | 44 | 0.0067496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1061-169_0_6_line_42 |  | 41 | 42 | 0.014157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1061-169_0_6_line_43 |  | 42 | 43 | 0.015044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1061-169_0_6_line_44 |  | 44 | 45 | 0.026526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1061-169_0_6_line_45 |  | 45 | 46 | 0.017255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1061-169_0_6_line_46 |  | 46 | 47 | 0.016107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1061-169_0_6_line_47 |  | 47 | 48 | 0.0099013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-169_0_6_trafo_25 | 0.63 MVA 20/0.4 kV | 49 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2666105.2675 | 1212249.7444 | 2666110.5107 | 1212232.1955
1 | 2666105.2675 | 1212249.7444 | 2666102.6742 | 1212258.4242
2 | 2666110.8749 | 1212230.9767 | 2666110.5107 | 1212232.1955
3 | 2666102.6742 | 1212258.4242 | 2666099.6351 | 1212268.5961
4 | 2666110.8749 | 1212230.9767 | 2666114.8403 | 1212217.7043
5 | 2666099.5401 | 1212268.9141 | 2666099.6351 | 1212268.5961
6 | 2666118.3248 | 1212206.0418 | 2666114.8403 | 1212217.7043
7 | 2666092.7409 | 1212291.671 | 2666099.5401 | 1212268.9141
8 | 2666118.3248 | 1212206.0418 | 2666123.0804 | 1212191.0673
9 | 2666118.3248 | 1212206.0418 | 2666132.3765 | 1212211.8648
10 | 2666089.538 | 1212305.2732 | 2666091.9541 | 1212294.3043 | 2666092.7409 | 1212291.671
11 | 2666146.6641 | 1212217.7854 | 2666132.3765 | 1212211.8648
12 | 2666146.6641 | 1212217.7854 | 2666147.8569 | 1212206.8363 | 2666148.9683 | 1212201.1674 | 2666150.1106 | 1212197.2513
13 | 2666146.6641 | 1212217.7854 | 2666142.1451 | 1212259.3293
14 | 2666159.0303 | 1212166.6736 | 2666150.1106 | 1212197.2513
15 | 2666159.0303 | 1212166.6736 | 2666166.0505 | 1212142.6075
16 | 2666174.3473 | 1212107.8911 | 2666177.5963 | 1212115.0093 | 2666176.3574 | 1212120.5212 | 2666170.8727 | 1212130.0107 | 2666167.1425 | 1212138.8637 | 2666166.0505 | 1212142.6075
17 | 2666036.3804 | 1212419.5906 | 2666035.1761 | 1212451.8045
18 | 2666036.3804 | 1212419.5906 | 2666036.599 | 1212413.743
19 | 2666037.8868 | 1212383.5983 | 2666037.3497 | 1212393.6611 | 2666036.599 | 1212413.743
20 | 2666038.8644 | 1212365.2825 | 2666037.8868 | 1212383.5983
21 | 2666038.8644 | 1212365.2825 | 2666053.6494 | 1212366.352
22 | 2666038.8644 | 1212365.2825 | 2666040.4245 | 1212336.1531
23 | 2666006.1438 | 1212341.5929 | 2666000.8634 | 1212354.7466
24 | 2666010.3666 | 1212331.0738 | 2666006.1438 | 1212341.5929
25 | 2665991.875 | 1212376.6962 | 2665995.5189 | 1212368.0602 | 2666000.8634 | 1212354.7466
26 | 2666010.3666 | 1212331.0738 | 2666016.085 | 1212316.8288
27 | 2665991.875 | 1212376.6962 | 2665987.869 | 1212386.1904
28 | 2666016.085 | 1212316.8288 | 2666018.1226 | 1212311.7532 | 2666019.3779 | 1212308.7518
29 | 2665987.869 | 1212386.1904 | 2665976.1091 | 1212414.0616
30 | 2666044.4415 | 1212259.6122 | 2666039.5601 | 1212261.993 | 2666037.5635 | 1212265.273 | 2666019.3779 | 1212308.7518
31 | 2665976.1091 | 1212414.0616 | 2665975.2163 | 1212416.1776
32 | 2666044.4415 | 1212259.6122 | 2666043.6049 | 1212276.8359
33 | 2666044.4415 | 1212259.6122 | 2666045.1642 | 1212246.0302
34 | 2666089.538 | 1212305.2732 | 2666087.5622 | 1212314.2124 | 2666085.0551 | 1212337.3658
35 | 2666089.538 | 1212305.2732 | 2666102.5889 | 1212307.7096
36 | 2666081.6966 | 1212368.3809 | 2666085.0551 | 1212337.3658
37 | 2666043.6049 | 1212276.8359 | 2666042.1102 | 1212304.6917
38 | 2666042.1102 | 1212304.6917 | 2666041.7572 | 1212311.27 | 2666040.8073 | 1212329.006
39 | 2666040.4245 | 1212336.1531 | 2666040.8073 | 1212329.006
40 | 2666081.6966 | 1212368.3809 | 2666053.6494 | 1212366.352
41 | 2666081.6966 | 1212368.3809 | 2666080.9704 | 1212375.0913
42 | 2666182.4241 | 1212096.2513 | 2666174.3473 | 1212107.8911
43 | 2666182.4241 | 1212096.2513 | 2666191.7487 | 1212101.5691 | 2666190.5026 | 1212105.6947
44 | 2666080.9704 | 1212375.0913 | 2666078.1165 | 1212401.4639
45 | 2666076.2601 | 1212418.6183 | 2666078.1165 | 1212401.4639
46 | 2666074.5272 | 1212434.6314 | 2666076.2601 | 1212418.6183
47 | 2666074.5272 | 1212434.6314 | 2666073.4823 | 1212444.4774

## bus_geodata
| x | y | coords
0 | 2666105.2675 | 1212249.7444
1 | 2666110.5107 | 1212232.1955
2 | 2666102.6742 | 1212258.4242
3 | 2666110.8749 | 1212230.9767
4 | 2666099.6351 | 1212268.5961
5 | 2666114.8403 | 1212217.7043
6 | 2666099.5401 | 1212268.9141
7 | 2666118.3248 | 1212206.0418
8 | 2666092.7409 | 1212291.671
9 | 2666132.3765 | 1212211.8648
10 | 2666146.6641 | 1212217.7854
11 | 2666123.0804 | 1212191.0673
12 | 2666150.1106 | 1212197.2513
13 | 2666142.1451 | 1212259.3293
14 | 2666159.0303 | 1212166.6736
15 | 2666166.0505 | 1212142.6075
16 | 2666035.1761 | 1212451.8045
17 | 2666036.3804 | 1212419.5906
18 | 2666036.599 | 1212413.743
19 | 2666037.8868 | 1212383.5983
20 | 2666038.8644 | 1212365.2825
21 | 2666006.1438 | 1212341.5929
22 | 2666000.8634 | 1212354.7466
23 | 2666010.3666 | 1212331.0738
24 | 2665991.875 | 1212376.6962
25 | 2666016.085 | 1212316.8288
26 | 2665987.869 | 1212386.1904
27 | 2666019.3779 | 1212308.7518
28 | 2665976.1091 | 1212414.0616
29 | 2666044.4415 | 1212259.6122
30 | 2665975.2163 | 1212416.1776
31 | 2666089.538 | 1212305.2732
32 | 2666085.0551 | 1212337.3658
33 | 2666102.5889 | 1212307.7096
34 | 2666043.6049 | 1212276.8359
35 | 2666045.1642 | 1212246.0302
36 | 2666042.1102 | 1212304.6917
37 | 2666040.8073 | 1212329.006
38 | 2666040.4245 | 1212336.1531
39 | 2666053.6494 | 1212366.352
40 | 2666081.6966 | 1212368.3809
41 | 2666174.3473 | 1212107.8911
42 | 2666182.4241 | 1212096.2513
43 | 2666190.5026 | 1212105.6947
44 | 2666080.9704 | 1212375.0913
45 | 2666078.1165 | 1212401.4639
46 | 2666076.2601 | 1212418.6183
47 | 2666074.5272 | 1212434.6314
48 | 2666073.4823 | 1212444.4774
49 | 2666089.538 | 1212305.2732

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99837 | -0.031062 | 0.0073086 | 0.0018317
1 | 0.99694 | -0.058473 | 0.0077647 | 0.001946
2 | 0.9991 | -0.017148 | 0.0054423 | 0.001364
3 | 0.99684 | -0.060322 | 0.0080216 | 0.0020104
4 | 0.99997 | -0.00053245 | 0.0070282 | 0.0017614
5 | 0.99582 | -0.079828 | 0.0077183 | 0.0019344
6 | 1 | 0 | -0.5694 | -0.14426
7 | 0.99496 | -0.09645 | 0 | 0
8 | 0.99792 | -0.039618 | 0.0068414 | 0.0017146
9 | 0.99415 | -0.11199 | 0.0064341 | 0.0016125
10 | 0.99296 | -0.13485 | 0 | 0
11 | 0.99411 | -0.11278 | 0.058981 | 0.014782
12 | 0.99144 | -0.16419 | 0.052703 | 0.013209
13 | 0.99263 | -0.14123 | 0.0086297 | 0.0021628
14 | 0.98834 | -0.22432 | 0.052721 | 0.013213
15 | 0.9871 | -0.24824 | 0.019306 | 0.0048386
16 | 0.98594 | -0.2707 | 0.017859 | 0.0044759
17 | 0.98647 | -0.26038 | 0.024197 | 0.0060642
18 | 0.98669 | -0.25597 | 0.0073564 | 0.0018437
19 | 0.98806 | -0.22932 | 0.029373 | 0.0073615
20 | 0.98939 | -0.20355 | 0 | 0
21 | 0.98534 | -0.28226 | 0.0021022 | 0.00052685
22 | 0.98485 | -0.29187 | 0.010689 | 0.0026789
23 | 0.98555 | -0.27821 | 0.0044023 | 0.0011033
24 | 0.98426 | -0.3034 | 0.019461 | 0.0048773
25 | 0.98576 | -0.27415 | 0.0043645 | 0.0010938
26 | 0.98418 | -0.30481 | 0.0029215 | 0.00073221
27 | 0.98589 | -0.27161 | 0.0058254 | 0.00146
28 | 0.98406 | -0.30734 | 0.002632 | 0.00065965
29 | 0.98683 | -0.25328 | 0 | 0
30 | 0.98405 | -0.30743 | 0.0020264 | 0.00050786
31 | 0.99672 | -0.062455 | 0 | 0
32 | 0.99412 | -0.11231 | 0.020378 | 0.0051071
33 | 0.99651 | -0.066548 | 0.017568 | 0.0044029
34 | 0.98717 | -0.24659 | 0 | 0
35 | 0.9867 | -0.25587 | 0.010611 | 0.0026595
36 | 0.98773 | -0.23578 | 0.015355 | 0.0038482
37 | 0.98833 | -0.22413 | 0.011369 | 0.0028494
38 | 0.98853 | -0.22022 | 0.0044056 | 0.0011042
39 | 0.99019 | -0.18817 | 0.013924 | 0.0034896
40 | 0.99181 | -0.15675 | 0 | 0
41 | 0.98591 | -0.27141 | 0 | 0
42 | 0.98547 | -0.28007 | 0 | 0
43 | 0.985 | -0.28929 | 0.034098 | 0.0085459
44 | 0.9917 | -0.15885 | 0.012807 | 0.0032096
45 | 0.99138 | -0.16512 | 0.015067 | 0.0037762
46 | 0.99118 | -0.16894 | 0.015067 | 0.003776
47 | 0.99104 | -0.17176 | 0 | 0
48 | 0.99095 | -0.17349 | 0.0098675 | 0.002473
49 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.25817 | 0.065397 | -0.25783 | -0.065181 | 0.00033942 | 0.00021651 | 0.38504 | 0.38504 | 0.38504 | 0.99837 | -0.031062 | 0.99694 | -0.058473 | 35.2598
1 | -0.26548 | -0.067229 | 0.26566 | 0.067342 | 0.00017751 | 0.00011325 | 0.39593 | 0.39593 | 0.39593 | 0.99837 | -0.031062 | 0.9991 | -0.017148 | 36.2573
2 | 0.25007 | 0.063235 | -0.25005 | -0.063221 | 2.2176e-05 | 1.4143e-05 | 0.37345 | 0.37345 | 0.37345 | 0.99694 | -0.058473 | 0.99684 | -0.060322 | 34.1985
3 | -0.2711 | -0.068706 | 0.27132 | 0.068844 | 0.00021663 | 0.00013823 | 0.40404 | 0.40403 | 0.40404 | 0.9991 | -0.017148 | 0.99997 | -0.00053245 | 36.9996
4 | 0.24202 | 0.06121 | -0.2418 | -0.061066 | 0.00022625 | 0.00014426 | 0.36147 | 0.36147 | 0.36147 | 0.99684 | -0.060322 | 0.99582 | -0.079828 | 33.102
5 | -0.27835 | -0.070606 | 0.27835 | 0.07061 | 7.1264e-06 | 4.5478e-06 | 0.41449 | 0.41449 | 0.41449 | 0.99997 | -0.00053245 | 1 | 0 | 37.9573
6 | 0.23408 | 0.059132 | -0.23389 | -0.059013 | 0.00018632 | 0.00011877 | 0.34994 | 0.34994 | 0.34994 | 0.99582 | -0.079828 | 0.99496 | -0.09645 | 32.0459
7 | 0.28939 | 0.073651 | -0.28884 | -0.073299 | 0.00055155 | 0.00035206 | 0.43102 | 0.43102 | 0.43102 | 1 | 0 | 0.99792 | -0.039618 | 39.4707
8 | 0.059027 | 0.014811 | -0.058981 | -0.014782 | 4.5921e-05 | 2.9186e-05 | 0.088284 | 0.088284 | 0.088284 | 0.99496 | -0.09645 | 0.99411 | -0.11278 | 24.2538
9 | 0.17487 | 0.044202 | -0.17474 | -0.044119 | 0.00013017 | 8.2718e-05 | 0.26166 | 0.26166 | 0.26166 | 0.99496 | -0.09645 | 0.99415 | -0.11199 | 23.9613
10 | 0.282 | 0.071584 | -0.28169 | -0.071387 | 0.00030947 | 0.00019751 | 0.42082 | 0.42082 | 0.42082 | 0.99792 | -0.039618 | 0.99672 | -0.062455 | 38.5365
11 | 0.1683 | 0.042506 | -0.16812 | -0.042389 | 0.00018419 | 0.00011748 | 0.25203 | 0.25203 | 0.25203 | 0.99415 | -0.11199 | 0.99296 | -0.13485 | 34.6191
12 | 0.15949 | 0.040225 | -0.15926 | -0.040082 | 0.00022369 | 0.00014262 | 0.23909 | 0.23909 | 0.23909 | 0.99296 | -0.13485 | 0.99144 | -0.16419 | 32.8421
13 | 0.0086323 | 0.0021639 | -0.0086297 | -0.0021628 | 2.6225e-06 | 1.138e-06 | 0.012936 | 0.012936 | 0.012936 | 0.99296 | -0.13485 | 0.99263 | -0.14123 | 3.554
14 | 0.10656 | 0.026874 | -0.10625 | -0.026678 | 0.00030574 | 0.00019527 | 0.15999 | 0.15999 | 0.15999 | 0.99144 | -0.16419 | 0.98834 | -0.22432 | 43.9534
15 | 0.053533 | 0.013465 | -0.053471 | -0.013426 | 6.1094e-05 | 3.8779e-05 | 0.080615 | 0.080615 | 0.080615 | 0.98834 | -0.22432 | 0.9871 | -0.24824 | 22.1469
16 | 0.034165 | 0.0085878 | -0.034127 | -0.0085641 | 3.7753e-05 | 2.3677e-05 | 0.051511 | 0.051512 | 0.051512 | 0.9871 | -0.24824 | 0.98591 | -0.27141 | 14.1516
17 | -0.017859 | -0.0044759 | 0.017868 | 0.0044811 | 8.7823e-06 | 5.2093e-06 | 0.026953 | 0.026953 | 0.026953 | 0.98594 | -0.2707 | 0.98647 | -0.26038 | 7.4048
18 | -0.042064 | -0.010545 | 0.042073 | 0.010551 | 8.835e-06 | 5.5797e-06 | 0.063452 | 0.063452 | 0.063452 | 0.98647 | -0.26038 | 0.98669 | -0.25597 | 17.4319
19 | -0.04943 | -0.012395 | 0.049492 | 0.012434 | 6.2878e-05 | 3.9856e-05 | 0.074546 | 0.074546 | 0.074546 | 0.98669 | -0.25597 | 0.98806 | -0.22932 | 20.4797
20 | -0.078865 | -0.019796 | 0.078962 | 0.019858 | 9.7044e-05 | 6.1873e-05 | 0.11878 | 0.11878 | 0.11878 | 0.98806 | -0.22932 | 0.98939 | -0.20355 | 32.6322
21 | -0.17542 | -0.044141 | 0.17555 | 0.044223 | 0.00012904 | 8.2015e-05 | 0.2639 | 0.2639 | 0.2639 | 0.98939 | -0.20355 | 0.99019 | -0.18817 | 24.1663
22 | 0.096462 | 0.024283 | -0.096385 | -0.024235 | 7.6787e-05 | 4.8021e-05 | 0.14511 | 0.14511 | 0.14511 | 0.98939 | -0.20355 | 0.98853 | -0.22022 | 13.2889
23 | 0.037763 | 0.0094761 | -0.037745 | -0.0094652 | 1.7288e-05 | 1.0884e-05 | 0.057032 | 0.057032 | 0.057032 | 0.98534 | -0.28226 | 0.98485 | -0.29187 | 15.668
24 | -0.039865 | -0.010003 | 0.039872 | 0.010008 | 7.7038e-06 | 4.6416e-06 | 0.060206 | 0.060206 | 0.060206 | 0.98534 | -0.28226 | 0.98555 | -0.27821 | 8.2701
25 | 0.027056 | 0.0067863 | -0.027042 | -0.0067771 | 1.4866e-05 | 9.2127e-06 | 0.040882 | 0.040882 | 0.040882 | 0.98485 | -0.29187 | 0.98426 | -0.3034 | 11.2313
26 | -0.044275 | -0.011111 | 0.044283 | 0.011116 | 8.5754e-06 | 4.9013e-06 | 0.066853 | 0.066853 | 0.066853 | 0.98555 | -0.27821 | 0.98576 | -0.27415 | 6.1221
27 | 0.007581 | 0.0018999 | -0.0075805 | -0.0018997 | 5.076e-07 | 1.9391e-07 | 0.011461 | 0.011461 | 0.011461 | 0.98426 | -0.3034 | 0.98418 | -0.30481 | 3.1487
28 | -0.048648 | -0.01221 | 0.048654 | 0.012213 | 5.8808e-06 | 3.4301e-06 | 0.073441 | 0.073441 | 0.073441 | 0.98576 | -0.27415 | 0.98589 | -0.27161 | 6.7254
29 | 0.004659 | 0.0011675 | -0.0046584 | -0.0011675 | 5.6287e-07 | -2.4126e-08 | 0.007044 | 0.0070441 | 0.0070441 | 0.98418 | -0.30481 | 0.98406 | -0.30734 | 1.9352
30 | -0.054479 | -0.013673 | 0.054527 | 0.013701 | 4.7674e-05 | 2.8351e-05 | 0.082233 | 0.082232 | 0.082233 | 0.98589 | -0.27161 | 0.98683 | -0.25328 | 7.5305
31 | 0.0020264 | 0.00050783 | -0.0020264 | -0.00050786 | 8.0862e-09 | -2.4002e-08 | 0.0030641 | 0.0030642 | 0.0030642 | 0.98406 | -0.30734 | 0.98405 | -0.30743 | 0.8418
32 | -0.06514 | -0.016362 | 0.06516 | 0.016374 | 2.0805e-05 | 1.2654e-05 | 0.098235 | 0.098235 | 0.098235 | 0.98683 | -0.25328 | 0.98717 | -0.24659 | 8.9959
33 | 0.010613 | 0.0026601 | -0.010611 | -0.0026595 | 1.3062e-06 | 6.6222e-07 | 0.016003 | 0.016003 | 0.016003 | 0.98683 | -0.25328 | 0.9867 | -0.25587 | 4.3964
34 | 0.26412 | 0.066982 | -0.26349 | -0.066579 | 0.00063143 | 0.00040285 | 0.39459 | 0.39459 | 0.39459 | 0.99672 | -0.062455 | 0.99412 | -0.11231 | 36.1343
35 | 0.017571 | 0.0044049 | -0.017568 | -0.0044029 | 3.4261e-06 | 2.0197e-06 | 0.026233 | 0.026233 | 0.026233 | 0.99672 | -0.062455 | 0.99651 | -0.066548 | 7.2068
36 | 0.24311 | 0.061472 | -0.24259 | -0.061142 | 0.00051692 | 0.00032962 | 0.36409 | 0.36409 | 0.36409 | 0.99412 | -0.11231 | 0.99181 | -0.15675 | 33.3412
37 | -0.06516 | -0.016374 | 0.065194 | 0.016395 | 3.365e-05 | 2.0465e-05 | 0.098235 | 0.098235 | 0.098235 | 0.98717 | -0.24659 | 0.98773 | -0.23578 | 8.9959
38 | -0.080549 | -0.020243 | 0.080594 | 0.020271 | 4.4832e-05 | 2.7757e-05 | 0.12137 | 0.12137 | 0.12137 | 0.98773 | -0.23578 | 0.98833 | -0.22413 | 11.1141
39 | -0.091963 | -0.02312 | 0.09198 | 0.023131 | 1.7158e-05 | 1.0706e-05 | 0.13848 | 0.13848 | 0.13848 | 0.98833 | -0.22413 | 0.98853 | -0.22022 | 12.6816
40 | -0.18948 | -0.047712 | 0.18976 | 0.047894 | 0.00028515 | 0.00018141 | 0.28482 | 0.28482 | 0.28482 | 0.99019 | -0.18817 | 0.99181 | -0.15675 | 26.0824
41 | 0.052832 | 0.013248 | -0.052827 | -0.013245 | 5.3011e-06 | 3.1314e-06 | 0.079266 | 0.079266 | 0.079266 | 0.99181 | -0.15675 | 0.9917 | -0.15885 | 7.2588
42 | 0.034127 | 0.0085641 | -0.034113 | -0.0085552 | 1.4087e-05 | 8.8351e-06 | 0.051512 | 0.051512 | 0.051512 | 0.98591 | -0.27141 | 0.98547 | -0.28007 | 14.1516
43 | 0.034113 | 0.0085552 | -0.034098 | -0.0085459 | 1.497e-05 | 9.389e-06 | 0.051512 | 0.051512 | 0.051512 | 0.98547 | -0.28007 | 0.985 | -0.28929 | 14.1516
44 | 0.04002 | 0.010035 | -0.040008 | -0.010029 | 1.1957e-05 | 6.6261e-06 | 0.060051 | 0.060051 | 0.060051 | 0.9917 | -0.15885 | 0.99138 | -0.16512 | 5.4992
45 | 0.024941 | 0.0062526 | -0.024936 | -0.0062501 | 4.5339e-06 | 2.4568e-06 | 0.037436 | 0.037436 | 0.037436 | 0.99138 | -0.16512 | 0.99118 | -0.16894 | 5.1423
46 | 0.0098697 | 0.0024741 | -0.0098683 | -0.0024734 | 1.326e-06 | 6.411e-07 | 0.014817 | 0.014817 | 0.014817 | 0.99118 | -0.16894 | 0.99104 | -0.17176 | 4.0706
47 | 0.0098683 | 0.0024734 | -0.0098675 | -0.002473 | 8.1517e-07 | 3.9414e-07 | 0.014817 | 0.014817 | 0.014817 | 0.99104 | -0.17176 | 0.99095 | -0.17349 | 4.0706

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57533 | 0.14575

## res_load
| p_mw | q_mvar
0 | 0.0073086 | 0.0018317
1 | 0.0077647 | 0.001946
2 | 0.0054423 | 0.001364
3 | 0.0080216 | 0.0020104
4 | 0.0070282 | 0.0017614
5 | 0.0077183 | 0.0019344
6 | 0.0059365 | 0.0014878
7 | 0.0068414 | 0.0017146
8 | 0.0064341 | 0.0016125
9 | 0.058981 | 0.014782
10 | 0.052703 | 0.013209
11 | 0.0086297 | 0.0021628
12 | 0.052721 | 0.013213
13 | 0.019306 | 0.0048386
14 | 0.017859 | 0.0044759
15 | 0.024197 | 0.0060642
16 | 0.0073564 | 0.0018437
17 | 0.029373 | 0.0073615
18 | 0.0021022 | 0.00052685
19 | 0.010689 | 0.0026789
20 | 0.0044023 | 0.0011033
21 | 0.019461 | 0.0048773
22 | 0.0043645 | 0.0010938
23 | 0.0029215 | 0.00073221
24 | 0.0058254 | 0.00146
25 | 0.002632 | 0.00065965
26 | 0.0020264 | 0.00050786
27 | 0.020378 | 0.0051071
28 | 0.017568 | 0.0044029
29 | 0.010611 | 0.0026595
30 | 0.015355 | 0.0038482
31 | 0.011369 | 0.0028494
32 | 0.0044056 | 0.0011042
33 | 0.013924 | 0.0034896
34 | 0.034098 | 0.0085459
35 | 0.012807 | 0.0032096
36 | 0.015067 | 0.0037762
37 | 0.015067 | 0.003776
38 | 0.0098675 | 0.002473

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1