## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-174_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-174_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-174_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-174_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1061-174_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1061-174_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1061-174_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1061-174_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1061-174_0_4_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1061-174_0_4_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_1061-174_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1061-174_0_4_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_1061-174_0_4_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_1061-174_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1061-174_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1061-174_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1061-174_0_4_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_1061-174_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1061-174_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1061-174_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1061-174_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1061-174_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1061-174_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1061-174_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1061-174_0_4_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_1061-174_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_1061-174_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1061-174_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1061-174_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_MV_24_1_node_191 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-174_0_4_load_0 | 0 | 0.012898 | 0.0032324 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-174_0_4_load_1 | 1 | 0.017534 | 0.0043944 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-174_0_4_load_4 | 3 | 0.0099052 | 0.0024825 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-174_0_4_load_5 | 4 | 0.0096659 | 0.0024225 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-174_0_4_load_3 | 5 | 0.01831 | 0.0045889 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-174_0_4_load_23 | 8 | 0.011368 | 0.0028491 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-174_0_4_load_21 | 9 | 0.012336 | 0.0030918 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-174_0_4_load_24 | 11 | 0.0056786 | 0.0014232 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-174_0_4_load_25 | 12 | 0.0052061 | 0.0013048 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-174_0_4_load_10 | 13 | 0.026344 | 0.0066023 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-174_0_4_load_15 | 17 | 0.010396 | 0.0026056 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-174_0_4_load_12 | 20 | 0.022115 | 0.0055425 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-174_0_4_load_30 | 24 | 0.037637 | 0.0094328 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-174_0_4_load_31 | 25 | 0.03763 | 0.009431 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-174_0_4_load_22 | 27 | 0.074835 | 0.018755 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-174_0_4_load_27 | 28 | 0.018468 | 0.0046285 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-174_0_4_line_0 |  | 0 | 1 | 0.023692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-174_0_4_line_1 |  | 0 | 2 | 0.013422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-174_0_4_line_2 |  | 2 | 3 | 0.0038852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-174_0_4_line_3 |  | 2 | 4 | 0.04074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-174_0_4_line_4 |  | 3 | 7 | 0.011206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-174_0_4_line_5 |  | 4 | 8 | 0.03521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-174_0_4_line_6 |  | 5 | 6 | 0.021176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-174_0_4_line_7 |  | 6 | 13 | 0.053854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-174_0_4_line_8 |  | 6 | 14 | 0.003438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-174_0_4_line_9 |  | 7 | 9 | 0.016245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-174_0_4_line_10 |  | 8 | 14 | 0.024971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-174_0_4_line_11 |  | 9 | 10 | 0.023648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-174_0_4_line_12 |  | 10 | 11 | 0.011572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-174_0_4_line_13 |  | 10 | 12 | 0.023202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-174_0_4_line_14 |  | 13 | 18 | 0.03612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-174_0_4_line_15 |  | 15 | 16 | 0.22057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-174_0_4_line_16 |  | 15 | 17 | 0.039265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-174_0_4_line_17 |  | 16 | 28 | 0.041469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-174_0_4_line_18 |  | 17 | 21 | 0.053114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-174_0_4_line_19 |  | 18 | 19 | 0.049724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-174_0_4_line_20 |  | 19 | 23 | 0.021343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1061-174_0_4_line_21 |  | 20 | 21 | 0.0062865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-174_0_4_line_22 |  | 21 | 22 | 0.028727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-174_0_4_line_23 |  | 22 | 24 | 0.029009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-174_0_4_line_24 |  | 22 | 23 | 0.040229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1061-174_0_4_line_25 |  | 23 | 25 | 0.015573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-174_0_4_line_26 |  | 23 | 26 | 0.03513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-174_0_4_line_27 |  | 26 | 27 | 0.0027798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-174_0_4_trafo_17 | 0.63 MVA 20/0.4 kV | 29 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2664467.7995 | 1210803.2853 | 2664491.4541 | 1210804.617
1 | 2664455.7519 | 1210799.1086 | 2664459.6005 | 1210802.3299 | 2664460.2332 | 1210802.8593 | 2664467.7995 | 1210803.2853
2 | 2664455.7519 | 1210799.1086 | 2664453.7277 | 1210796.5407 | 2664453.3453 | 1210796.0585
3 | 2664455.7519 | 1210799.1086 | 2664458.1859 | 1210798.9125 | 2664496.4234 | 1210801.0647
4 | 2664442.1731 | 1210796.8161 | 2664446.6473 | 1210796.3085 | 2664453.3453 | 1210796.0585
5 | 2664531.4989 | 1210803.6627 | 2664527.1341 | 1210802.7933 | 2664496.4234 | 1210801.0647
6 | 2664554.1844 | 1210814.4596 | 2664547.6575 | 1210811.5317 | 2664534.0936 | 1210807.9763
7 | 2664554.1844 | 1210814.4596 | 2664553.9621 | 1210816.036 | 2664550.492 | 1210831.9193 | 2664549.0115 | 1210838.8075 | 2664549.1385 | 1210867.7661
8 | 2664555.2533 | 1210811.1914 | 2664554.4516 | 1210813.6398 | 2664554.1844 | 1210814.4596
9 | 2664442.1731 | 1210796.8161 | 2664431.3911 | 1210798.0449 | 2664426.1434 | 1210799.2892
10 | 2664555.2533 | 1210811.1914 | 2664543.149 | 1210806.7911 | 2664537.7584 | 1210804.9095 | 2664531.4989 | 1210803.6627
11 | 2664403.0091 | 1210804.1089 | 2664405.7255 | 1210803.8047 | 2664414.9336 | 1210801.9474 | 2664426.1434 | 1210799.2892
12 | 2664403.0091 | 1210804.1089 | 2664402.716 | 1210792.5431
13 | 2664403.0091 | 1210804.1089 | 2664397.0058 | 1210804.7668 | 2664379.8484 | 1210805.2153
14 | 2664544.0303 | 1210900.925 | 2664549.2701 | 1210897.7687 | 2664549.1385 | 1210867.7661
15 | 2664357.7284 | 1210874.697 | 2664146.491 | 1210938.1617
16 | 2664357.7284 | 1210874.697 | 2664396.9821 | 1210873.7519
17 | 2664146.491 | 1210938.1617 | 2664138.2249 | 1210952.0925 | 2664131.674 | 1210968.3654 | 2664129.2462 | 1210975.703
18 | 2664449.8627 | 1210875.7141 | 2664445.9525 | 1210874.6713 | 2664437.8629 | 1210873.6055 | 2664427.8682 | 1210873.0083 | 2664396.9821 | 1210873.7519
19 | 2664495.8668 | 1210888.0298 | 2664544.0303 | 1210900.925
20 | 2664495.8668 | 1210888.0298 | 2664494.8168 | 1210891.654 | 2664508.7426 | 1210895.5624 | 2664508.1624 | 1210898.6136
21 | 2664449.8627 | 1210875.7141 | 2664455.9353 | 1210877.3398
22 | 2664449.8627 | 1210875.7141 | 2664449.6879 | 1210876.4127 | 2664448.845 | 1210879.8724 | 2664448.3756 | 1210881.8129 | 2664448.2086 | 1210882.5004 | 2664469.2062 | 1210888.1418
23 | 2664469.2062 | 1210888.1418 | 2664460.7064 | 1210898.3006 | 2664455.6486 | 1210898.6796 | 2664451.0729 | 1210904.3781 | 2664447.647 | 1210904.2299
24 | 2664508.1624 | 1210898.6136 | 2664469.2062 | 1210888.1418
25 | 2664508.1624 | 1210898.6136 | 2664507.8232 | 1210900.4666 | 2664506.6295 | 1210904.7341 | 2664502.9021 | 1210907.8846 | 2664498.8039 | 1210909.4747
26 | 2664508.1624 | 1210898.6136 | 2664512.7241 | 1210899.8414 | 2664533.881 | 1210905.4959 | 2664533.9485 | 1210914.0018
27 | 2664533.9485 | 1210914.0018 | 2664533.9716 | 1210916.7815

## bus_geodata
| x | y | coords
0 | 2664467.7995 | 1210803.2853
1 | 2664491.4541 | 1210804.617
2 | 2664455.7519 | 1210799.1086
3 | 2664453.3453 | 1210796.0585
4 | 2664496.4234 | 1210801.0647
5 | 2664534.0936 | 1210807.9763
6 | 2664554.1844 | 1210814.4596
7 | 2664442.1731 | 1210796.8161
8 | 2664531.4989 | 1210803.6627
9 | 2664426.1434 | 1210799.2892
10 | 2664403.0091 | 1210804.1089
11 | 2664402.716 | 1210792.5431
12 | 2664379.8484 | 1210805.2153
13 | 2664549.1385 | 1210867.7661
14 | 2664555.2533 | 1210811.1914
15 | 2664357.7284 | 1210874.697
16 | 2664146.491 | 1210938.1617
17 | 2664396.9821 | 1210873.7519
18 | 2664544.0303 | 1210900.925
19 | 2664495.8668 | 1210888.0298
20 | 2664455.9353 | 1210877.3398
21 | 2664449.8627 | 1210875.7141
22 | 2664469.2062 | 1210888.1418
23 | 2664508.1624 | 1210898.6136
24 | 2664447.647 | 1210904.2299
25 | 2664498.8039 | 1210909.4747
26 | 2664533.9485 | 1210914.0018
27 | 2664533.9716 | 1210916.7815
28 | 2664129.2462 | 1210975.703
29 | 2664448.845 | 1210879.8724

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97128 | -0.55374 | 0.012898 | 0.0032324
1 | 0.9709 | -0.56141 | 0.017534 | 0.0043944
2 | 0.97167 | -0.54619 | 0 | 0
3 | 0.97155 | -0.54857 | 0.0099052 | 0.0024825
4 | 0.97408 | -0.49851 | 0.0096659 | 0.0024225
5 | 0.97837 | -0.41449 | 0.01831 | 0.0045889
6 | 0.97873 | -0.40743 | 0 | 0
7 | 0.9713 | -0.55337 | 0 | 0
8 | 0.97649 | -0.45126 | 0.011368 | 0.0028491
9 | 0.97095 | -0.56035 | 0.012336 | 0.0030918
10 | 0.97071 | -0.56511 | 0 | 0
11 | 0.97065 | -0.56632 | 0.0056786 | 0.0014232
12 | 0.9706 | -0.56734 | 0.0052061 | 0.0013048
13 | 0.9839 | -0.30712 | 0.026344 | 0.0066023
14 | 0.97846 | -0.41272 | 0 | 0
15 | 0.9966 | -0.065129 | 0 | 0
16 | 0.99288 | -0.1369 | 0 | 0
17 | 0.99727 | -0.052405 | 0.010396 | 0.0026056
18 | 0.98824 | -0.22343 | 0 | 0
19 | 0.99423 | -0.10942 | 0 | 0
20 | 0.99854 | -0.027995 | 0.022115 | 0.0055425
21 | 0.99867 | -0.025565 | 0 | 0
22 | 1 | 0 | -0.33585 | -0.085251
23 | 0.99551 | -0.085128 | 0 | 0
24 | 0.99901 | -0.019049 | 0.037637 | 0.0094328
25 | 0.99498 | -0.095439 | 0.03763 | 0.009431
26 | 0.99311 | -0.13147 | 0 | 0
27 | 0.99292 | -0.13515 | 0.074835 | 0.018755
28 | 0.99218 | -0.15045 | 0.018468 | 0.0046285
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01754 | 0.0043982 | -0.017534 | -0.0043944 | 6.4159e-06 | 3.8131e-06 | 0.026873 | 0.026873 | 0.026873 | 0.97128 | -0.55374 | 0.9709 | -0.56141 | 7.3826
1 | -0.030438 | -0.0076307 | 0.030449 | 0.0076375 | 1.0945e-05 | 6.8386e-06 | 0.046632 | 0.046632 | 0.046632 | 0.97128 | -0.55374 | 0.97167 | -0.54619 | 12.8109
2 | 0.033147 | 0.008314 | -0.033143 | -0.0083117 | 3.7544e-06 | 2.3547e-06 | 0.050763 | 0.050763 | 0.050763 | 0.97167 | -0.54619 | 0.97155 | -0.54857 | 13.946
3 | -0.063595 | -0.015952 | 0.06374 | 0.016044 | 0.00014492 | 9.2242e-05 | 0.097395 | 0.097395 | 0.097395 | 0.97167 | -0.54619 | 0.97408 | -0.49851 | 26.7569
4 | 0.023238 | 0.0058292 | -0.023232 | -0.0058259 | 5.3233e-06 | 3.2682e-06 | 0.035593 | 0.035593 | 0.035593 | 0.97155 | -0.54857 | 0.9713 | -0.55337 | 9.7782
5 | -0.073406 | -0.018466 | 0.073572 | 0.018572 | 0.0001661 | 0.00010587 | 0.11216 | 0.11216 | 0.11216 | 0.97408 | -0.49851 | 0.97649 | -0.45126 | 30.8133
6 | -0.01831 | -0.0045889 | 0.018316 | 0.0045926 | 6.158e-06 | 3.6751e-06 | 0.027848 | 0.027848 | 0.027848 | 0.97837 | -0.41449 | 0.97873 | -0.40743 | 7.6504
7 | -0.10344 | -0.026128 | 0.10393 | 0.026447 | 0.0004999 | 0.00031925 | 0.15733 | 0.15733 | 0.15733 | 0.97873 | -0.40743 | 0.9839 | -0.30712 | 43.2228
8 | 0.085119 | 0.021535 | -0.085097 | -0.021521 | 2.1616e-05 | 1.3791e-05 | 0.12948 | 0.12948 | 0.12948 | 0.97873 | -0.40743 | 0.97846 | -0.41272 | 35.5724
9 | 0.023232 | 0.0058259 | -0.023225 | -0.0058212 | 7.7174e-06 | 4.7382e-06 | 0.035593 | 0.035593 | 0.035593 | 0.9713 | -0.55337 | 0.97095 | -0.56035 | 9.7782
10 | -0.08494 | -0.021421 | 0.085097 | 0.021521 | 0.000157 | 0.00010017 | 0.12948 | 0.12948 | 0.12948 | 0.97649 | -0.45126 | 0.97846 | -0.41272 | 35.5724
11 | 0.010888 | 0.0027294 | -0.010886 | -0.0027281 | 2.4692e-06 | 1.2879e-06 | 0.016687 | 0.016687 | 0.016687 | 0.97095 | -0.56035 | 0.97071 | -0.56511 | 4.5843
12 | 0.005679 | 0.0014233 | -0.0056786 | -0.0014232 | 3.2886e-07 | 6.7428e-08 | 0.0087054 | 0.0087054 | 0.0087054 | 0.97071 | -0.56511 | 0.97065 | -0.56632 | 2.3916
13 | 0.0052067 | 0.0013048 | -0.0052061 | -0.0013048 | 5.5427e-07 | 6.7936e-08 | 0.0079813 | 0.0079814 | 0.0079814 | 0.97071 | -0.56511 | 0.9706 | -0.56734 | 2.1927
14 | -0.13028 | -0.033049 | 0.1308 | 0.033386 | 0.00052658 | 0.00033655 | 0.19717 | 0.19717 | 0.19717 | 0.9839 | -0.30712 | 0.98824 | -0.22343 | 54.168
15 | 0.018543 | 0.0046734 | -0.01848 | -0.0046356 | 6.3448e-05 | 3.7743e-05 | 0.027696 | 0.027697 | 0.027697 | 0.9966 | -0.065129 | 0.99288 | -0.1369 | 7.6091
16 | -0.018543 | -0.0046734 | 0.018555 | 0.0046801 | 1.1295e-05 | 6.7165e-06 | 0.027696 | 0.027696 | 0.027696 | 0.9966 | -0.065129 | 0.99727 | -0.052405 | 7.6088
17 | 0.01848 | 0.0046356 | -0.018468 | -0.0046285 | 1.193e-05 | 7.099e-06 | 0.027697 | 0.027697 | 0.027697 | 0.99288 | -0.1369 | 0.99218 | -0.15045 | 7.6091
18 | -0.028951 | -0.0072856 | 0.028988 | 0.0073087 | 3.7185e-05 | 2.3104e-05 | 0.043208 | 0.043208 | 0.043208 | 0.99727 | -0.052405 | 0.99867 | -0.025565 | 11.8703
19 | -0.1308 | -0.033386 | 0.13153 | 0.033849 | 0.00072491 | 0.0004633 | 0.19717 | 0.19717 | 0.19717 | 0.98824 | -0.22343 | 0.99423 | -0.10942 | 54.1679
20 | -0.13153 | -0.033849 | 0.13169 | 0.033948 | 0.00015558 | 9.9014e-05 | 0.19717 | 0.19717 | 0.19717 | 0.99423 | -0.10942 | 0.99551 | -0.085128 | 27.0839
21 | -0.022115 | -0.0055425 | 0.022117 | 0.005544 | 2.5603e-06 | 1.5563e-06 | 0.032955 | 0.032955 | 0.032955 | 0.99854 | -0.027995 | 0.99867 | -0.025565 | 9.0536
22 | -0.051105 | -0.012853 | 0.051168 | 0.012892 | 6.249e-05 | 3.9617e-05 | 0.076163 | 0.076163 | 0.076163 | 0.99867 | -0.025565 | 1 | 0 | 20.9239
23 | 0.037671 | 0.0094543 | -0.037637 | -0.0094328 | 3.4188e-05 | 2.15e-05 | 0.05606 | 0.05606 | 0.05606 | 1 | 0 | 0.99901 | -0.019049 | 15.4012
24 | 0.24536 | 0.062904 | -0.24435 | -0.06226 | 0.0010082 | 0.00064419 | 0.36559 | 0.3656 | 0.3656 | 1 | 0 | 0.99551 | -0.085128 | 50.2191
25 | 0.037649 | 0.0094427 | -0.03763 | -0.009431 | 1.8495e-05 | 1.1635e-05 | 0.056277 | 0.056277 | 0.056277 | 0.99551 | -0.085128 | 0.99498 | -0.095439 | 15.4607
26 | 0.075014 | 0.018869 | -0.074848 | -0.018764 | 0.00016569 | 0.00010559 | 0.11215 | 0.11215 | 0.11215 | 0.99551 | -0.085128 | 0.99311 | -0.13147 | 30.8102
27 | 0.074848 | 0.018764 | -0.074835 | -0.018755 | 1.3111e-05 | 8.3552e-06 | 0.11215 | 0.11215 | 0.11215 | 0.99311 | -0.13147 | 0.99292 | -0.13515 | 30.8102

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33585 | 0.085251

## res_load
| p_mw | q_mvar
0 | 0.012898 | 0.0032324
1 | 0.017534 | 0.0043944
2 | 0.0099052 | 0.0024825
3 | 0.0096659 | 0.0024225
4 | 0.01831 | 0.0045889
5 | 0.011368 | 0.0028491
6 | 0.012336 | 0.0030918
7 | 0.0056786 | 0.0014232
8 | 0.0052061 | 0.0013048
9 | 0.026344 | 0.0066023
10 | 0.010396 | 0.0026056
11 | 0.022115 | 0.0055425
12 | 0.037637 | 0.0094328
13 | 0.03763 | 0.009431
14 | 0.074835 | 0.018755
15 | 0.018468 | 0.0046285

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1