## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-178_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-178_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-178_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-178_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-178_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-178_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1061-178_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1061-178_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1061-178_0_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1061-178_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1061-178_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1061-178_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1061-178_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1061-178_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1061-178_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1061-178_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1061-178_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1061-178_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1061-178_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1061-178_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1061-178_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1061-178_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1061-178_0_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1061-178_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1061-178_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1061-178_0_4_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_1061-178_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1061-178_0_4_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1061-178_0_4_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_1061-178_0_4_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1061-178_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1061-178_0_4_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1061-178_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_219_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-178_0_4_load_0 | 0 | 0.00968 | 0.002426 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-178_0_4_load_1 | 1 | 0.018018 | 0.0045158 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-178_0_4_load_2 | 2 | 0.015986 | 0.0040065 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-178_0_4_load_3 | 3 | 0.012646 | 0.0031694 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-178_0_4_load_15 | 5 | 0.018571 | 0.0046543 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-178_0_4_load_10 | 6 | 0.016366 | 0.0041018 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-178_0_4_load_13 | 7 | 0.022199 | 0.0055636 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-178_0_4_load_25 | 8 | 0.017809 | 0.0044634 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-178_0_4_load_6 | 9 | 0.015734 | 0.0039434 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-178_0_4_load_5 | 10 | 0.010639 | 0.0026664 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-178_0_4_load_8 | 12 | 0.013437 | 0.0033676 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-178_0_4_load_9 | 13 | 0.01878 | 0.0047066 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-178_0_4_load_14 | 14 | 0.017066 | 0.0042772 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-178_0_4_load_26 | 15 | 0.0085002 | 0.0021304 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-178_0_4_load_12 | 16 | 0.029463 | 0.0073841 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-178_0_4_load_11 | 18 | 0.016159 | 0.0040497 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-178_0_4_load_16 | 19 | 0.020927 | 0.0052447 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-178_0_4_load_19 | 21 | 0.020167 | 0.0050543 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-178_0_4_load_33 | 22 | 0.054098 | 0.013558 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-178_0_4_load_35 | 25 | 0.0087987 | 0.0022052 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-178_0_4_load_28 | 26 | 0.015966 | 0.0040014 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-178_0_4_load_30 | 27 | 0.013578 | 0.0034031 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-178_0_4_load_34 | 28 | 0.020419 | 0.0051175 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-178_0_4_load_27 | 29 | 0.020583 | 0.0051587 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-178_0_4_load_29 | 30 | 0.020659 | 0.0051775 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-178_0_4_load_31 | 31 | 0.033575 | 0.0084148 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-178_0_4_load_32 | 32 | 0.023879 | 0.0059846 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-178_0_4_line_0 |  | 0 | 1 | 0.012003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-178_0_4_line_1 |  | 0 | 2 | 0.0049755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-178_0_4_line_2 |  | 1 | 3 | 0.0072281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-178_0_4_line_3 |  | 2 | 4 | 0.015964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-178_0_4_line_4 |  | 3 | 5 | 0.011688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-178_0_4_line_5 |  | 4 | 6 | 0.011346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-178_0_4_line_6 |  | 5 | 7 | 0.0034095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-178_0_4_line_7 |  | 6 | 8 | 0.00050371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-178_0_4_line_8 |  | 7 | 18 | 0.01661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1061-178_0_4_line_9 |  | 9 | 10 | 0.0093352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-178_0_4_line_10 |  | 10 | 11 | 0.012414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-178_0_4_line_11 |  | 11 | 12 | 0.0040636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1061-178_0_4_line_12 |  | 11 | 13 | 0.0097019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1061-178_0_4_line_13 |  | 12 | 14 | 0.013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1061-178_0_4_line_14 |  | 13 | 15 | 0.0012392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1061-178_0_4_line_15 |  | 14 | 16 | 0.0049559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1061-178_0_4_line_16 |  | 15 | 17 | 0.012966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1061-178_0_4_line_17 |  | 16 | 18 | 0.009417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1061-178_0_4_line_18 |  | 17 | 24 | 0.045232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1061-178_0_4_line_19 |  | 19 | 20 | 0.015611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-178_0_4_line_20 |  | 20 | 21 | 0.011087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-178_0_4_line_21 |  | 21 | 22 | 0.0093235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-178_0_4_line_22 |  | 22 | 28 | 0.0082695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-178_0_4_line_23 |  | 23 | 24 | 0.043559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-178_0_4_line_24 |  | 23 | 25 | 0.014882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-178_0_4_line_25 |  | 24 | 26 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-178_0_4_line_26 |  | 24 | 27 | 0.017056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1061-178_0_4_line_27 |  | 26 | 29 | 0.0056185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-178_0_4_line_28 |  | 27 | 30 | 0.013789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1061-178_0_4_line_29 |  | 28 | 32 | 0.017649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-178_0_4_line_30 |  | 30 | 31 | 0.016971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1061-178_0_4_line_31 |  | 31 | 32 | 0.00020745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-178_0_4_trafo_13 | 0.63 MVA 20/0.4 kV | 33 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2665569.8339 | 1211106.4261 | 2665579.9895 | 1211112.8233
1 | 2665569.8339 | 1211106.4261 | 2665565.624 | 1211103.7742
2 | 2665582.3766 | 1211117.5168 | 2665583.8217 | 1211115.2372 | 2665579.9895 | 1211112.8233
3 | 2665552.1164 | 1211095.2655 | 2665565.624 | 1211103.7742
4 | 2665582.3766 | 1211117.5168 | 2665576.1191 | 1211127.3885
5 | 2665552.1164 | 1211095.2655 | 2665555.751 | 1211089.5352 | 2665558.1924 | 1211085.6836
6 | 2665574.2937 | 1211130.2681 | 2665576.1191 | 1211127.3885
7 | 2665558.1924 | 1211085.6836 | 2665558.462 | 1211085.2581
8 | 2665574.2937 | 1211130.2681 | 2665565.4007 | 1211144.2973
9 | 2665537.955 | 1211164.4086 | 2665530.0576 | 1211159.431
10 | 2665548.4567 | 1211171.0275 | 2665537.955 | 1211164.4086
11 | 2665548.4567 | 1211171.0275 | 2665550.6323 | 1211167.5953
12 | 2665548.4567 | 1211171.0275 | 2665545.4868 | 1211175.7422 | 2665543.2796 | 1211179.2326
13 | 2665557.7057 | 1211156.4367 | 2665550.6323 | 1211167.5953
14 | 2665543.2796 | 1211179.2326 | 2665542.6173 | 1211180.2799
15 | 2665560.359 | 1211152.2509 | 2665557.7057 | 1211156.4367
16 | 2665535.6958 | 1211191.2442 | 2665539.7407 | 1211184.8291 | 2665542.6173 | 1211180.2799
17 | 2665560.359 | 1211152.2509 | 2665565.4007 | 1211144.2973
18 | 2665535.6958 | 1211191.2442 | 2665539.2123 | 1211193.4953 | 2665549.8373 | 1211200.294 | 2665556.4703 | 1211204.5472 | 2665561.2073 | 1211197.3837 | 2665567.9125 | 1211187.4624
19 | 2665619.8386 | 1211108.6847 | 2665613.1595 | 1211104.4753 | 2665606.6314 | 1211100.362
20 | 2665619.8386 | 1211108.6847 | 2665615.4414 | 1211115.3404 | 2665613.7303 | 1211117.9369
21 | 2665613.7303 | 1211117.9369 | 2665608.5999 | 1211125.7219
22 | 2665604.0495 | 1211132.6269 | 2665608.5999 | 1211125.7219
23 | 2665575.9495 | 1211216.7688 | 2665562.8778 | 1211208.5645 | 2665556.4703 | 1211204.5472 | 2665561.2073 | 1211197.3837 | 2665567.9125 | 1211187.4624
24 | 2665575.9495 | 1211216.7688 | 2665588.6347 | 1211224.5509
25 | 2665567.9125 | 1211187.4624 | 2665574.5513 | 1211191.8825 | 2665580.4251 | 1211195.7145
26 | 2665567.9125 | 1211187.4624 | 2665577.2977 | 1211173.221
27 | 2665585.1308 | 1211198.7844 | 2665580.4251 | 1211195.7145
28 | 2665584.8853 | 1211161.7073 | 2665577.2977 | 1211173.221
29 | 2665604.0495 | 1211132.6269 | 2665594.3382 | 1211147.3632
30 | 2665584.8853 | 1211161.7073 | 2665594.224 | 1211147.5364
31 | 2665594.224 | 1211147.5364 | 2665594.3382 | 1211147.3632

## bus_geodata
| x | y | coords
0 | 2665569.8339 | 1211106.4261
1 | 2665579.9895 | 1211112.8233
2 | 2665565.624 | 1211103.7742
3 | 2665582.3766 | 1211117.5168
4 | 2665552.1164 | 1211095.2655
5 | 2665576.1191 | 1211127.3885
6 | 2665558.1924 | 1211085.6836
7 | 2665574.2937 | 1211130.2681
8 | 2665558.462 | 1211085.2581
9 | 2665530.0576 | 1211159.431
10 | 2665537.955 | 1211164.4086
11 | 2665548.4567 | 1211171.0275
12 | 2665550.6323 | 1211167.5953
13 | 2665543.2796 | 1211179.2326
14 | 2665557.7057 | 1211156.4367
15 | 2665542.6173 | 1211180.2799
16 | 2665560.359 | 1211152.2509
17 | 2665535.6958 | 1211191.2442
18 | 2665565.4007 | 1211144.2973
19 | 2665606.6314 | 1211100.362
20 | 2665619.8386 | 1211108.6847
21 | 2665613.7303 | 1211117.9369
22 | 2665608.5999 | 1211125.7219
23 | 2665575.9495 | 1211216.7688
24 | 2665567.9125 | 1211187.4624
25 | 2665588.6347 | 1211224.5509
26 | 2665580.4251 | 1211195.7145
27 | 2665577.2977 | 1211173.221
28 | 2665604.0495 | 1211132.6269
29 | 2665585.1308 | 1211198.7844
30 | 2665584.8853 | 1211161.7073
31 | 2665594.224 | 1211147.5364
32 | 2665594.3382 | 1211147.3632
33 | 2665548.4567 | 1211171.0275

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99754 | -0.047364 | 0.00968 | 0.002426
1 | 0.99819 | -0.034792 | 0.018018 | 0.0045158
2 | 0.99731 | -0.051737 | 0.015986 | 0.0040065
3 | 0.9987 | -0.024952 | 0.012646 | 0.0031694
4 | 0.99681 | -0.061303 | 0 | 0
5 | 0.99966 | -0.0064842 | 0.018571 | 0.0046543
6 | 0.99646 | -0.068107 | 0.016366 | 0.0041018
7 | 1 | 0 | -0.49727 | -0.12581
8 | 0.99645 | -0.068264 | 0.017809 | 0.0044634
9 | 0.99438 | -0.10729 | 0.015734 | 0.0039434
10 | 0.99452 | -0.1047 | 0.010639 | 0.0026664
11 | 0.99482 | -0.098933 | 0 | 0
12 | 0.9952 | -0.091629 | 0.013437 | 0.0033676
13 | 0.99398 | -0.11489 | 0.01878 | 0.0047066
14 | 0.99649 | -0.06688 | 0.017066 | 0.0042772
15 | 0.99388 | -0.11679 | 0.0085002 | 0.0021304
16 | 0.997 | -0.057118 | 0.029463 | 0.0073841
17 | 0.99288 | -0.13608 | 0 | 0
18 | 0.99806 | -0.036979 | 0.016159 | 0.0040497
19 | 0.98261 | -0.33519 | 0.020927 | 0.0052447
20 | 0.98291 | -0.3293 | 0 | 0
21 | 0.98313 | -0.32511 | 0.020167 | 0.0050543
22 | 0.98348 | -0.31821 | 0.054098 | 0.013558
23 | 0.98902 | -0.2105 | 0 | 0
24 | 0.98937 | -0.20367 | 0 | 0
25 | 0.9889 | -0.21283 | 0.0087987 | 0.0022052
26 | 0.98887 | -0.21343 | 0.015966 | 0.0040014
27 | 0.98829 | -0.22468 | 0.013578 | 0.0034031
28 | 0.98421 | -0.30403 | 0.020419 | 0.0051175
29 | 0.98876 | -0.21549 | 0.020583 | 0.0051587
30 | 0.98747 | -0.24058 | 0.020659 | 0.0051775
31 | 0.98611 | -0.26687 | 0.033575 | 0.0084148
32 | 0.98609 | -0.26739 | 0.023879 | 0.0059846
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.059879 | -0.015021 | 0.059915 | 0.015044 | 3.5914e-05 | 2.2828e-05 | 0.089326 | 0.089326 | 0.089326 | 0.99754 | -0.047364 | 0.99819 | -0.034792 | 24.5401
1 | 0.050199 | 0.012595 | -0.050189 | -0.012589 | 1.0463e-05 | 6.6316e-06 | 0.074887 | 0.074887 | 0.074887 | 0.99754 | -0.047364 | 0.99731 | -0.051737 | 20.5732
2 | -0.077933 | -0.01956 | 0.07797 | 0.019583 | 3.659e-05 | 2.3323e-05 | 0.11619 | 0.11619 | 0.11619 | 0.99819 | -0.034792 | 0.9987 | -0.024952 | 31.9193
3 | 0.034202 | 0.008582 | -0.034187 | -0.0085722 | 1.5592e-05 | 9.7708e-06 | 0.051035 | 0.051035 | 0.051035 | 0.99731 | -0.051737 | 0.99681 | -0.061303 | 14.0205
4 | -0.090616 | -0.022753 | 0.090696 | 0.022804 | 7.9913e-05 | 5.0991e-05 | 0.13503 | 0.13503 | 0.13503 | 0.9987 | -0.024952 | 0.99966 | -0.0064842 | 37.0957
5 | 0.034187 | 0.0085722 | -0.034176 | -0.0085653 | 1.1082e-05 | 6.9444e-06 | 0.051035 | 0.051035 | 0.051035 | 0.99681 | -0.061303 | 0.99646 | -0.068107 | 14.0205
6 | -0.10927 | -0.027458 | 0.1093 | 0.027479 | 3.3833e-05 | 2.1608e-05 | 0.16267 | 0.16267 | 0.16267 | 0.99966 | -0.0064842 | 1 | 0 | 44.69
7 | 0.017809 | 0.0044635 | -0.017809 | -0.0044634 | 1.336e-07 | 7.8942e-08 | 0.026595 | 0.026595 | 0.026595 | 0.99646 | -0.068107 | 0.99645 | -0.068264 | 7.3062
8 | 0.38632 | 0.098331 | -0.38564 | -0.097891 | 0.0006874 | 0.00043929 | 0.57539 | 0.57539 | 0.57539 | 1 | 0 | 0.99806 | -0.036979 | 52.6913
9 | -0.015734 | -0.0039434 | 0.015736 | 0.0039445 | 1.9407e-06 | 1.1209e-06 | 0.023545 | 0.023545 | 0.023545 | 0.99438 | -0.10729 | 0.99452 | -0.1047 | 6.4685
10 | -0.026375 | -0.0066109 | 0.026383 | 0.0066154 | 7.2497e-06 | 4.4787e-06 | 0.039464 | 0.039464 | 0.039464 | 0.99452 | -0.1047 | 0.99482 | -0.098933 | 10.8417
11 | -0.3085 | -0.078168 | 0.30861 | 0.078237 | 0.0001083 | 6.9154e-05 | 0.46175 | 0.46175 | 0.46175 | 0.99482 | -0.098933 | 0.9952 | -0.091629 | 42.2849
12 | 0.28212 | 0.071553 | -0.2819 | -0.071415 | 0.00021626 | 0.00013803 | 0.42229 | 0.42229 | 0.42229 | 0.99482 | -0.098933 | 0.99398 | -0.11489 | 38.671
13 | -0.32205 | -0.081605 | 0.32243 | 0.08185 | 0.00038342 | 0.00024487 | 0.48184 | 0.48184 | 0.48184 | 0.9952 | -0.091629 | 0.99649 | -0.06688 | 44.1247
14 | 0.26312 | 0.066708 | -0.2631 | -0.066693 | 2.4068e-05 | 1.5355e-05 | 0.39417 | 0.39417 | 0.39417 | 0.99398 | -0.11489 | 0.99388 | -0.11679 | 36.0965
15 | -0.3395 | -0.086127 | 0.33966 | 0.086229 | 0.00015944 | 0.00010185 | 0.50733 | 0.50733 | 0.50733 | 0.99649 | -0.06688 | 0.997 | -0.057118 | 46.4584
16 | 0.2546 | 0.064562 | -0.25436 | -0.064412 | 0.00023583 | 0.00015043 | 0.38145 | 0.38145 | 0.38145 | 0.99388 | -0.11679 | 0.99288 | -0.13608 | 34.9311
17 | -0.36912 | -0.093613 | 0.36948 | 0.093842 | 0.00035776 | 0.0002286 | 0.5513 | 0.5513 | 0.5513 | 0.997 | -0.057118 | 0.99806 | -0.036979 | 50.4852
18 | 0.25436 | 0.064412 | -0.25354 | -0.063887 | 0.00082266 | 0.00052476 | 0.38145 | 0.38145 | 0.38145 | 0.99288 | -0.13608 | 0.98937 | -0.20367 | 34.9312
19 | -0.020927 | -0.0052447 | 0.020932 | 0.0052483 | 5.879e-06 | 3.5648e-06 | 0.03169 | 0.03169 | 0.03169 | 0.98261 | -0.33519 | 0.98291 | -0.3293 | 8.7061
20 | -0.020932 | -0.0052483 | 0.020937 | 0.0052508 | 4.1752e-06 | 2.5316e-06 | 0.03169 | 0.03169 | 0.03169 | 0.98291 | -0.3293 | 0.98313 | -0.32511 | 8.7061
21 | -0.041103 | -0.010305 | 0.041117 | 0.010314 | 1.3533e-05 | 8.5426e-06 | 0.062214 | 0.062214 | 0.062214 | 0.98313 | -0.32511 | 0.98348 | -0.31821 | 17.0917
22 | -0.095215 | -0.023872 | 0.095279 | 0.023913 | 6.4361e-05 | 4.1086e-05 | 0.14406 | 0.14406 | 0.14406 | 0.98348 | -0.31821 | 0.98421 | -0.30403 | 39.5781
23 | -0.0087997 | -0.0022056 | 0.0088026 | 0.0022069 | 2.8632e-06 | 1.2732e-06 | 0.01324 | 0.013239 | 0.01324 | 0.98902 | -0.2105 | 0.98937 | -0.20367 | 3.6372
24 | 0.0087997 | 0.0022056 | -0.0087987 | -0.0022052 | 9.7824e-07 | 4.3512e-07 | 0.01324 | 0.01324 | 0.01324 | 0.98902 | -0.2105 | 0.9889 | -0.21283 | 3.6373
25 | 0.036568 | 0.009172 | -0.036551 | -0.0091613 | 1.7004e-05 | 1.069e-05 | 0.055001 | 0.055001 | 0.055001 | 0.98937 | -0.20367 | 0.98887 | -0.21343 | 15.1102
26 | 0.20817 | 0.052508 | -0.20796 | -0.052375 | 0.00020915 | 0.0001332 | 0.31321 | 0.31321 | 0.31321 | 0.98937 | -0.20367 | 0.98829 | -0.22468 | 28.6821
27 | 0.020586 | 0.0051599 | -0.020583 | -0.0051587 | 2.0217e-06 | 1.2218e-06 | 0.030977 | 0.030977 | 0.030977 | 0.98887 | -0.21343 | 0.98876 | -0.21549 | 8.5101
28 | 0.19438 | 0.048972 | -0.19423 | -0.048878 | 0.00014773 | 9.402e-05 | 0.29276 | 0.29276 | 0.29276 | 0.98829 | -0.22468 | 0.98747 | -0.24058 | 26.8099
29 | -0.1157 | -0.02903 | 0.1159 | 0.02916 | 0.00020253 | 0.0001294 | 0.17494 | 0.17494 | 0.17494 | 0.98421 | -0.30403 | 0.98609 | -0.26739 | 48.0592
30 | 0.17358 | 0.0437 | -0.17336 | -0.043561 | 0.00021782 | 0.00013897 | 0.26163 | 0.26163 | 0.26163 | 0.98747 | -0.24058 | 0.98611 | -0.26687 | 35.9387
31 | 0.13978 | 0.035147 | -0.13978 | -0.035144 | 3.4625e-06 | 2.2133e-06 | 0.21097 | 0.21097 | 0.21097 | 0.98611 | -0.26687 | 0.98609 | -0.26739 | 57.9586

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51947 | 0.13137

## res_load
| p_mw | q_mvar
0 | 0.00968 | 0.002426
1 | 0.018018 | 0.0045158
2 | 0.015986 | 0.0040065
3 | 0.012646 | 0.0031694
4 | 0.018571 | 0.0046543
5 | 0.016366 | 0.0041018
6 | 0.022199 | 0.0055636
7 | 0.017809 | 0.0044634
8 | 0.015734 | 0.0039434
9 | 0.010639 | 0.0026664
10 | 0.013437 | 0.0033676
11 | 0.01878 | 0.0047066
12 | 0.017066 | 0.0042772
13 | 0.0085002 | 0.0021304
14 | 0.029463 | 0.0073841
15 | 0.016159 | 0.0040497
16 | 0.020927 | 0.0052447
17 | 0.020167 | 0.0050543
18 | 0.054098 | 0.013558
19 | 0.0087987 | 0.0022052
20 | 0.015966 | 0.0040014
21 | 0.013578 | 0.0034031
22 | 0.020419 | 0.0051175
23 | 0.020583 | 0.0051587
24 | 0.020659 | 0.0051775
25 | 0.033575 | 0.0084148
26 | 0.023879 | 0.0059846

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1