## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-182_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-182_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1061-182_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1061-182_0_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_1061-182_0_4_node_91 | 0.4 | n |  | TRUE
5 | bus_LV_1061-182_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1061-182_0_4_node_85 | 0.4 | n |  | TRUE
7 | bus_LV_1061-182_0_4_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_1061-182_0_4_node_92 | 0.4 | n |  | TRUE
9 | bus_LV_1061-182_0_4_node_93 | 0.4 | n |  | TRUE
10 | bus_LV_1061-182_0_4_node_66 | 0.4 | n |  | TRUE
11 | bus_LV_1061-182_0_4_node_114 | 0.4 | n |  | TRUE
12 | bus_LV_1061-182_0_4_node_90 | 0.4 | n |  | TRUE
13 | bus_LV_1061-182_0_4_node_89 | 0.4 | n |  | TRUE
14 | bus_LV_1061-182_0_4_node_87 | 0.4 | n |  | TRUE
15 | bus_LV_1061-182_0_4_node_86 | 0.4 | n |  | TRUE
16 | bus_LV_1061-182_0_4_node_95 | 0.4 | n |  | TRUE
17 | bus_LV_1061-182_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1061-182_0_4_node_49 | 0.4 | n |  | TRUE
19 | bus_LV_1061-182_0_4_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_1061-182_0_4_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_1061-182_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1061-182_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1061-182_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1061-182_0_4_node_62 | 0.4 | n |  | TRUE
25 | bus_LV_1061-182_0_4_node_51 | 0.4 | n |  | TRUE
26 | bus_LV_1061-182_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_1061-182_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1061-182_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1061-182_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1061-182_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1061-182_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1061-182_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1061-182_0_4_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_1061-182_0_4_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_1061-182_0_4_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1061-182_0_4_node_113 | 0.4 | n |  | TRUE
37 | bus_LV_1061-182_0_4_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_1061-182_0_4_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_1061-182_0_4_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_1061-182_0_4_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1061-182_0_4_node_68 | 0.4 | n |  | TRUE
42 | bus_LV_1061-182_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_1061-182_0_4_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_1061-182_0_4_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_1061-182_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_1061-182_0_4_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_1061-182_0_4_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_1061-182_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1061-182_0_4_node_106 | 0.4 | n |  | TRUE
50 | bus_LV_1061-182_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_1061-182_0_4_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_1061-182_0_4_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_1061-182_0_4_node_96 | 0.4 | n |  | TRUE
54 | bus_LV_1061-182_0_4_node_71 | 0.4 | n |  | TRUE
55 | bus_LV_1061-182_0_4_node_108 | 0.4 | n |  | TRUE
56 | bus_LV_1061-182_0_4_node_102 | 0.4 | n |  | TRUE
57 | bus_LV_1061-182_0_4_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_1061-182_0_4_node_98 | 0.4 | n |  | TRUE
59 | bus_LV_1061-182_0_4_node_69 | 0.4 | n |  | TRUE
60 | bus_LV_1061-182_0_4_node_72 | 0.4 | n |  | TRUE
61 | bus_LV_1061-182_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_1061-182_0_4_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_1061-182_0_4_node_94 | 0.4 | n |  | TRUE
64 | bus_LV_1061-182_0_4_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_1061-182_0_4_node_109 | 0.4 | n |  | TRUE
66 | bus_LV_1061-182_0_4_node_28 | 0.4 | n |  | TRUE
67 | bus_LV_1061-182_0_4_node_29 | 0.4 | n |  | TRUE
68 | bus_LV_1061-182_0_4_node_30 | 0.4 | n |  | TRUE
69 | bus_LV_1061-182_0_4_node_31 | 0.4 | n |  | TRUE
70 | bus_LV_1061-182_0_4_node_32 | 0.4 | n |  | TRUE
71 | bus_LV_1061-182_0_4_node_33 | 0.4 | n |  | TRUE
72 | bus_LV_1061-182_0_4_node_34 | 0.4 | n |  | TRUE
73 | bus_LV_1061-182_0_4_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_1061-182_0_4_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_1061-182_0_4_node_122 | 0.4 | n |  | TRUE
76 | bus_LV_1061-182_0_4_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_1061-182_0_4_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_1061-182_0_4_node_83 | 0.4 | n |  | TRUE
79 | bus_LV_1061-182_0_4_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_1061-182_0_4_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_1061-182_0_4_node_121 | 0.4 | n |  | TRUE
82 | bus_LV_1061-182_0_4_node_123 | 0.4 | n |  | TRUE
83 | bus_LV_1061-182_0_4_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1061-182_0_4_node_35 | 0.4 | n |  | TRUE
85 | bus_LV_1061-182_0_4_node_36 | 0.4 | n |  | TRUE
86 | bus_LV_1061-182_0_4_node_37 | 0.4 | n |  | TRUE
87 | bus_LV_1061-182_0_4_node_38 | 0.4 | n |  | TRUE
88 | bus_LV_1061-182_0_4_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_1061-182_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_1061-182_0_4_node_54 | 0.4 | n |  | TRUE
91 | bus_LV_1061-182_0_4_node_118 | 0.4 | n |  | TRUE
92 | bus_LV_1061-182_0_4_node_103 | 0.4 | n |  | TRUE
93 | bus_LV_1061-182_0_4_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_1061-182_0_4_node_46 | 0.4 | n |  | TRUE
95 | bus_LV_1061-182_0_4_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_1061-182_0_4_node_120 | 0.4 | n |  | TRUE
97 | bus_LV_1061-182_0_4_node_101 | 0.4 | n |  | TRUE
98 | bus_LV_1061-182_0_4_node_58 | 0.4 | n |  | TRUE
99 | bus_LV_1061-182_0_4_node_55 | 0.4 | n |  | TRUE
100 | bus_LV_1061-182_0_4_node_52 | 0.4 | n |  | TRUE
101 | bus_LV_1061-182_0_4_node_53 | 0.4 | n |  | TRUE
102 | bus_LV_1061-182_0_4_node_56 | 0.4 | n |  | TRUE
103 | bus_LV_1061-182_0_4_node_61 | 0.4 | n |  | TRUE
104 | bus_LV_1061-182_0_4_node_63 | 0.4 | n |  | TRUE
105 | bus_LV_1061-182_0_4_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_1061-182_0_4_node_116 | 0.4 | n |  | TRUE
107 | bus_LV_1061-182_0_4_node_64 | 0.4 | n |  | TRUE
108 | bus_LV_1061-182_0_4_node_128 | 0.4 | n |  | TRUE
109 | bus_LV_1061-182_0_4_node_77 | 0.4 | n |  | TRUE
110 | bus_LV_1061-182_0_4_node_80 | 0.4 | n |  | TRUE
111 | bus_LV_1061-182_0_4_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_1061-182_0_4_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_1061-182_0_4_node_99 | 0.4 | n |  | TRUE
114 | bus_LV_1061-182_0_4_node_117 | 0.4 | n |  | TRUE
115 | bus_LV_1061-182_0_4_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_1061-182_0_4_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_1061-182_0_4_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_1061-182_0_4_node_129 | 0.4 | n |  | TRUE
119 | bus_LV_1061-182_0_4_node_132 | 0.4 | n |  | TRUE
120 | bus_LV_1061-182_0_4_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_1061-182_0_4_node_110 | 0.4 | n |  | TRUE
122 | bus_LV_1061-182_0_4_node_124 | 0.4 | n |  | TRUE
123 | bus_LV_1061-182_0_4_node_125 | 0.4 | n |  | TRUE
124 | bus_LV_1061-182_0_4_node_127 | 0.4 | n |  | TRUE
125 | bus_LV_1061-182_0_4_node_130 | 0.4 | n |  | TRUE
126 | bus_MV_219_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-182_0_4_load_0 | 0 | 0.0085763 | 0.0021494 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-182_0_4_load_6 | 3 | 0.0053095 | 0.0013307 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-182_0_4_load_91 | 4 | 0.010128 | 0.0025383 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-182_0_4_load_85 | 6 | 0.0075425 | 0.0018903 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-182_0_4_load_50 | 7 | 0.0091371 | 0.00229 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-182_0_4_load_114 | 11 | 0.0043035 | 0.0010786 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-182_0_4_load_90 | 12 | 0.0082133 | 0.0020585 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-182_0_4_load_89 | 13 | 0.007174 | 0.001798 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-182_0_4_load_87 | 14 | 0.016891 | 0.0042333 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-182_0_4_load_10 | 17 | 0.006898 | 0.0017288 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-182_0_4_load_49 | 18 | 0.006001 | 0.001504 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-182_0_4_load_7 | 19 | 0.0079959 | 0.002004 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-182_0_4_load_8 | 20 | 0.008927 | 0.0022373 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-182_0_4_load_11 | 22 | 0.0093283 | 0.0023379 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-182_0_4_load_12 | 23 | 0.0050105 | 0.0012558 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-182_0_4_load_62 | 24 | 0.0071665 | 0.0017961 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-182_0_4_load_51 | 25 | 0.0064204 | 0.0016091 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-182_0_4_load_13 | 26 | 0.0033671 | 0.00084388 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-182_0_4_load_17 | 29 | 0.0042193 | 0.0010575 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-182_0_4_load_20 | 31 | 0.0037888 | 0.00094955 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-182_0_4_load_48 | 34 | 0.0042446 | 0.0010638 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-182_0_4_load_44 | 35 | 0.0030893 | 0.00077425 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-182_0_4_load_113 | 36 | 0.004332 | 0.0010857 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-182_0_4_load_67 | 37 | 0.0052682 | 0.0013203 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-182_0_4_load_65 | 38 | 0.0070252 | 0.0017607 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-182_0_4_load_57 | 39 | 0.0027426 | 0.00068737 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-182_0_4_load_45 | 40 | 0.0058596 | 0.0014686 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-182_0_4_load_21 | 42 | 0.0038351 | 0.00096115 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-182_0_4_load_22 | 44 | 0.010894 | 0.0027303 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-182_0_4_load_106 | 49 | 0.0092901 | 0.0023283 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-182_0_4_load_41 | 50 | 0.0044042 | 0.0011038 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-182_0_4_load_60 | 52 | 0.010127 | 0.0025381 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-182_0_4_load_71 | 54 | 0.007042 | 0.0017649 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1061-182_0_4_load_108 | 55 | 0.0063803 | 0.0015991 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1061-182_0_4_load_102 | 56 | 0.0079232 | 0.0019857 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1061-182_0_4_load_42 | 57 | 0.0077122 | 0.0019329 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1061-182_0_4_load_69 | 59 | 0.0032772 | 0.00082135 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1061-182_0_4_load_40 | 61 | 0.002974 | 0.00074534 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1061-182_0_4_load_59 | 62 | 0.0063245 | 0.0015851 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1061-182_0_4_load_94 | 63 | 0.0065273 | 0.0016359 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1061-182_0_4_load_70 | 64 | 0.0040458 | 0.001014 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1061-182_0_4_load_109 | 65 | 0.0099488 | 0.0024934 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1061-182_0_4_load_28 | 66 | 0.0017111 | 0.00042884 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1061-182_0_4_load_29 | 67 | 0.0031739 | 0.00079546 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1061-182_0_4_load_33 | 71 | 0.0046572 | 0.0011672 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1061-182_0_4_load_104 | 73 | 0.0029937 | 0.0007503 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1061-182_0_4_load_122 | 75 | 0.0026251 | 0.0006579 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1061-182_0_4_load_74 | 76 | 0.0045266 | 0.0011345 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1061-182_0_4_load_105 | 77 | 0.004303 | 0.0010784 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1061-182_0_4_load_83 | 78 | 0.0050737 | 0.0012716 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1061-182_0_4_load_78 | 79 | 0.0030079 | 0.00075385 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1061-182_0_4_load_75 | 80 | 0.0023262 | 0.000583 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1061-182_0_4_load_121 | 81 | 0.001766 | 0.00044261 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1061-182_0_4_load_123 | 82 | 0.005326 | 0.0013348 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1061-182_0_4_load_35 | 84 | 0.0031289 | 0.00078417 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1061-182_0_4_load_36 | 85 | 0.002462 | 0.00061704 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1061-182_0_4_load_37 | 86 | 0.0024311 | 0.00060929 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1061-182_0_4_load_81 | 89 | 0.0019136 | 0.00047959 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1061-182_0_4_load_118 | 91 | 0.0070245 | 0.0017605 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1061-182_0_4_load_103 | 92 | 0.0094568 | 0.0023701 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1061-182_0_4_load_120 | 96 | 0.0028075 | 0.00070364 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1061-182_0_4_load_58 | 98 | 0.0029158 | 0.00073077 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1061-182_0_4_load_55 | 99 | 0.0045633 | 0.0011437 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1061-182_0_4_load_52 | 100 | 0.0065764 | 0.0016482 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1061-182_0_4_load_53 | 101 | 0.016605 | 0.0041617 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1061-182_0_4_load_56 | 102 | 0.0023778 | 0.00059593 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1061-182_0_4_load_63 | 104 | 0.01182 | 0.0029624 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1061-182_0_4_load_115 | 105 | 0.011443 | 0.0028678 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1061-182_0_4_load_116 | 106 | 0.007258 | 0.001819 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1061-182_0_4_load_64 | 107 | 0.012256 | 0.0030716 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1061-182_0_4_load_128 | 108 | 0.0031731 | 0.00079525 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1061-182_0_4_load_77 | 109 | 0.0079047 | 0.0019811 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1061-182_0_4_load_80 | 110 | 0.0055504 | 0.0013911 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1061-182_0_4_load_84 | 111 | 0.0039845 | 0.00099861 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1061-182_0_4_load_97 | 112 | 0.0080804 | 0.0020251 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1061-182_0_4_load_117 | 114 | 0.010444 | 0.0026175 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1061-182_0_4_load_111 | 117 | 0.015164 | 0.0038005 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1061-182_0_4_load_129 | 118 | 0.0021906 | 0.00054902 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1061-182_0_4_load_132 | 119 | 0.0018702 | 0.00046872 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1061-182_0_4_load_119 | 120 | 0.010341 | 0.0025916 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1061-182_0_4_load_110 | 121 | 0.0051282 | 0.0012852 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1061-182_0_4_load_124 | 122 | 0.0025749 | 0.00064533 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1061-182_0_4_load_125 | 123 | 0.002479 | 0.00062131 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1061-182_0_4_load_127 | 124 | 0.0016268 | 0.00040772 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1061-182_0_4_load_130 | 125 | 0.0018328 | 0.00045934 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-182_0_4_line_0 |  | 0 | 1 | 0.011957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-182_0_4_line_1 |  | 1 | 2 | 0.003975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-182_0_4_line_2 |  | 1 | 3 | 0.01056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-182_0_4_line_3 |  | 2 | 4 | 0.031892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-182_0_4_line_4 |  | 3 | 8 | 0.034662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-182_0_4_line_5 |  | 4 | 13 | 0.0012521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-182_0_4_line_6 |  | 5 | 6 | 0.014336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-182_0_4_line_7 |  | 5 | 7 | 0.009032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-182_0_4_line_8 |  | 6 | 14 | 0.0057642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-182_0_4_line_9 |  | 7 | 18 | 0.012315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-182_0_4_line_10 |  | 8 | 9 | 0.019017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1061-182_0_4_line_11 |  | 8 | 10 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-182_0_4_line_12 |  | 9 | 11 | 0.020321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1061-182_0_4_line_13 |  | 9 | 12 | 0.015854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-182_0_4_line_14 |  | 10 | 38 | 0.023169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-182_0_4_line_15 |  | 10 | 29 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1061-182_0_4_line_16 |  | 11 | 106 | 0.029994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1061-182_0_4_line_17 |  | 15 | 16 | 0.028074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-182_0_4_line_18 |  | 15 | 17 | 0.0031373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-182_0_4_line_19 |  | 16 | 112 | 0.011396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-182_0_4_line_20 |  | 16 | 113 | 0.02852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-182_0_4_line_21 |  | 16 | 63 | 0.017446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-182_0_4_line_22 |  | 17 | 20 | 0.0096258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-182_0_4_line_23 |  | 18 | 25 | 0.012443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-182_0_4_line_24 |  | 19 | 20 | 0.020076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-182_0_4_line_25 |  | 19 | 21 | 0.0015255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-182_0_4_line_26 |  | 21 | 22 | 0.015812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-182_0_4_line_27 |  | 21 | 23 | 0.018517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-182_0_4_line_28 |  | 22 | 24 | 0.0012699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-182_0_4_line_29 |  | 23 | 25 | 0.010535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-182_0_4_line_30 |  | 26 | 27 | 0.017581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1061-182_0_4_line_31 |  | 26 | 28 | 0.0082398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1061-182_0_4_line_32 |  | 27 | 29 | 0.014017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_1061-182_0_4_line_33 |  | 28 | 30 | 0.005705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1061-182_0_4_line_34 |  | 28 | 31 | 0.018814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1061-182_0_4_line_35 |  | 30 | 33 | 0.008018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1061-182_0_4_line_36 |  | 30 | 36 | 0.014503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1061-182_0_4_line_37 |  | 31 | 37 | 0.021721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1061-182_0_4_line_38 |  | 32 | 33 | 0.004736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1061-182_0_4_line_39 |  | 32 | 34 | 0.0033056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1061-182_0_4_line_40 |  | 32 | 35 | 0.044643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1061-182_0_4_line_41 |  | 33 | 39 | 0.03373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_1061-182_0_4_line_42 |  | 35 | 40 | 0.01732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1061-182_0_4_line_43 |  | 37 | 41 | 0.024636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_1061-182_0_4_line_44 |  | 38 | 107 | 0.0053479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1061-182_0_4_line_45 |  | 39 | 99 | 0.021429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1061-182_0_4_line_46 |  | 41 | 74 | 0.003547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_1061-182_0_4_line_47 |  | 42 | 43 | 0.041844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1061-182_0_4_line_48 |  | 43 | 46 | 0.003523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1061-182_0_4_line_49 |  | 43 | 47 | 0.006451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1061-182_0_4_line_50 |  | 44 | 45 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1061-182_0_4_line_51 |  | 45 | 48 | 0.002952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1061-182_0_4_line_52 |  | 45 | 49 | 0.03572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1061-182_0_4_line_53 |  | 46 | 50 | 0.029329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1061-182_0_4_line_54 |  | 47 | 54 | 0.014344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1061-182_0_4_line_55 |  | 47 | 55 | 0.019847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1061-182_0_4_line_56 |  | 48 | 56 | 0.0096251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1061-182_0_4_line_57 |  | 48 | 57 | 0.015201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1061-182_0_4_line_58 |  | 49 | 58 | 0.031268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1061-182_0_4_line_59 |  | 50 | 61 | 0.021951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1061-182_0_4_line_60 |  | 51 | 52 | 0.0022605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_1061-182_0_4_line_61 |  | 51 | 53 | 0.03048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_1061-182_0_4_line_62 |  | 52 | 62 | 0.028121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1061-182_0_4_line_63 |  | 53 | 58 | 0.003923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1061-182_0_4_line_64 |  | 53 | 63 | 0.01197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1061-182_0_4_line_65 |  | 54 | 64 | 0.024519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1061-182_0_4_line_66 |  | 55 | 65 | 0.019422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1061-182_0_4_line_67 |  | 56 | 91 | 0.023821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1061-182_0_4_line_68 |  | 58 | 93 | 0.005404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1061-182_0_4_line_69 |  | 59 | 60 | 0.029318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1061-182_0_4_line_70 |  | 60 | 96 | 0.0090752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1061-182_0_4_line_71 |  | 60 | 94 | 0.006685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1061-182_0_4_line_72 |  | 62 | 103 | 0.013512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_1061-182_0_4_line_73 |  | 64 | 94 | 0.022933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1061-182_0_4_line_74 |  | 65 | 121 | 0.0095558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1061-182_0_4_line_75 |  | 66 | 67 | 0.013634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_1061-182_0_4_line_76 |  | 66 | 68 | 0.020067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1061-182_0_4_line_77 |  | 67 | 69 | 0.013528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_1061-182_0_4_line_78 |  | 68 | 70 | 0.023458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1061-182_0_4_line_79 |  | 68 | 71 | 0.01422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1061-182_0_4_line_80 |  | 68 | 72 | 0.003577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_1061-182_0_4_line_81 |  | 69 | 73 | 0.019642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1061-182_0_4_line_82 |  | 69 | 74 | 0.0099659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_1061-182_0_4_line_83 |  | 70 | 75 | 0.011795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1061-182_0_4_line_84 |  | 71 | 76 | 0.025193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1061-182_0_4_line_85 |  | 72 | 77 | 0.018542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1061-182_0_4_line_86 |  | 72 | 78 | 0.04726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_1061-182_0_4_line_87 |  | 74 | 79 | 0.022468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1061-182_0_4_line_88 |  | 74 | 80 | 0.01925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1061-182_0_4_line_89 |  | 75 | 81 | 0.0017731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1061-182_0_4_line_90 |  | 77 | 82 | 0.004419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1061-182_0_4_line_91 |  | 78 | 83 | 0.0093939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_1061-182_0_4_line_92 |  | 80 | 109 | 0.013552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1061-182_0_4_line_93 |  | 83 | 111 | 0.020835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1061-182_0_4_line_94 |  | 83 | 110 | 0.014603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_1061-182_0_4_line_95 |  | 84 | 85 | 0.021843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1061-182_0_4_line_96 |  | 84 | 86 | 0.0308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1061-182_0_4_line_97 |  | 85 | 87 | 0.010202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1061-182_0_4_line_98 |  | 87 | 88 | 0.003774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1061-182_0_4_line_99 |  | 88 | 89 | 0.01005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1061-182_0_4_line_100 |  | 88 | 90 | 0.057958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1061-182_0_4_line_101 |  | 89 | 110 | 0.011965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_1061-182_0_4_line_102 |  | 90 | 101 | 0.067249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1061-182_0_4_line_103 |  | 91 | 120 | 0.0010222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1061-182_0_4_line_104 |  | 92 | 93 | 0.019906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1061-182_0_4_line_105 |  | 94 | 95 | 0.018718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1061-182_0_4_line_106 |  | 95 | 97 | 0.052805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1061-182_0_4_line_107 |  | 95 | 98 | 0.027598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1061-182_0_4_line_108 |  | 97 | 108 | 0.021461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1061-182_0_4_line_109 |  | 98 | 102 | 0.025432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
110 | LV_1061-182_0_4_line_110 |  | 99 | 102 | 0.026433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_1061-182_0_4_line_111 |  | 100 | 101 | 0.028529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1061-182_0_4_line_112 |  | 103 | 104 | 0.016083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_1061-182_0_4_line_113 |  | 104 | 105 | 0.034153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_1061-182_0_4_line_114 |  | 105 | 106 | 0.034968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_1061-182_0_4_line_115 |  | 108 | 118 | 0.014767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1061-182_0_4_line_116 |  | 108 | 119 | 0.143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1061-182_0_4_line_117 |  | 113 | 114 | 0.0063703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1061-182_0_4_line_118 |  | 114 | 115 | 0.026128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1061-182_0_4_line_119 |  | 115 | 116 | 0.011169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1061-182_0_4_line_120 |  | 116 | 117 | 0.0316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1061-182_0_4_line_121 |  | 118 | 125 | 0.0081719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1061-182_0_4_line_122 |  | 122 | 123 | 0.01424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1061-182_0_4_line_123 |  | 123 | 124 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1061-182_0_4_line_124 |  | 124 | 125 | 0.0086233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-182_0_4_trafo_115 | 0.63 MVA 20/0.4 kV | 126 | 105 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2665036.475 | 1210924.0298 | 2665041.0749 | 1210912.9924
1 | 2665036.475 | 1210924.0298 | 2665040.3481 | 1210924.9725
2 | 2665036.475 | 1210924.0298 | 2665032.8937 | 1210933.9635
3 | 2665040.3481 | 1210924.9725 | 2665042.4702 | 1210925.496 | 2665041.946 | 1210930.3599 | 2665047.6291 | 1210931.8784 | 2665048.2993 | 1210929.6621 | 2665053.3966 | 1210931.2408 | 2665052.3103 | 1210933.9862 | 2665060.3961 | 1210935.9774
4 | 2665027.8157 | 1210968.2514 | 2665032.8937 | 1210933.9635
5 | 2665060.3961 | 1210935.9774 | 2665061.6119 | 1210936.2767
6 | 2665110.0761 | 1210983.958 | 2665097.7282 | 1210976.6752
7 | 2665110.0761 | 1210983.958 | 2665112.4321 | 1210985.3401 | 2665118.4041 | 1210987.3479
8 | 2665092.7632 | 1210973.7469 | 2665097.7282 | 1210976.6752
9 | 2665118.4041 | 1210987.3479 | 2665130.0773 | 1210991.2725
10 | 2665027.8157 | 1210968.2514 | 2665031.0664 | 1210969.1207 | 2665032.4227 | 1210969.4913 | 2665033.6193 | 1210974.0516 | 2665036.0342 | 1210983.2724
11 | 2665026.28 | 1210980.8535 | 2665027.8157 | 1210968.2514
12 | 2665036.0342 | 1210983.2724 | 2665040.8337 | 1210994.0313 | 2665048.4482 | 1210997.8982
13 | 2665036.0342 | 1210983.2724 | 2665047.6728 | 1210982.9213 | 2665051.8807 | 1210982.7944
14 | 2665026.28 | 1210980.8535 | 2665016.6001 | 1210979.2916 | 2665004.6859 | 1210974.9369 | 2665004.0869 | 1210974.6172
15 | 2665026.28 | 1210980.8535 | 2665025.4034 | 1210988.0706 | 2665028.8751 | 1211000.0269
16 | 2665048.4482 | 1210997.8982 | 2665055.5333 | 1211001.4961 | 2665075.2419 | 1211011.3789
17 | 2665228.6646 | 1211024.4111 | 2665201.9822 | 1211015.4474
18 | 2665201.9822 | 1211015.4474 | 2665199.0085 | 1211014.4476
19 | 2665228.6646 | 1211024.4111 | 2665229.7576 | 1211020.365 | 2665224.7742 | 1211019.4989 | 2665225.056 | 1211017.3563
20 | 2665228.6646 | 1211024.4111 | 2665234.5251 | 1211026.3764 | 2665242.5545 | 1211023.8849 | 2665251.7358 | 1211026.5647 | 2665250.5547 | 1211029.6314 | 2665250.1637 | 1211030.6389
21 | 2665228.6646 | 1211024.4111 | 2665226.7422 | 1211027.1696 | 2665224.5286 | 1211033.616 | 2665223.2257 | 1211037.4041 | 2665222.318 | 1211040.5369
22 | 2665189.8845 | 1211011.3801 | 2665199.0085 | 1211014.4476
23 | 2665141.8718 | 1210995.2378 | 2665130.0773 | 1210991.2725
24 | 2665170.8549 | 1211004.9821 | 2665189.8845 | 1211011.3801
25 | 2665169.409 | 1211004.496 | 2665170.8549 | 1211004.9821
26 | 2665169.409 | 1211004.496 | 2665165.0646 | 1211019.6994
27 | 2665169.409 | 1211004.496 | 2665151.8576 | 1210998.5951
28 | 2665164.7157 | 1211020.9204 | 2665165.0646 | 1211019.6994
29 | 2665151.8576 | 1210998.5951 | 2665141.8718 | 1210995.2378
30 | 2665036.8658 | 1211011.5433 | 2665033.8432 | 1211013.456 | 2665033.2998 | 1211013.8058 | 2665034.2464 | 1211015.5061 | 2665035.2525 | 1211017.3182 | 2665035.6287 | 1211021.8473 | 2665035.1686 | 1211026.6191
31 | 2665039.6053 | 1211033.5089 | 2665036.9436 | 1211029.4996 | 2665035.1489 | 1211026.8229 | 2665035.1686 | 1211026.6191
32 | 2665036.8658 | 1211011.5433 | 2665035.9156 | 1211010.1765 | 2665028.8751 | 1211000.0269
33 | 2665039.6053 | 1211033.5089 | 2665042.7756 | 1211038.2574
34 | 2665039.6053 | 1211033.5089 | 2665038.5952 | 1211034.1427 | 2665035.1334 | 1211036.6065 | 2665031.7805 | 1211040.9281 | 2665029.1726 | 1211048.3884
35 | 2665042.7756 | 1211038.2574 | 2665044.7324 | 1211037.9119 | 2665048.1793 | 1211038.2163 | 2665050.6402 | 1211039.0325
36 | 2665042.7756 | 1211038.2574 | 2665041.6184 | 1211038.4561 | 2665039.0809 | 1211039.7848 | 2665035.0825 | 1211043.3656 | 2665033.8104 | 1211045.731 | 2665033.043 | 1211048.0172
37 | 2665029.1726 | 1211048.3884 | 2665022.0048 | 1211068.8921
38 | 2665054.7395 | 1211036.6424 | 2665051.1296 | 1211038.7488 | 2665050.6402 | 1211039.0325
39 | 2665054.7395 | 1211036.6424 | 2665057.1564 | 1211035.2234 | 2665057.5923 | 1211034.9725
40 | 2665054.7395 | 1211036.6424 | 2665069.5704 | 1211062.0086 | 2665076.218 | 1211075.7435
41 | 2665050.6402 | 1211039.0325 | 2665053.7803 | 1211040.9791 | 2665056.2415 | 1211043.8632 | 2665066.2212 | 1211063.9065 | 2665067.8787 | 1211067.3853
42 | 2665083.7637 | 1211091.3339 | 2665076.218 | 1211075.7435
43 | 2665008.1226 | 1211088.4218 | 2665010.7525 | 1211086.9829 | 2665014.762 | 1211083.0686 | 2665017.965 | 1211078.5563 | 2665019.9674 | 1211074.7202 | 2665022.0048 | 1211068.8921
44 | 2664999.3688 | 1210972.0991 | 2665004.0869 | 1210974.6172
45 | 2665077.096 | 1211086.7304 | 2665067.8787 | 1211067.3853
46 | 2665010.2729 | 1211091.2469 | 2665008.1226 | 1211088.4218
47 | 2665146.6998 | 1211082.596 | 2665149.8959 | 1211081.4969 | 2665156.3033 | 1211081.4001 | 2665161.2704 | 1211083.0554 | 2665165.717 | 1211086.4393 | 2665168.7319 | 1211091.4976 | 2665172.0045 | 1211106.3536 | 2665172.014 | 1211106.4849
48 | 2665146.6998 | 1211082.596 | 2665147.6461 | 1211085.0189 | 2665147.9786 | 1211085.8787
49 | 2665141.5212 | 1211086.3863 | 2665145.8836 | 1211082.8762 | 2665146.6998 | 1211082.596
50 | 2665225.7096 | 1211114.6343 | 2665225.2907 | 1211120.978 | 2665222.1714 | 1211126.3188
51 | 2665225.7096 | 1211114.6343 | 2665228.6382 | 1211115.0666
52 | 2665225.7096 | 1211114.6343 | 2665224.114 | 1211106.2784 | 2665220.4006 | 1211098.3885 | 2665215.6587 | 1211086.5627 | 2665215.901 | 1211080.8159
53 | 2665147.9786 | 1211085.8787 | 2665150.0001 | 1211085.1781 | 2665153.7193 | 1211084.8963 | 2665157.2229 | 1211085.5683 | 2665160.4985 | 1211086.9271 | 2665163.3406 | 1211089.0261 | 2665165.7537 | 1211092.121 | 2665167.1418 | 1211095.8385 | 2665167.8843 | 1211100.702
54 | 2665141.5212 | 1211086.3863 | 2665133.3472 | 1211098.1733
55 | 2665141.5212 | 1211086.3863 | 2665123.6113 | 1211077.8344
56 | 2665228.6382 | 1211115.0666 | 2665238.1586 | 1211116.4829
57 | 2665228.6382 | 1211115.0666 | 2665228.3384 | 1211118.8545 | 2665227.2792 | 1211123.2901 | 2665225.2136 | 1211128.026 | 2665224.2987 | 1211129.4282
58 | 2665223.2183 | 1211050.5899 | 2665216.1923 | 1211073.9052 | 2665215.901 | 1211080.8159
59 | 2665167.8843 | 1211100.702 | 2665170.17 | 1211115.6726 | 2665171.8557 | 1211122.2676
60 | 2665191.5987 | 1211064.3529 | 2665189.3452 | 1211064.5311
61 | 2665191.5987 | 1211064.3529 | 2665219.6142 | 1211052.1626
62 | 2665163.4848 | 1211055.6299 | 2665182.3346 | 1211065.0855 | 2665189.3452 | 1211064.5311
63 | 2665223.2183 | 1211050.5899 | 2665219.6142 | 1211052.1626
64 | 2665219.6142 | 1211052.1626 | 2665220.1141 | 1211048.1434 | 2665222.318 | 1211040.5369
65 | 2665119.3748 | 1211118.3216 | 2665133.3472 | 1211098.1733
66 | 2665123.6113 | 1211077.8344 | 2665106.085 | 1211069.4657
67 | 2665260.8906 | 1211123.3271 | 2665243.964 | 1211117.3466 | 2665238.1586 | 1211116.4829
68 | 2665228.3517 | 1211052.3249 | 2665227.2917 | 1211051.9686 | 2665223.2183 | 1211050.5899
69 | 2665112.8885 | 1211138.4391 | 2665113.9301 | 1211134.915 | 2665116.0513 | 1211130.6466 | 2665127.5494 | 1211113.2213
70 | 2665112.8885 | 1211138.4391 | 2665115.0118 | 1211138.8514 | 2665119.3449 | 1211140.7999 | 2665121.137 | 1211142.0079
71 | 2665106.3062 | 1211137.1665 | 2665112.8885 | 1211138.4391
72 | 2665151.4074 | 1211049.5716 | 2665163.4848 | 1211055.6299
73 | 2665106.3062 | 1211137.1665 | 2665119.3748 | 1211118.3216
74 | 2665097.4618 | 1211065.3481 | 2665106.085 | 1211069.4657
75 | 2664987.6867 | 1211094.8142 | 2664987.6867 | 1211094.8142 | 2664979.7272 | 1211091.6034 | 2664975.8489 | 1211089.0485 | 2664975.555 | 1211088.7676
76 | 2664965.0534 | 1211072.0205 | 2664966.2718 | 1211075.9695 | 2664968.3041 | 1211079.8607 | 2664972.2238 | 1211085.5847 | 2664975.555 | 1211088.7676
77 | 2665001.0983 | 1211094.927 | 2664999.4901 | 1211095.3654 | 2664992.0335 | 1211095.5176 | 2664987.6867 | 1211094.8142
78 | 2664965.0534 | 1211072.0205 | 2664942.1803 | 1211077.5082
79 | 2664965.0534 | 1211072.0205 | 2664964.4075 | 1211067.1327 | 2664965.3802 | 1211057.8942
80 | 2664965.0534 | 1211072.0205 | 2664968.5429 | 1211071.1913
81 | 2664999.1687 | 1211114.3958 | 2665001.4242 | 1211097.0986 | 2665001.0983 | 1211094.927
82 | 2665001.0983 | 1211094.927 | 2665003.3772 | 1211094.3182 | 2665006.2048 | 1211093.5596 | 2665010.2729 | 1211091.2469
83 | 2664942.1803 | 1211077.5082 | 2664938.4421 | 1211088.6952
84 | 2664965.3802 | 1211057.8942 | 2664966.891 | 1211043.5452 | 2664967.0938 | 1211037.4882 | 2664965.8579 | 1211032.9494
85 | 2664968.5429 | 1211071.1913 | 2664986.0869 | 1211065.1897
86 | 2664968.5429 | 1211071.1913 | 2664967.946 | 1211065.9927 | 2664970.3199 | 1211037.1231 | 2664968.7037 | 1211029.2228 | 2664966.2519 | 1211024.8692
87 | 2665010.2729 | 1211091.2469 | 2665012.5668 | 1211089.9489 | 2665018.8142 | 1211084.3024 | 2665024.2067 | 1211074.2459
88 | 2665010.2729 | 1211091.2469 | 2665021.9106 | 1211106.581
89 | 2664937.8802 | 1211090.3769 | 2664938.4421 | 1211088.6952
90 | 2664987.8173 | 1211061.2061 | 2664987.0192 | 1211064.0103 | 2664986.0869 | 1211065.1897
91 | 2664960.01 | 1211018.0547 | 2664964.4766 | 1211021.7167 | 2664966.2519 | 1211024.8692
92 | 2665032.9229 | 1211113.185 | 2665025.3837 | 1211111.1571 | 2665021.9106 | 1211106.581
93 | 2664960.01 | 1211018.0547 | 2664970.5009 | 1211008.652 | 2664977.0407 | 1211006.9922
94 | 2664960.01 | 1211018.0547 | 2664953.7328 | 1211014.5731 | 2664951.3668 | 1211013.4133 | 2664948.5861 | 1211012.6492 | 2664946.71 | 1211012.311
95 | 2664920.5551 | 1211027.3252 | 2664909.9562 | 1211046.4247
96 | 2664895.0112 | 1211073.3559 | 2664909.9562 | 1211046.4247
97 | 2664927.5316 | 1211020.0024 | 2664924.3429 | 1211022.5137 | 2664921.1406 | 1211026.2701 | 2664920.5551 | 1211027.3252
98 | 2664925.6369 | 1211016.7354 | 2664927.0392 | 1211019.1521 | 2664927.5316 | 1211020.0024
99 | 2664925.6369 | 1211016.7354 | 2664927.657 | 1211015.4566 | 2664931.0238 | 1211014.0368 | 2664934.616 | 1211012.864 | 2664934.8387 | 1211012.8242
100 | 2664925.6369 | 1211016.7354 | 2664923.9884 | 1211013.8824 | 2664922.8867 | 1211012.4695 | 2664922.1224 | 1211012.1721 | 2664920.6268 | 1211012.734 | 2664919.5427 | 1211012.4887 | 2664916.6963 | 1211003.1075 | 2664913.4525 | 1210993.9222 | 2664909.3942 | 1210986.2511 | 2664904.4514 | 1210976.7693 | 2664898.8019 | 1210967.9691
101 | 2664946.71 | 1211012.311 | 2664945.5674 | 1211012.1049 | 2664941.9826 | 1211011.9103 | 2664938.9561 | 1211012.0885 | 2664934.8387 | 1211012.8242
102 | 2664898.8019 | 1210967.9691 | 2664901.8477 | 1210965.3228 | 2664910.6946 | 1210956.8472 | 2664928.6475 | 1210936.341 | 2664944.6974 | 1210918.8924
103 | 2665260.8906 | 1211123.3271 | 2665261.8544 | 1211123.6676
104 | 2665228.3517 | 1211052.3249 | 2665222.0622 | 1211071.2116
105 | 2665106.3062 | 1211137.1665 | 2665111.6274 | 1211155.1134
106 | 2665111.6274 | 1211155.1134 | 2665113.3913 | 1211154.3321 | 2665114.3612 | 1211153.898 | 2665115.7664 | 1211157.4377 | 2665131.0525 | 1211196.0394 | 2665131.7488 | 1211200.4719
107 | 2665111.6274 | 1211155.1134 | 2665109.8253 | 1211155.9053 | 2665108.9471 | 1211156.296 | 2665100.5144 | 1211135.8803 | 2665099.4048 | 1211133.5515
108 | 2665131.7488 | 1211200.4719 | 2665132.2669 | 1211203.8352 | 2665131.7636 | 1211206.776 | 2665131.6765 | 1211211.9671 | 2665133.3262 | 1211216.7769 | 2665136.3243 | 1211220.523
109 | 2665088.4657 | 1211110.5928 | 2665099.4048 | 1211133.5515
110 | 2665077.096 | 1211086.7304 | 2665088.4657 | 1211110.5928
111 | 2664964.0327 | 1210897.9146 | 2664953.6266 | 1210909.185 | 2664944.6974 | 1210918.8924
112 | 2665151.4074 | 1211049.5716 | 2665137.0305 | 1211042.3624
113 | 2665137.0305 | 1211042.3624 | 2665106.5006 | 1211027.0534
114 | 2665106.5006 | 1211027.0534 | 2665075.2419 | 1211011.3789
115 | 2665136.3243 | 1211220.523 | 2665137.4645 | 1211221.9475 | 2665141.5658 | 1211225.6279 | 2665146.8112 | 1211228.9316 | 2665147.9059 | 1211229.4986
116 | 2665136.3243 | 1211220.523 | 2665012.6781 | 1211292.3634
117 | 2665250.1637 | 1211030.6389 | 2665252.8719 | 1211031.7692 | 2665255.7376 | 1211033.6643
118 | 2665276.1866 | 1211049.8575 | 2665262.65 | 1211038.2356 | 2665255.7376 | 1211033.6643
119 | 2665271.3344 | 1211059.9217 | 2665276.1866 | 1211049.8575
120 | 2665271.3344 | 1211059.9217 | 2665288.7389 | 1211069.4735 | 2665286.809 | 1211081.0609
121 | 2665147.9059 | 1211229.4986 | 2665155.1622 | 1211233.2571
122 | 2665186.0562 | 1211246.8784 | 2665173.1476 | 1211241.6603 | 2665172.8588 | 1211241.5295
123 | 2665162.9155 | 1211237.0248 | 2665172.8588 | 1211241.5295
124 | 2665162.9155 | 1211237.0248 | 2665159.0904 | 1211235.2918 | 2665155.1622 | 1211233.2571

## bus_geodata
| x | y | coords
0 | 2665041.0749 | 1210912.9924
1 | 2665036.475 | 1210924.0298
2 | 2665040.3481 | 1210924.9725
3 | 2665032.8937 | 1210933.9635
4 | 2665060.3961 | 1210935.9774
5 | 2665110.0761 | 1210983.958
6 | 2665097.7282 | 1210976.6752
7 | 2665118.4041 | 1210987.3479
8 | 2665027.8157 | 1210968.2514
9 | 2665036.0342 | 1210983.2724
10 | 2665026.28 | 1210980.8535
11 | 2665048.4483 | 1210997.8982
12 | 2665051.8807 | 1210982.7944
13 | 2665061.6119 | 1210936.2767
14 | 2665092.7632 | 1210973.7469
15 | 2665201.9822 | 1211015.4474
16 | 2665228.6646 | 1211024.4111
17 | 2665199.0085 | 1211014.4476
18 | 2665130.0773 | 1210991.2725
19 | 2665170.8549 | 1211004.9821
20 | 2665189.8845 | 1211011.3801
21 | 2665169.409 | 1211004.496
22 | 2665165.0646 | 1211019.6994
23 | 2665151.8576 | 1210998.5951
24 | 2665164.7157 | 1211020.9204
25 | 2665141.8718 | 1210995.2379
26 | 2665035.1686 | 1211026.6191
27 | 2665036.8658 | 1211011.5433
28 | 2665039.6053 | 1211033.5089
29 | 2665028.8751 | 1211000.0269
30 | 2665042.7756 | 1211038.2574
31 | 2665029.1726 | 1211048.3884
32 | 2665054.7395 | 1211036.6424
33 | 2665050.6402 | 1211039.0325
34 | 2665057.5923 | 1211034.9725
35 | 2665076.218 | 1211075.7435
36 | 2665033.043 | 1211048.0172
37 | 2665022.0048 | 1211068.8921
38 | 2665004.0869 | 1210974.6172
39 | 2665067.8787 | 1211067.3853
40 | 2665083.7637 | 1211091.3339
41 | 2665008.1226 | 1211088.4218
42 | 2665172.014 | 1211106.4849
43 | 2665146.6998 | 1211082.596
44 | 2665222.1714 | 1211126.3188
45 | 2665225.7096 | 1211114.6343
46 | 2665147.9786 | 1211085.8787
47 | 2665141.5212 | 1211086.3863
48 | 2665228.6382 | 1211115.0666
49 | 2665215.901 | 1211080.8159
50 | 2665167.8843 | 1211100.702
51 | 2665191.5987 | 1211064.3529
52 | 2665189.3452 | 1211064.5311
53 | 2665219.6142 | 1211052.1626
54 | 2665133.3472 | 1211098.1733
55 | 2665123.6113 | 1211077.8344
56 | 2665238.1586 | 1211116.4829
57 | 2665224.2987 | 1211129.4282
58 | 2665223.2183 | 1211050.5899
59 | 2665127.5494 | 1211113.2213
60 | 2665112.8885 | 1211138.4391
61 | 2665171.8557 | 1211122.2676
62 | 2665163.4848 | 1211055.6299
63 | 2665222.318 | 1211040.5369
64 | 2665119.3748 | 1211118.3216
65 | 2665106.085 | 1211069.4657
66 | 2664975.555 | 1211088.7676
67 | 2664987.6867 | 1211094.8142
68 | 2664965.0534 | 1211072.0205
69 | 2665001.0983 | 1211094.927
70 | 2664942.1803 | 1211077.5082
71 | 2664965.3802 | 1211057.8942
72 | 2664968.5429 | 1211071.1913
73 | 2664999.1687 | 1211114.3958
74 | 2665010.2729 | 1211091.2469
75 | 2664938.4421 | 1211088.6951
76 | 2664965.8579 | 1211032.9494
77 | 2664986.0869 | 1211065.1897
78 | 2664966.2519 | 1211024.8692
79 | 2665024.2067 | 1211074.2459
80 | 2665021.9106 | 1211106.581
81 | 2664937.8802 | 1211090.3769
82 | 2664987.8173 | 1211061.2061
83 | 2664960.01 | 1211018.0547
84 | 2664909.9562 | 1211046.4247
85 | 2664920.5551 | 1211027.3252
86 | 2664895.0112 | 1211073.3559
87 | 2664927.5316 | 1211020.0024
88 | 2664925.6369 | 1211016.7354
89 | 2664934.8387 | 1211012.8242
90 | 2664898.8019 | 1210967.9691
91 | 2665260.8906 | 1211123.3271
92 | 2665222.0622 | 1211071.2116
93 | 2665228.3517 | 1211052.3249
94 | 2665106.3062 | 1211137.1665
95 | 2665111.6274 | 1211155.1134
96 | 2665121.1369 | 1211142.0079
97 | 2665131.7488 | 1211200.4719
98 | 2665099.4048 | 1211133.5515
99 | 2665077.096 | 1211086.7303
100 | 2664964.0327 | 1210897.9146
101 | 2664944.6974 | 1210918.8924
102 | 2665088.4657 | 1211110.5928
103 | 2665151.4074 | 1211049.5716
104 | 2665137.0305 | 1211042.3624
105 | 2665106.5006 | 1211027.0534
106 | 2665075.2419 | 1211011.3789
107 | 2664999.3688 | 1210972.0991
108 | 2665136.3243 | 1211220.523
109 | 2665032.9229 | 1211113.185
110 | 2664946.71 | 1211012.311
111 | 2664977.0407 | 1211006.9922
112 | 2665225.056 | 1211017.3563
113 | 2665250.1637 | 1211030.6389
114 | 2665255.7376 | 1211033.6643
115 | 2665276.1866 | 1211049.8575
116 | 2665271.3344 | 1211059.9217
117 | 2665286.809 | 1211081.0609
118 | 2665147.9059 | 1211229.4986
119 | 2665012.6781 | 1211292.3634
120 | 2665261.8544 | 1211123.6676
121 | 2665097.4618 | 1211065.3481
122 | 2665186.0562 | 1211246.8784
123 | 2665172.8588 | 1211241.5295
124 | 2665162.9155 | 1211237.0248
125 | 2665155.1622 | 1211233.2571
126 | 2665151.4074 | 1211049.5716

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98573 | -0.27176 | 0.0085763 | 0.0021494
1 | 0.98583 | -0.26992 | 0 | 0
2 | 0.98576 | -0.27115 | 0 | 0
3 | 0.98608 | -0.26502 | 0.0053095 | 0.0013307
4 | 0.98526 | -0.28106 | 0.010128 | 0.0025383
5 | 0.97728 | -0.43802 | 0 | 0
6 | 0.97695 | -0.44441 | 0.0075425 | 0.0018903
7 | 0.97748 | -0.43399 | 0.0091371 | 0.00229
8 | 0.98707 | -0.24566 | 0 | 0
9 | 0.98933 | -0.20239 | 0 | 0
10 | 0.98575 | -0.2711 | 0 | 0
11 | 0.99181 | -0.1549 | 0.0043035 | 0.0010786
12 | 0.98921 | -0.20471 | 0.0082133 | 0.0020585
13 | 0.98525 | -0.28122 | 0.007174 | 0.001798
14 | 0.97686 | -0.44619 | 0.016891 | 0.0042333
15 | 0.98217 | -0.34226 | 0 | 0
16 | 0.98455 | -0.29605 | 0 | 0
17 | 0.9819 | -0.34744 | 0.006898 | 0.0017288
18 | 0.97787 | -0.42645 | 0.006001 | 0.001504
19 | 0.97975 | -0.38963 | 0.0079959 | 0.002004
20 | 0.98115 | -0.36214 | 0.008927 | 0.0022373
21 | 0.97965 | -0.39149 | 0 | 0
22 | 0.97941 | -0.39623 | 0.0093283 | 0.0023379
23 | 0.97877 | -0.40866 | 0.0050105 | 0.0012558
24 | 0.9794 | -0.3964 | 0.0071665 | 0.0017961
25 | 0.97833 | -0.41748 | 0.0064204 | 0.0016091
26 | 0.98093 | -0.36447 | 0.0033671 | 0.00084388
27 | 0.98257 | -0.33264 | 0 | 0
28 | 0.98017 | -0.37917 | 0 | 0
29 | 0.98387 | -0.30734 | 0.0042193 | 0.0010575
30 | 0.97992 | -0.38413 | 0 | 0
31 | 0.97929 | -0.39645 | 0.0037888 | 0.00094955
32 | 0.97952 | -0.39192 | 0 | 0
33 | 0.97958 | -0.39078 | 0 | 0
34 | 0.97951 | -0.39217 | 0.0042446 | 0.0010638
35 | 0.97915 | -0.39918 | 0.0030893 | 0.00077425
36 | 0.97986 | -0.38527 | 0.004332 | 0.0010857
37 | 0.9783 | -0.41568 | 0.0052682 | 0.0013203
38 | 0.98534 | -0.27912 | 0.0070252 | 0.0017607
39 | 0.97835 | -0.41477 | 0.0027426 | 0.00068737
40 | 0.97905 | -0.40102 | 0.0058596 | 0.0014686
41 | 0.97725 | -0.43636 | 0 | 0
42 | 0.97084 | -0.56231 | 0.0038351 | 0.00096115
43 | 0.97099 | -0.55934 | 0 | 0
44 | 0.98469 | -0.2935 | 0.010894 | 0.0027303
45 | 0.98482 | -0.29104 | 0 | 0
46 | 0.97097 | -0.55982 | 0 | 0
47 | 0.97106 | -0.558 | 0 | 0
48 | 0.98473 | -0.29279 | 0 | 0
49 | 0.98626 | -0.2629 | 0.0092901 | 0.0023283
50 | 0.97077 | -0.56382 | 0.0044042 | 0.0011038
51 | 0.99076 | -0.17607 | 0 | 0
52 | 0.99096 | -0.17217 | 0.010127 | 0.0025381
53 | 0.98802 | -0.22876 | 0 | 0
54 | 0.9715 | -0.54934 | 0.007042 | 0.0017649
55 | 0.97066 | -0.56588 | 0.0063803 | 0.0015991
56 | 0.98451 | -0.29717 | 0.0079232 | 0.0019857
57 | 0.98462 | -0.2949 | 0.0077122 | 0.0019329
58 | 0.9878 | -0.23315 | 0 | 0
59 | 0.97322 | -0.51541 | 0.0032772 | 0.00082135
60 | 0.97331 | -0.51364 | 0 | 0
61 | 0.9707 | -0.56503 | 0.002974 | 0.00074534
62 | 0.99361 | -0.12132 | 0.0063245 | 0.0015851
63 | 0.98656 | -0.25692 | 0.0065273 | 0.0016359
64 | 0.97241 | -0.53137 | 0.0040458 | 0.001014
65 | 0.97039 | -0.57129 | 0.0099488 | 0.0024934
66 | 0.97579 | -0.46495 | 0.0017111 | 0.00042884
67 | 0.97625 | -0.45589 | 0.0031739 | 0.00079546
68 | 0.97513 | -0.47799 | 0 | 0
69 | 0.97673 | -0.44651 | 0 | 0
70 | 0.97503 | -0.47988 | 0 | 0
71 | 0.975 | -0.48038 | 0.0046572 | 0.0011672
72 | 0.97503 | -0.47987 | 0 | 0
73 | 0.97667 | -0.44758 | 0.0029937 | 0.0007503
74 | 0.97709 | -0.43934 | 0 | 0
75 | 0.97498 | -0.48083 | 0.0026251 | 0.0006579
76 | 0.9749 | -0.48247 | 0.0045266 | 0.0011345
77 | 0.97486 | -0.48314 | 0.004303 | 0.0010784
78 | 0.97398 | -0.50057 | 0.0050737 | 0.0012716
79 | 0.97703 | -0.44057 | 0.0030079 | 0.00075385
80 | 0.97691 | -0.44293 | 0.0023262 | 0.000583
81 | 0.97498 | -0.48088 | 0.001766 | 0.00044261
82 | 0.97484 | -0.48357 | 0.005326 | 0.0013348
83 | 0.97379 | -0.50425 | 0 | 0
84 | 0.97283 | -0.52317 | 0.0031289 | 0.00078417
85 | 0.97294 | -0.52093 | 0.002462 | 0.00061704
86 | 0.97276 | -0.52454 | 0.0024311 | 0.00060929
87 | 0.97302 | -0.51942 | 0 | 0
88 | 0.97305 | -0.51886 | 0 | 0
89 | 0.97334 | -0.51309 | 0.0019136 | 0.00047959
90 | 0.97179 | -0.54363 | 0 | 0
91 | 0.98413 | -0.30461 | 0.0070245 | 0.0017605
92 | 0.98758 | -0.23743 | 0.0094568 | 0.0023701
93 | 0.98775 | -0.23406 | 0 | 0
94 | 0.97334 | -0.51289 | 0 | 0
95 | 0.97422 | -0.49574 | 0 | 0
96 | 0.97328 | -0.51411 | 0.0028075 | 0.00070364
97 | 0.97344 | -0.51103 | 0 | 0
98 | 0.9759 | -0.46255 | 0.0029158 | 0.00073077
99 | 0.97759 | -0.42951 | 0.0045633 | 0.0011437
100 | 0.97016 | -0.57592 | 0.0065764 | 0.0016482
101 | 0.97034 | -0.57245 | 0.016605 | 0.0041617
102 | 0.97672 | -0.44661 | 0.0023778 | 0.00059593
103 | 0.99493 | -0.096227 | 0 | 0
104 | 0.99649 | -0.066448 | 0.01182 | 0.0029624
105 | 1 | 0 | -0.50795 | -0.13043
106 | 0.99554 | -0.084094 | 0.007258 | 0.001819
107 | 0.98528 | -0.2803 | 0.012256 | 0.0030716
108 | 0.97313 | -0.51725 | 0.0031731 | 0.00079525
109 | 0.97681 | -0.44489 | 0.0079047 | 0.0019811
110 | 0.97353 | -0.50945 | 0.0055504 | 0.0013911
111 | 0.97371 | -0.50578 | 0.0039845 | 0.00099861
112 | 0.98446 | -0.29771 | 0.0080804 | 0.0020251
113 | 0.98387 | -0.30919 | 0 | 0
114 | 0.98372 | -0.31213 | 0.010444 | 0.0026175
115 | 0.98336 | -0.31927 | 0 | 0
116 | 0.9832 | -0.32233 | 0 | 0
117 | 0.98276 | -0.33097 | 0.015164 | 0.0038005
118 | 0.97298 | -0.52016 | 0.0021906 | 0.00054902
119 | 0.97288 | -0.52218 | 0.0018702 | 0.00046872
120 | 0.98412 | -0.3048 | 0.010341 | 0.0025916
121 | 0.97034 | -0.5722 | 0.0051282 | 0.0012852
122 | 0.97277 | -0.5242 | 0.0025749 | 0.00064533
123 | 0.97281 | -0.52352 | 0.002479 | 0.00062131
124 | 0.97286 | -0.5225 | 0.0016268 | 0.00040772
125 | 0.97291 | -0.52144 | 0.0018328 | 0.00045934
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0085763 | -0.0021494 | 0.008577 | 0.0021497 | 7.5156e-07 | 3.2855e-07 | 0.012946 | 0.012946 | 0.012946 | 0.98573 | -0.27176 | 0.98583 | -0.26992 | 3.5567
1 | 0.017311 | 0.0043418 | -0.01731 | -0.0043412 | 1.0178e-06 | 6.0074e-07 | 0.026131 | 0.026131 | 0.026131 | 0.98583 | -0.26992 | 0.98576 | -0.27115 | 7.1789
2 | -0.025888 | -0.0064915 | 0.025894 | 0.0064952 | 6.0468e-06 | 3.7353e-06 | 0.039077 | 0.039077 | 0.039077 | 0.98583 | -0.26992 | 0.98608 | -0.26502 | 10.7355
3 | 0.01731 | 0.0043412 | -0.017302 | -0.0043363 | 8.1663e-06 | 4.8201e-06 | 0.026131 | 0.026131 | 0.026131 | 0.98576 | -0.27115 | 0.98526 | -0.28106 | 7.1789
4 | -0.031204 | -0.0078259 | 0.031233 | 0.0078439 | 2.8822e-05 | 1.8004e-05 | 0.047089 | 0.047089 | 0.047089 | 0.98608 | -0.26502 | 0.98707 | -0.24566 | 12.9367
5 | 0.007174 | 0.001798 | -0.007174 | -0.001798 | 5.5121e-08 | 1.9332e-08 | 0.010835 | 0.010835 | 0.010835 | 0.98526 | -0.28106 | 0.98525 | -0.28122 | 2.9766
6 | 0.024442 | 0.0061291 | -0.024435 | -0.0061245 | 7.4464e-06 | 4.5861e-06 | 0.037218 | 0.037218 | 0.037218 | 0.97728 | -0.43802 | 0.97695 | -0.44441 | 10.2246
7 | -0.024442 | -0.0061291 | 0.024447 | 0.006132 | 4.6915e-06 | 2.8893e-06 | 0.037218 | 0.037218 | 0.037218 | 0.97728 | -0.43802 | 0.97748 | -0.43399 | 10.2246
8 | 0.016893 | 0.0042342 | -0.016891 | -0.0042333 | 1.431e-06 | 8.4366e-07 | 0.025729 | 0.02573 | 0.02573 | 0.97695 | -0.44441 | 0.97686 | -0.44619 | 7.0686
9 | -0.033584 | -0.0084219 | 0.033596 | 0.0084295 | 1.2072e-05 | 7.5715e-06 | 0.051127 | 0.051127 | 0.051127 | 0.97748 | -0.43399 | 0.97787 | -0.42645 | 14.0458
10 | -0.25741 | -0.065472 | 0.25794 | 0.065816 | 0.00053787 | 0.00034375 | 0.38839 | 0.38838 | 0.38839 | 0.98707 | -0.24566 | 0.98933 | -0.20239 | 53.3496
11 | 0.22617 | 0.057628 | -0.2259 | -0.057451 | 0.00027731 | 0.00017715 | 0.3413 | 0.3413 | 0.3413 | 0.98707 | -0.24566 | 0.98575 | -0.2711 | 46.8813
12 | -0.26616 | -0.067875 | 0.26677 | 0.068266 | 0.00061189 | 0.00039108 | 0.40074 | 0.40074 | 0.40074 | 0.98933 | -0.20239 | 0.99181 | -0.1549 | 55.0467
13 | 0.0082142 | 0.0020588 | -0.0082133 | -0.0020585 | 9.0749e-07 | 3.7724e-07 | 0.012355 | 0.012355 | 0.012355 | 0.98933 | -0.20239 | 0.98921 | -0.20471 | 3.3942
14 | 0.019289 | 0.0048371 | -0.019282 | -0.0048327 | 7.3668e-06 | 4.4195e-06 | 0.029118 | 0.029118 | 0.029118 | 0.98575 | -0.2711 | 0.98534 | -0.27912 | 7.9996
15 | 0.20661 | 0.052614 | -0.20625 | -0.052384 | 0.00036035 | 0.00023012 | 0.31218 | 0.31218 | 0.31218 | 0.98575 | -0.2711 | 0.98387 | -0.30734 | 42.8816
16 | -0.27107 | -0.069345 | 0.27201 | 0.069941 | 0.00093248 | 0.00059601 | 0.4072 | 0.4072 | 0.4072 | 0.99181 | -0.1549 | 0.99554 | -0.084094 | 55.9335
17 | -0.091613 | -0.023074 | 0.091816 | 0.023203 | 0.00020293 | 0.00012952 | 0.13884 | 0.13884 | 0.13884 | 0.98217 | -0.34226 | 0.98455 | -0.29605 | 38.1422
18 | 0.091613 | 0.023074 | -0.091591 | -0.023059 | 2.2678e-05 | 1.4474e-05 | 0.13884 | 0.13884 | 0.13884 | 0.98217 | -0.34226 | 0.9819 | -0.34744 | 38.1422
19 | 0.0080811 | 0.0020254 | -0.0080804 | -0.0020251 | 6.3748e-07 | 2.6308e-07 | 0.012214 | 0.012214 | 0.012214 | 0.98455 | -0.29605 | 0.98446 | -0.29771 | 3.3554
20 | 0.025642 | 0.006438 | -0.025626 | -0.0064281 | 1.6066e-05 | 9.9197e-06 | 0.038758 | 0.038758 | 0.038758 | 0.98455 | -0.29605 | 0.98387 | -0.30919 | 10.6479
21 | -0.12554 | -0.031667 | 0.12577 | 0.031817 | 0.0002357 | 0.00015062 | 0.18981 | 0.18981 | 0.18981 | 0.98455 | -0.29605 | 0.98656 | -0.25692 | 52.1453
22 | 0.084693 | 0.02133 | -0.084633 | -0.021292 | 5.9496e-05 | 3.7956e-05 | 0.12838 | 0.12838 | 0.12838 | 0.9819 | -0.34744 | 0.98115 | -0.36214 | 35.2704
23 | -0.039597 | -0.0099335 | 0.039614 | 0.0099442 | 1.6943e-05 | 1.0688e-05 | 0.060258 | 0.060258 | 0.060258 | 0.97787 | -0.42645 | 0.97833 | -0.41748 | 16.5545
24 | -0.075607 | -0.018992 | 0.075706 | 0.019055 | 9.9299e-05 | 6.3298e-05 | 0.11485 | 0.11485 | 0.11485 | 0.97975 | -0.38963 | 0.98115 | -0.36214 | 31.551
25 | 0.067611 | 0.016988 | -0.067605 | -0.016984 | 6.0337e-06 | 3.8424e-06 | 0.1027 | 0.1027 | 0.1027 | 0.97975 | -0.38963 | 0.97965 | -0.39149 | 28.2147
26 | 0.016499 | 0.0041362 | -0.016495 | -0.004134 | 3.7239e-06 | 2.1843e-06 | 0.025061 | 0.025061 | 0.025061 | 0.97965 | -0.39149 | 0.97941 | -0.39623 | 6.8848
27 | 0.051106 | 0.012848 | -0.051065 | -0.012821 | 4.1858e-05 | 2.6556e-05 | 0.077641 | 0.077641 | 0.077641 | 0.97965 | -0.39149 | 0.97877 | -0.40866 | 21.33
28 | 0.0071666 | 0.0017961 | -0.0071665 | -0.0017961 | 5.6456e-08 | 2.0151e-08 | 0.010888 | 0.010888 | 0.010888 | 0.97941 | -0.39623 | 0.9794 | -0.3964 | 2.9913
29 | 0.046054 | 0.011566 | -0.046035 | -0.011553 | 1.9371e-05 | 1.2265e-05 | 0.070024 | 0.070024 | 0.070024 | 0.97877 | -0.40866 | 0.97833 | -0.41748 | 19.2373
30 | -0.20147 | -0.050973 | 0.20178 | 0.05117 | 0.00030825 | 0.00019683 | 0.3058 | 0.3058 | 0.3058 | 0.98093 | -0.36447 | 0.98257 | -0.33264 | 42.0051
31 | 0.19811 | 0.050129 | -0.19797 | -0.05004 | 0.00013969 | 8.9191e-05 | 0.30069 | 0.30069 | 0.30069 | 0.98093 | -0.36447 | 0.98017 | -0.37917 | 41.3035
32 | -0.20178 | -0.05117 | 0.20203 | 0.051327 | 0.00024577 | 0.00015694 | 0.3058 | 0.3058 | 0.3058 | 0.98257 | -0.33264 | 0.98387 | -0.30734 | 42.0051
33 | 0.096294 | 0.024347 | -0.096271 | -0.024333 | 2.2883e-05 | 1.4502e-05 | 0.14626 | 0.14626 | 0.14626 | 0.98017 | -0.37917 | 0.97992 | -0.38413 | 20.091
34 | 0.10167 | 0.025692 | -0.10159 | -0.025639 | 8.4127e-05 | 5.3367e-05 | 0.15443 | 0.15443 | 0.15443 | 0.98017 | -0.37917 | 0.97929 | -0.39645 | 21.2125
35 | 0.091939 | 0.023247 | -0.091909 | -0.023229 | 2.9333e-05 | 1.8571e-05 | 0.13968 | 0.13968 | 0.13968 | 0.97992 | -0.38413 | 0.97958 | -0.39078 | 19.1874
36 | 0.0043322 | 0.0010857 | -0.004332 | -0.0010857 | 2.3537e-07 | -3.206e-08 | 0.0065785 | 0.0065785 | 0.0065785 | 0.97992 | -0.38413 | 0.97986 | -0.38527 | 1.8073
37 | 0.0978 | 0.024689 | -0.09771 | -0.024632 | 9.0016e-05 | 5.7064e-05 | 0.14867 | 0.14867 | 0.14867 | 0.97929 | -0.39645 | 0.9783 | -0.41568 | 20.4218
38 | -0.013197 | -0.0033081 | 0.013198 | 0.0033085 | 7.1384e-07 | 3.9724e-07 | 0.020048 | 0.020048 | 0.020048 | 0.97952 | -0.39192 | 0.97958 | -0.39078 | 5.5078
39 | 0.0042446 | 0.0010638 | -0.0042446 | -0.0010638 | 5.1542e-08 | -8.622e-09 | 0.0064482 | 0.0064482 | 0.0064482 | 0.97952 | -0.39192 | 0.97951 | -0.39217 | 1.7715
40 | 0.0089525 | 0.0022443 | -0.0089494 | -0.0022429 | 3.0966e-06 | 1.4201e-06 | 0.0136 | 0.0136 | 0.0136 | 0.97952 | -0.39192 | 0.97915 | -0.39918 | 3.7364
41 | 0.078712 | 0.01992 | -0.078621 | -0.019863 | 9.0519e-05 | 5.7084e-05 | 0.11964 | 0.11964 | 0.11964 | 0.97958 | -0.39078 | 0.97835 | -0.41477 | 16.4335
42 | 0.0058601 | 0.0014687 | -0.0058596 | -0.0014686 | 5.1514e-07 | 1.1186e-07 | 0.0089056 | 0.0089057 | 0.0089057 | 0.97915 | -0.39918 | 0.97905 | -0.40102 | 2.4466
43 | 0.092442 | 0.023312 | -0.09235 | -0.023254 | 9.1389e-05 | 5.7871e-05 | 0.14066 | 0.14066 | 0.14066 | 0.9783 | -0.41568 | 0.97725 | -0.43636 | 19.3211
44 | 0.012257 | 0.003072 | -0.012256 | -0.0030716 | 6.8707e-07 | 3.7161e-07 | 0.018509 | 0.018509 | 0.018509 | 0.98534 | -0.27912 | 0.98528 | -0.2803 | 5.085
45 | 0.075878 | 0.019176 | -0.075825 | -0.019142 | 5.3567e-05 | 3.3745e-05 | 0.11546 | 0.11546 | 0.11546 | 0.97835 | -0.41477 | 0.97759 | -0.42951 | 15.8605
46 | 0.09235 | 0.023254 | -0.092337 | -0.023246 | 1.3158e-05 | 8.3322e-06 | 0.14066 | 0.14066 | 0.14066 | 0.97725 | -0.43636 | 0.97709 | -0.43934 | 19.3211
47 | -0.0038351 | -0.00096115 | 0.0038356 | 0.00096098 | 5.4214e-07 | -1.7053e-07 | 0.005878 | 0.0058778 | 0.005878 | 0.97084 | -0.56231 | 0.97099 | -0.55934 | 1.6148
48 | 0.0073799 | 0.0018496 | -0.0073798 | -0.0018495 | 1.6898e-07 | 6.4571e-08 | 0.01131 | 0.01131 | 0.01131 | 0.97099 | -0.55934 | 0.97097 | -0.55982 | 3.107
49 | -0.011216 | -0.0028106 | 0.011216 | 0.0028109 | 7.1462e-07 | 3.7756e-07 | 0.017187 | 0.017187 | 0.017187 | 0.97099 | -0.55934 | 0.97106 | -0.558 | 4.7218
50 | -0.010894 | -0.0027303 | 0.010895 | 0.0027309 | 1.2746e-06 | 6.5621e-07 | 0.016462 | 0.016462 | 0.016462 | 0.98469 | -0.2935 | 0.98482 | -0.29104 | 4.5226
51 | 0.033016 | 0.0082797 | -0.033013 | -0.0082779 | 2.755e-06 | 1.7256e-06 | 0.049887 | 0.049887 | 0.049887 | 0.98482 | -0.29104 | 0.98473 | -0.29279 | 13.7051
52 | -0.043911 | -0.011011 | 0.04397 | 0.011048 | 5.8967e-05 | 3.7284e-05 | 0.066349 | 0.066349 | 0.066349 | 0.98482 | -0.29104 | 0.98626 | -0.2629 | 18.2277
53 | 0.0073798 | 0.0018495 | -0.0073784 | -0.001849 | 1.4068e-06 | 5.3765e-07 | 0.01131 | 0.01131 | 0.01131 | 0.97097 | -0.55982 | 0.97077 | -0.56382 | 3.1071
54 | -0.032686 | -0.0081958 | 0.032699 | 0.0082043 | 1.3495e-05 | 8.4591e-06 | 0.050088 | 0.050088 | 0.050088 | 0.97106 | -0.558 | 0.9715 | -0.54934 | 13.7604
55 | 0.021469 | 0.0053849 | -0.021461 | -0.00538 | 8.0562e-06 | 4.9105e-06 | 0.0329 | 0.032901 | 0.032901 | 0.97106 | -0.558 | 0.97066 | -0.56588 | 9.0386
56 | 0.0253 | 0.0063448 | -0.025295 | -0.0063415 | 5.2758e-06 | 3.2541e-06 | 0.038232 | 0.038232 | 0.038232 | 0.98473 | -0.29279 | 0.98451 | -0.29717 | 10.5032
57 | 0.007713 | 0.0019332 | -0.0077122 | -0.0019329 | 7.7435e-07 | 3.0222e-07 | 0.011655 | 0.011655 | 0.011655 | 0.98473 | -0.29279 | 0.98462 | -0.2949 | 3.2019
58 | -0.05326 | -0.013376 | 0.053335 | 0.013424 | 7.5729e-05 | 4.8067e-05 | 0.080365 | 0.080365 | 0.080365 | 0.98626 | -0.2629 | 0.9878 | -0.23315 | 22.0783
59 | 0.0029741 | 0.00074518 | -0.002974 | -0.00074534 | 1.7108e-07 | -1.6189e-07 | 0.0045587 | 0.0045588 | 0.0045588 | 0.97077 | -0.56382 | 0.9707 | -0.56503 | 1.2524
60 | -0.19578 | -0.049687 | 0.19582 | 0.049711 | 3.6702e-05 | 2.3431e-05 | 0.29427 | 0.29427 | 0.29427 | 0.99076 | -0.17607 | 0.99096 | -0.17217 | 40.4213
61 | 0.19578 | 0.049687 | -0.19529 | -0.049371 | 0.00049488 | 0.00031594 | 0.29427 | 0.29427 | 0.29427 | 0.99076 | -0.17607 | 0.98802 | -0.22876 | 40.4213
62 | -0.20595 | -0.052249 | 0.20645 | 0.052571 | 0.00050499 | 0.00032247 | 0.30947 | 0.30947 | 0.30947 | 0.99096 | -0.17217 | 0.99361 | -0.12132 | 42.5102
63 | 0.062807 | 0.015804 | -0.062794 | -0.015795 | 1.3169e-05 | 8.378e-06 | 0.094614 | 0.094614 | 0.094614 | 0.98802 | -0.22876 | 0.9878 | -0.23315 | 25.9928
64 | 0.13248 | 0.033568 | -0.1323 | -0.033453 | 0.00017892 | 0.00011436 | 0.19965 | 0.19965 | 0.19965 | 0.98802 | -0.22876 | 0.98656 | -0.25692 | 54.85
65 | -0.039741 | -0.0099692 | 0.039775 | 0.0099907 | 3.4072e-05 | 2.1502e-05 | 0.060874 | 0.060874 | 0.060874 | 0.9715 | -0.54934 | 0.97241 | -0.53137 | 16.7236
66 | 0.015081 | 0.0037809 | -0.015077 | -0.0037787 | 3.893e-06 | 2.2515e-06 | 0.02312 | 0.02312 | 0.02312 | 0.97066 | -0.56588 | 0.97039 | -0.57129 | 6.3515
67 | 0.017371 | 0.0043558 | -0.017365 | -0.0043521 | 6.1584e-06 | 3.6386e-06 | 0.026256 | 0.026256 | 0.026256 | 0.98451 | -0.29717 | 0.98413 | -0.30461 | 7.2133
68 | 0.0094587 | 0.002371 | -0.0094583 | -0.0023708 | 4.1143e-07 | 1.9414e-07 | 0.014249 | 0.014249 | 0.014249 | 0.9878 | -0.23315 | 0.98775 | -0.23406 | 3.9145
69 | -0.0032772 | -0.00082135 | 0.0032775 | 0.00082116 | 2.7603e-07 | -1.8768e-07 | 0.0050107 | 0.0050106 | 0.0050107 | 0.97322 | -0.51541 | 0.97331 | -0.51364 | 1.3766
70 | 0.0028076 | 0.00070356 | -0.0028075 | -0.00070364 | 6.2701e-08 | -7.2657e-08 | 0.0042923 | 0.0042924 | 0.0042924 | 0.97331 | -0.51364 | 0.97328 | -0.51411 | 1.1792
71 | -0.0060851 | -0.0015247 | 0.0060853 | 0.0015248 | 2.1696e-07 | 5.5765e-08 | 0.0093029 | 0.0093029 | 0.0093029 | 0.97331 | -0.51364 | 0.97334 | -0.51289 | 2.5557
72 | -0.21278 | -0.054156 | 0.21303 | 0.054321 | 0.00025772 | 0.00016459 | 0.31895 | 0.31895 | 0.31895 | 0.99361 | -0.12132 | 0.99493 | -0.096227 | 43.8112
73 | -0.043821 | -0.011005 | 0.04386 | 0.011029 | 3.8679e-05 | 2.447e-05 | 0.067065 | 0.067065 | 0.067065 | 0.97241 | -0.53137 | 0.97334 | -0.51289 | 18.4244
74 | 0.0051284 | 0.0012853 | -0.0051282 | -0.0012852 | 2.2161e-07 | 2.3784e-08 | 0.007864 | 0.007864 | 0.007864 | 0.97039 | -0.57129 | 0.97034 | -0.5722 | 2.1604
75 | -0.072835 | -0.018323 | 0.072867 | 0.018343 | 3.1549e-05 | 1.9851e-05 | 0.11109 | 0.11109 | 0.11109 | 0.97579 | -0.46495 | 0.97625 | -0.45589 | 15.2601
76 | 0.071124 | 0.017894 | -0.07108 | -0.017866 | 4.4282e-05 | 2.784e-05 | 0.10848 | 0.10848 | 0.10848 | 0.97579 | -0.46495 | 0.97513 | -0.47799 | 14.9017
77 | -0.076041 | -0.019138 | 0.076075 | 0.01916 | 3.4092e-05 | 2.148e-05 | 0.11593 | 0.11593 | 0.11593 | 0.97625 | -0.45589 | 0.97673 | -0.44651 | 15.9246
78 | 0.0043917 | 0.0011004 | -0.0043913 | -0.0011005 | 3.9508e-07 | -3.9755e-08 | 0.0067016 | 0.0067017 | 0.0067017 | 0.97513 | -0.47799 | 0.97503 | -0.47988 | 1.8411
79 | 0.0091852 | 0.0023021 | -0.0091842 | -0.0023016 | 1.0476e-06 | 4.9311e-07 | 0.014016 | 0.014017 | 0.014017 | 0.97513 | -0.47799 | 0.975 | -0.48038 | 3.8507
80 | 0.057503 | 0.014464 | -0.057498 | -0.01446 | 5.1663e-06 | 3.2172e-06 | 0.087767 | 0.087767 | 0.087767 | 0.97513 | -0.47799 | 0.97503 | -0.47987 | 12.0559
81 | 0.0029939 | 0.00075015 | -0.0029937 | -0.0007503 | 1.5323e-07 | -1.4775e-07 | 0.004561 | 0.0045611 | 0.0045611 | 0.97673 | -0.44651 | 0.97667 | -0.44758 | 1.2531
82 | -0.079069 | -0.01991 | 0.079096 | 0.019927 | 2.7129e-05 | 1.7113e-05 | 0.12049 | 0.12049 | 0.12049 | 0.97673 | -0.44651 | 0.97709 | -0.43934 | 16.5511
83 | 0.0043913 | 0.0011005 | -0.0043911 | -0.0011005 | 1.9865e-07 | -1.9965e-08 | 0.0067017 | 0.0067017 | 0.0067017 | 0.97503 | -0.47988 | 0.97498 | -0.48083 | 1.8411
84 | 0.004527 | 0.0011344 | -0.0045266 | -0.0011345 | 4.5095e-07 | -2.555e-08 | 0.0069089 | 0.006909 | 0.006909 | 0.975 | -0.48038 | 0.9749 | -0.48247 | 1.8981
85 | 0.0096306 | 0.002414 | -0.0096291 | -0.0024133 | 1.5021e-06 | 7.301e-07 | 0.014698 | 0.014698 | 0.014698 | 0.97503 | -0.47987 | 0.97486 | -0.48314 | 4.0378
86 | 0.047867 | 0.012046 | -0.04782 | -0.012017 | 4.7311e-05 | 2.9102e-05 | 0.073069 | 0.073069 | 0.073069 | 0.97503 | -0.47987 | 0.97398 | -0.50057 | 10.037
87 | 0.0030081 | 0.00075368 | -0.0030079 | -0.00075385 | 1.7681e-07 | -1.6824e-07 | 0.0045809 | 0.004581 | 0.004581 | 0.97709 | -0.43934 | 0.97703 | -0.44057 | 1.2585
88 | 0.010233 | 0.0025653 | -0.010232 | -0.0025644 | 1.7533e-06 | 8.8106e-07 | 0.015585 | 0.015585 | 0.015585 | 0.97709 | -0.43934 | 0.97691 | -0.44293 | 4.2815
89 | 0.0017661 | 0.00044259 | -0.001766 | -0.00044261 | 4.8305e-09 | -1.9021e-08 | 0.0026953 | 0.0026953 | 0.0026953 | 0.97498 | -0.48083 | 0.97498 | -0.48088 | 0.74048
90 | 0.0053262 | 0.0013348 | -0.005326 | -0.0013348 | 1.0952e-07 | 1.5e-08 | 0.0081297 | 0.0081298 | 0.0081298 | 0.97486 | -0.48314 | 0.97484 | -0.48357 | 2.2335
91 | 0.042746 | 0.010746 | -0.042739 | -0.010741 | 7.5148e-06 | 4.5757e-06 | 0.065318 | 0.065318 | 0.065318 | 0.97398 | -0.50057 | 0.97379 | -0.50425 | 8.9723
92 | 0.0079054 | 0.0019814 | -0.0079047 | -0.0019811 | 7.3688e-07 | 3.0194e-07 | 0.012041 | 0.012042 | 0.012042 | 0.97691 | -0.44293 | 0.97681 | -0.44489 | 3.3081
93 | 0.0039848 | 0.00099853 | -0.0039845 | -0.00099861 | 2.8968e-07 | -7.3786e-08 | 0.0060889 | 0.006089 | 0.006089 | 0.97379 | -0.50425 | 0.97371 | -0.50578 | 1.6728
94 | 0.038754 | 0.0097426 | -0.038744 | -0.0097368 | 9.6055e-06 | 5.7843e-06 | 0.059229 | 0.059229 | 0.059229 | 0.97379 | -0.50425 | 0.97353 | -0.50945 | 8.1359
95 | -0.0055601 | -0.0013932 | 0.0055607 | 0.0013933 | 5.9243e-07 | 1.0792e-07 | 0.0085045 | 0.0085044 | 0.0085045 | 0.97283 | -0.52317 | 0.97294 | -0.52093 | 2.3364
96 | 0.0024312 | 0.00060901 | -0.0024311 | -0.00060929 | 1.5972e-07 | -2.8017e-07 | 0.0037186 | 0.0037188 | 0.0037188 | 0.97283 | -0.52317 | 0.97276 | -0.52454 | 1.0216
97 | -0.0080227 | -0.0020103 | 0.0080233 | 0.0020106 | 5.7594e-07 | 2.419e-07 | 0.01227 | 0.01227 | 0.01227 | 0.97294 | -0.52093 | 0.97302 | -0.51942 | 3.3708
98 | -0.0080233 | -0.0020106 | 0.0080235 | 0.0020107 | 2.1306e-07 | 8.9481e-08 | 0.01227 | 0.01227 | 0.01227 | 0.97302 | -0.51942 | 0.97305 | -0.51886 | 3.3708
99 | -0.031266 | -0.0078573 | 0.031274 | 0.0078627 | 8.6181e-06 | 5.3907e-06 | 0.04782 | 0.04782 | 0.04782 | 0.97305 | -0.51886 | 0.97334 | -0.51309 | 13.1374
100 | 0.023242 | 0.0058467 | -0.023215 | -0.0058298 | 2.7469e-05 | 1.6861e-05 | 0.035551 | 0.035551 | 0.035551 | 0.97305 | -0.51886 | 0.97179 | -0.54363 | 9.7667
101 | -0.033188 | -0.0083423 | 0.033194 | 0.0083457 | 5.7773e-06 | 3.4e-06 | 0.050746 | 0.050746 | 0.050746 | 0.97334 | -0.51309 | 0.97353 | -0.50945 | 6.9706
102 | 0.023215 | 0.0058298 | -0.023183 | -0.0058103 | 3.1873e-05 | 1.9567e-05 | 0.035551 | 0.035551 | 0.035551 | 0.97179 | -0.54363 | 0.97034 | -0.57245 | 9.7668
103 | 0.010341 | 0.0025916 | -0.010341 | -0.0025916 | 9.3708e-08 | 4.6985e-08 | 0.015635 | 0.015635 | 0.015635 | 0.98413 | -0.30461 | 0.98412 | -0.3048 | 4.2954
104 | -0.0094568 | -0.0023701 | 0.0094583 | 0.0023708 | 1.5156e-06 | 7.1523e-07 | 0.014249 | 0.014249 | 0.014249 | 0.98758 | -0.23743 | 0.98775 | -0.23406 | 3.9145
105 | -0.049945 | -0.012554 | 0.049986 | 0.01258 | 4.0936e-05 | 2.5966e-05 | 0.076368 | 0.076367 | 0.076368 | 0.97334 | -0.51289 | 0.97422 | -0.49574 | 20.9801
106 | 0.015767 | 0.0039556 | -0.015755 | -0.0039489 | 1.1486e-05 | 6.6938e-06 | 0.024084 | 0.024084 | 0.024084 | 0.97422 | -0.49574 | 0.97344 | -0.51103 | 6.6164
107 | -0.065753 | -0.016535 | 0.065857 | 0.016602 | 0.00010443 | 6.6489e-05 | 0.10045 | 0.10045 | 0.10045 | 0.97422 | -0.49574 | 0.9759 | -0.46255 | 27.5964
108 | 0.015755 | 0.0039489 | -0.015751 | -0.0039462 | 4.6681e-06 | 2.7209e-06 | 0.024084 | 0.024084 | 0.024084 | 0.97344 | -0.51103 | 0.97313 | -0.51725 | 6.6165
109 | -0.068773 | -0.017333 | 0.068825 | 0.017366 | 5.2469e-05 | 3.2944e-05 | 0.1049 | 0.1049 | 0.1049 | 0.9759 | -0.46255 | 0.97672 | -0.44661 | 14.4089
110 | 0.071262 | 0.017998 | -0.071203 | -0.017962 | 5.8365e-05 | 3.6691e-05 | 0.10852 | 0.10852 | 0.10852 | 0.97759 | -0.42951 | 0.97672 | -0.44661 | 14.9065
111 | -0.0065764 | -0.0016482 | 0.0065775 | 0.0016485 | 1.0885e-06 | 3.4428e-07 | 0.010087 | 0.010087 | 0.010087 | 0.97016 | -0.57592 | 0.97034 | -0.57245 | 2.7711
112 | -0.21303 | -0.054321 | 0.21334 | 0.054517 | 0.00030676 | 0.00019591 | 0.31895 | 0.31894 | 0.31895 | 0.99493 | -0.096227 | 0.99649 | -0.066448 | 43.8111
113 | -0.22516 | -0.057479 | 0.22589 | 0.057943 | 0.00072552 | 0.00046344 | 0.3366 | 0.33659 | 0.3366 | 0.99649 | -0.066448 | 1 | 0 | 46.2356
114 | 0.28041 | 0.072492 | -0.27926 | -0.07176 | 0.0011458 | 0.00073242 | 0.41804 | 0.41804 | 0.41804 | 1 | 0 | 0.99554 | -0.084094 | 57.4236
115 | 0.010707 | 0.0026837 | -0.010705 | -0.002683 | 1.4843e-06 | 7.6654e-07 | 0.016372 | 0.016372 | 0.016372 | 0.97313 | -0.51725 | 0.97298 | -0.52016 | 4.4978
116 | 0.0018706 | 0.00046722 | -0.0018702 | -0.00046872 | 4.3869e-07 | -1.4954e-06 | 0.0028598 | 0.0028605 | 0.0028605 | 0.97313 | -0.51725 | 0.97288 | -0.52218 | 0.78585
117 | 0.025626 | 0.0064281 | -0.025622 | -0.0064259 | 3.5886e-06 | 2.2158e-06 | 0.038758 | 0.038758 | 0.038758 | 0.98387 | -0.30919 | 0.98372 | -0.31213 | 10.6479
118 | 0.015178 | 0.0038084 | -0.015173 | -0.0038054 | 5.1653e-06 | 2.9742e-06 | 0.02296 | 0.02296 | 0.02296 | 0.98372 | -0.31213 | 0.98336 | -0.31927 | 6.3078
119 | 0.015173 | 0.0038054 | -0.01517 | -0.0038041 | 2.208e-06 | 1.2715e-06 | 0.02296 | 0.02296 | 0.02296 | 0.98336 | -0.31927 | 0.9832 | -0.32233 | 6.3078
120 | 0.01517 | 0.0038041 | -0.015164 | -0.0038005 | 6.2471e-06 | 3.5976e-06 | 0.02296 | 0.02296 | 0.02296 | 0.9832 | -0.32233 | 0.98276 | -0.33097 | 6.3078
121 | 0.0085147 | 0.0021339 | -0.0085142 | -0.0021337 | 5.1964e-07 | 2.3109e-07 | 0.013022 | 0.013022 | 0.013022 | 0.97298 | -0.52016 | 0.97291 | -0.52144 | 3.5775
122 | -0.0025749 | -0.00064533 | 0.002575 | 0.0006452 | 8.2843e-08 | -1.2378e-07 | 0.0039387 | 0.0039387 | 0.0039387 | 0.97277 | -0.5242 | 0.97281 | -0.52352 | 1.0821
123 | -0.005054 | -0.0012665 | 0.0050543 | 0.0012665 | 2.4464e-07 | 2.1032e-08 | 0.0077306 | 0.0077306 | 0.0077306 | 0.97281 | -0.52352 | 0.97286 | -0.5225 | 2.1238
124 | -0.0066811 | -0.0016743 | 0.0066814 | 0.0016744 | 3.3768e-07 | 1.0904e-07 | 0.010219 | 0.010219 | 0.010219 | 0.97286 | -0.5225 | 0.97291 | -0.52144 | 2.8074

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51939 | 0.1333

## res_load
| p_mw | q_mvar
0 | 0.0085763 | 0.0021494
1 | 0.0053095 | 0.0013307
2 | 0.010128 | 0.0025383
3 | 0.0075425 | 0.0018903
4 | 0.0091371 | 0.00229
5 | 0.0043035 | 0.0010786
6 | 0.0082133 | 0.0020585
7 | 0.007174 | 0.001798
8 | 0.016891 | 0.0042333
9 | 0.006898 | 0.0017288
10 | 0.006001 | 0.001504
11 | 0.0079959 | 0.002004
12 | 0.008927 | 0.0022373
13 | 0.0093283 | 0.0023379
14 | 0.0050105 | 0.0012558
15 | 0.0071665 | 0.0017961
16 | 0.0064204 | 0.0016091
17 | 0.0033671 | 0.00084388
18 | 0.0042193 | 0.0010575
19 | 0.0037888 | 0.00094955
20 | 0.0042446 | 0.0010638
21 | 0.0030893 | 0.00077425
22 | 0.004332 | 0.0010857
23 | 0.0052682 | 0.0013203
24 | 0.0070252 | 0.0017607
25 | 0.0027426 | 0.00068737
26 | 0.0058596 | 0.0014686
27 | 0.0038351 | 0.00096115
28 | 0.010894 | 0.0027303
29 | 0.0092901 | 0.0023283
30 | 0.0044042 | 0.0011038
31 | 0.010127 | 0.0025381
32 | 0.007042 | 0.0017649
33 | 0.0063803 | 0.0015991
34 | 0.0079232 | 0.0019857
35 | 0.0077122 | 0.0019329
36 | 0.0032772 | 0.00082135
37 | 0.002974 | 0.00074534
38 | 0.0063245 | 0.0015851
39 | 0.0065273 | 0.0016359
40 | 0.0040458 | 0.001014
41 | 0.0099488 | 0.0024934
42 | 0.0017111 | 0.00042884
43 | 0.0031739 | 0.00079546
44 | 0.0046572 | 0.0011672
45 | 0.0029937 | 0.0007503
46 | 0.0026251 | 0.0006579
47 | 0.0045266 | 0.0011345
48 | 0.004303 | 0.0010784
49 | 0.0050737 | 0.0012716
50 | 0.0030079 | 0.00075385
51 | 0.0023262 | 0.000583
52 | 0.001766 | 0.00044261
53 | 0.005326 | 0.0013348
54 | 0.0031289 | 0.00078417
55 | 0.002462 | 0.00061704
56 | 0.0024311 | 0.00060929
57 | 0.0019136 | 0.00047959
58 | 0.0070245 | 0.0017605
59 | 0.0094568 | 0.0023701
60 | 0.0028075 | 0.00070364
61 | 0.0029158 | 0.00073077
62 | 0.0045633 | 0.0011437
63 | 0.0065764 | 0.0016482
64 | 0.016605 | 0.0041617
65 | 0.0023778 | 0.00059593
66 | 0.01182 | 0.0029624
67 | 0.011443 | 0.0028678
68 | 0.007258 | 0.001819
69 | 0.012256 | 0.0030716
70 | 0.0031731 | 0.00079525
71 | 0.0079047 | 0.0019811
72 | 0.0055504 | 0.0013911
73 | 0.0039845 | 0.00099861
74 | 0.0080804 | 0.0020251
75 | 0.010444 | 0.0026175
76 | 0.015164 | 0.0038005
77 | 0.0021906 | 0.00054902
78 | 0.0018702 | 0.00046872
79 | 0.010341 | 0.0025916
80 | 0.0051282 | 0.0012852
81 | 0.0025749 | 0.00064533
82 | 0.002479 | 0.00062131
83 | 0.0016268 | 0.00040772
84 | 0.0018328 | 0.00045934

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1