## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-205_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-205_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-205_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1061-205_0_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_1061-205_0_4_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_1061-205_0_4_node_68 | 0.4 | n |  | TRUE
6 | bus_LV_1061-205_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1061-205_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1061-205_0_4_node_62 | 0.4 | n |  | TRUE
9 | bus_LV_1061-205_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1061-205_0_4_node_88 | 0.4 | n |  | TRUE
11 | bus_LV_1061-205_0_4_node_89 | 0.4 | n |  | TRUE
12 | bus_LV_1061-205_0_4_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_1061-205_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1061-205_0_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1061-205_0_4_node_85 | 0.4 | n |  | TRUE
16 | bus_LV_1061-205_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1061-205_0_4_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_1061-205_0_4_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1061-205_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1061-205_0_4_node_54 | 0.4 | n |  | TRUE
21 | bus_LV_1061-205_0_4_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_1061-205_0_4_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_1061-205_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1061-205_0_4_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1061-205_0_4_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1061-205_0_4_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_1061-205_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1061-205_0_4_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_1061-205_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1061-205_0_4_node_55 | 0.4 | n |  | TRUE
31 | bus_LV_1061-205_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1061-205_0_4_node_61 | 0.4 | n |  | TRUE
33 | bus_LV_1061-205_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1061-205_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_1061-205_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1061-205_0_4_node_79 | 0.4 | n |  | TRUE
37 | bus_LV_1061-205_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1061-205_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1061-205_0_4_node_86 | 0.4 | n |  | TRUE
40 | bus_LV_1061-205_0_4_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_1061-205_0_4_node_81 | 0.4 | n |  | TRUE
42 | bus_LV_1061-205_0_4_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_1061-205_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1061-205_0_4_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_1061-205_0_4_node_74 | 0.4 | n |  | TRUE
46 | bus_LV_1061-205_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1061-205_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_1061-205_0_4_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1061-205_0_4_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1061-205_0_4_node_70 | 0.4 | n |  | TRUE
51 | bus_LV_1061-205_0_4_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_1061-205_0_4_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_1061-205_0_4_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_1061-205_0_4_node_66 | 0.4 | n |  | TRUE
55 | bus_LV_1061-205_0_4_node_76 | 0.4 | n |  | TRUE
56 | bus_LV_1061-205_0_4_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_1061-205_0_4_node_84 | 0.4 | n |  | TRUE
58 | bus_LV_1061-205_0_4_node_31 | 0.4 | n |  | TRUE
59 | bus_LV_1061-205_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_1061-205_0_4_node_72 | 0.4 | n |  | TRUE
61 | bus_LV_1061-205_0_4_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_1061-205_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_1061-205_0_4_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_1061-205_0_4_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_1061-205_0_4_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_1061-205_0_4_node_37 | 0.4 | n |  | TRUE
67 | bus_LV_1061-205_0_4_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_1061-205_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_1061-205_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_1061-205_0_4_node_42 | 0.4 | n |  | TRUE
71 | bus_LV_1061-205_0_4_node_58 | 0.4 | n |  | TRUE
72 | bus_LV_1061-205_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1061-205_0_4_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_1061-205_0_4_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_1061-205_0_4_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_1061-205_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_1061-205_0_4_node_83 | 0.4 | n |  | TRUE
78 | bus_LV_1061-205_0_4_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_1061-205_0_4_node_87 | 0.4 | n |  | TRUE
80 | bus_LV_1061-205_0_4_node_82 | 0.4 | n |  | TRUE
81 | bus_MV_3_0_node_24 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-205_0_4_load_0 | 0 | 0.0097033 | 0.0024319 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-205_0_4_load_1 | 1 | 0.020929 | 0.0052454 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-205_0_4_load_68 | 5 | 0.019173 | 0.0048053 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-205_0_4_load_62 | 8 | 0.0010787 | 0.00027036 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-205_0_4_load_88 | 10 | 0.01195 | 0.0029949 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-205_0_4_load_89 | 11 | 0.014568 | 0.0036511 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-205_0_4_load_85 | 15 | 0.0073532 | 0.0018429 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-205_0_4_load_30 | 17 | 0.0077385 | 0.0019395 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-205_0_4_load_29 | 18 | 0.0011155 | 0.00027957 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-205_0_4_load_63 | 22 | 0.014569 | 0.0036514 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-205_0_4_load_39 | 25 | 0.0092918 | 0.0023287 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-205_0_4_load_69 | 26 | 0.0059592 | 0.0014935 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-205_0_4_load_32 | 27 | 0.0041144 | 0.0010312 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-205_0_4_load_50 | 28 | 0.0040172 | 0.0010068 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-205_0_4_load_55 | 30 | 0.010465 | 0.0026228 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-205_0_4_load_61 | 32 | 0.012094 | 0.003031 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-205_0_4_load_79 | 36 | 0.014057 | 0.003523 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-205_0_4_load_86 | 39 | 0.014017 | 0.0035129 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-205_0_4_load_75 | 40 | 0.027513 | 0.0068953 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-205_0_4_load_81 | 41 | 0.01364 | 0.0034185 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-205_0_4_load_74 | 45 | 0.0031407 | 0.00078714 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-205_0_4_load_38 | 46 | 0.01364 | 0.0034185 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-205_0_4_load_34 | 47 | 0.0067329 | 0.0016874 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-205_0_4_load_70 | 50 | 0.0035373 | 0.00088654 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-205_0_4_load_52 | 51 | 0.016788 | 0.0042076 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-205_0_4_load_77 | 53 | 0.014302 | 0.0035845 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-205_0_4_load_76 | 55 | 0.014509 | 0.0036362 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-205_0_4_load_84 | 57 | 0.016566 | 0.0041519 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-205_0_4_load_31 | 58 | 0.0032712 | 0.00081983 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-205_0_4_load_44 | 59 | 0.0063499 | 0.0015914 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-205_0_4_load_72 | 60 | 0.012954 | 0.0032465 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-205_0_4_load_59 | 64 | 0.0026026 | 0.00065227 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-205_0_4_load_37 | 66 | 0.014518 | 0.0036386 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1061-205_0_4_load_71 | 67 | 0.003068 | 0.00076891 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1061-205_0_4_load_40 | 68 | 0.0051422 | 0.0012888 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1061-205_0_4_load_41 | 69 | 0.0050089 | 0.0012554 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1061-205_0_4_load_42 | 70 | 0.0032602 | 0.00081707 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1061-205_0_4_load_58 | 71 | 0.0027518 | 0.00068966 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1061-205_0_4_load_45 | 73 | 0.0021864 | 0.00054797 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1061-205_0_4_load_60 | 75 | 0.0031789 | 0.00079672 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1061-205_0_4_load_51 | 76 | 0.0011441 | 0.00028674 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1061-205_0_4_load_80 | 78 | 0.00081079 | 0.0002032 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1061-205_0_4_load_87 | 79 | 0.013904 | 0.0034846 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1061-205_0_4_load_82 | 80 | 0.016558 | 0.0041499 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-205_0_4_line_0 |  | 0 | 1 | 0.026202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-205_0_4_line_1 |  | 1 | 2 | 0.0036371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-205_0_4_line_2 |  | 2 | 3 | 0.0082178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-205_0_4_line_3 |  | 3 | 4 | 0.016554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-205_0_4_line_4 |  | 3 | 5 | 0.025969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-205_0_4_line_5 |  | 4 | 29 | 0.028758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-205_0_4_line_6 |  | 4 | 30 | 0.017828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-205_0_4_line_7 |  | 6 | 7 | 0.036622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-205_0_4_line_8 |  | 6 | 8 | 0.019418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-205_0_4_line_9 |  | 7 | 18 | 0.013685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-205_0_4_line_10 |  | 8 | 31 | 0.014676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-205_0_4_line_11 |  | 9 | 10 | 0.006319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-205_0_4_line_12 |  | 9 | 11 | 0.008572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-205_0_4_line_13 |  | 9 | 12 | 0.04079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-205_0_4_line_14 |  | 12 | 44 | 0.018153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-205_0_4_line_15 |  | 13 | 14 | 0.034733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1061-205_0_4_line_16 |  | 13 | 15 | 0.01137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1061-205_0_4_line_17 |  | 14 | 26 | 0.014584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-205_0_4_line_18 |  | 14 | 27 | 0.052738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-205_0_4_line_19 |  | 14 | 28 | 0.014957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1061-205_0_4_line_20 |  | 15 | 39 | 0.019237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1061-205_0_4_line_21 |  | 16 | 17 | 0.012488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-205_0_4_line_22 |  | 16 | 18 | 0.011299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-205_0_4_line_23 |  | 17 | 29 | 0.0071579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-205_0_4_line_24 |  | 19 | 20 | 0.0044054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-205_0_4_line_25 |  | 19 | 21 | 0.030211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-205_0_4_line_26 |  | 19 | 22 | 0.019733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-205_0_4_line_27 |  | 20 | 51 | 0.021858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-205_0_4_line_28 |  | 20 | 43 | 0.014527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-205_0_4_line_29 |  | 21 | 56 | 0.00884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1061-205_0_4_line_30 |  | 21 | 52 | 0.022523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1061-205_0_4_line_31 |  | 23 | 24 | 0.033614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-205_0_4_line_32 |  | 23 | 25 | 0.025393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-205_0_4_line_33 |  | 24 | 42 | 0.029809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1061-205_0_4_line_34 |  | 24 | 40 | 0.031645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1061-205_0_4_line_35 |  | 24 | 38 | 0.016818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1061-205_0_4_line_36 |  | 27 | 58 | 0.020234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1061-205_0_4_line_37 |  | 28 | 59 | 0.0031515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1061-205_0_4_line_38 |  | 31 | 32 | 0.0165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1061-205_0_4_line_39 |  | 32 | 43 | 0.030439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1061-205_0_4_line_40 |  | 33 | 34 | 0.030209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1061-205_0_4_line_41 |  | 33 | 35 | 0.031748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1061-205_0_4_line_42 |  | 34 | 36 | 0.021671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1061-205_0_4_line_43 |  | 35 | 40 | 0.032007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1061-205_0_4_line_44 |  | 36 | 61 | 0.014946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1061-205_0_4_line_45 |  | 37 | 38 | 0.026252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1061-205_0_4_line_46 |  | 37 | 39 | 0.024131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1061-205_0_4_line_47 |  | 38 | 41 | 0.019822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1061-205_0_4_line_48 |  | 41 | 46 | 0.01906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1061-205_0_4_line_49 |  | 42 | 54 | 0.0047841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1061-205_0_4_line_50 |  | 42 | 60 | 0.018754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1061-205_0_4_line_51 |  | 44 | 45 | 0.018888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1061-205_0_4_line_52 |  | 45 | 62 | 0.012119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1061-205_0_4_line_53 |  | 47 | 48 | 0.00063347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1061-205_0_4_line_54 |  | 48 | 66 | 0.016954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1061-205_0_4_line_55 |  | 48 | 49 | 0.04253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1061-205_0_4_line_56 |  | 49 | 50 | 0.0060068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1061-205_0_4_line_57 |  | 50 | 67 | 0.017823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1061-205_0_4_line_58 |  | 51 | 76 | 0.023426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1061-205_0_4_line_59 |  | 52 | 53 | 0.018528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_1061-205_0_4_line_60 |  | 53 | 61 | 0.0082865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1061-205_0_4_line_61 |  | 54 | 55 | 0.019829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1061-205_0_4_line_62 |  | 55 | 66 | 0.019171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1061-205_0_4_line_63 |  | 56 | 57 | 0.012027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1061-205_0_4_line_64 |  | 57 | 77 | 0.0075148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1061-205_0_4_line_65 |  | 59 | 70 | 0.025462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1061-205_0_4_line_66 |  | 61 | 78 | 0.021026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1061-205_0_4_line_67 |  | 62 | 63 | 0.01537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1061-205_0_4_line_68 |  | 63 | 73 | 0.0081797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1061-205_0_4_line_69 |  | 64 | 65 | 0.017397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1061-205_0_4_line_70 |  | 65 | 71 | 0.02018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1061-205_0_4_line_71 |  | 65 | 69 | 0.026571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1061-205_0_4_line_72 |  | 68 | 69 | 0.0043525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1061-205_0_4_line_73 |  | 68 | 70 | 0.02924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1061-205_0_4_line_74 |  | 71 | 72 | 0.019468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1061-205_0_4_line_75 |  | 72 | 75 | 0.007128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1061-205_0_4_line_76 |  | 72 | 74 | 0.018789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1061-205_0_4_line_77 |  | 73 | 74 | 0.0099005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1061-205_0_4_line_78 |  | 77 | 80 | 0.011616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1061-205_0_4_line_79 |  | 78 | 79 | 0.0049235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-205_0_4_trafo_84 | 0.63 MVA 20/0.4 kV | 81 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2662573.5894 | 1211369.7188 | 2662581.1548 | 1211360.9337 | 2662586.5854 | 1211353.2192 | 2662589.096 | 1211348.6952
1 | 2662590.8609 | 1211345.5149 | 2662589.096 | 1211348.6952
2 | 2662590.8609 | 1211345.5149 | 2662591.882 | 1211345.9704 | 2662594.983 | 1211347.3593 | 2662597.5318 | 1211348.5089 | 2662598.3561 | 1211348.8845
3 | 2662598.3561 | 1211348.8845 | 2662601.0803 | 1211343.4542 | 2662602.2005 | 1211341.7093 | 2662602.7104 | 1211340.9142 | 2662605.2356 | 1211338.517 | 2662606.9138 | 1211337.1782 | 2662608.4592 | 1211336.1938
4 | 2662598.3561 | 1211348.8845 | 2662595.0299 | 1211354.4752 | 2662589.5912 | 1211362.9567 | 2662583.9188 | 1211370.437
5 | 2662602.3319 | 1211316.1618 | 2662603.3623 | 1211316.4505 | 2662606.7568 | 1211317.3867 | 2662609.6133 | 1211318.1838 | 2662610.6437 | 1211318.4726 | 2662610.9805 | 1211321.1333 | 2662612.8455 | 1211324.4438 | 2662612.7406 | 1211325.0319 | 2662611.9331 | 1211329.5596 | 2662611.3153 | 1211334.1225 | 2662611.2002 | 1211334.9552 | 2662609.7647 | 1211335.6072 | 2662608.4592 | 1211336.1938
6 | 2662608.4592 | 1211336.1938 | 2662609.7535 | 1211343.1895 | 2662610.4127 | 1211353.8833
7 | 2662613.9546 | 1211273.0908 | 2662614.9018 | 1211273.3453 | 2662616.8265 | 1211273.8658 | 2662618.3496 | 1211274.2709 | 2662619.8576 | 1211274.6759 | 2662621.4943 | 1211275.1267 | 2662623.4569 | 1211275.6476 | 2662624.1844 | 1211275.8442 | 2662624.3637 | 1211275.4125 | 2662627.3405 | 1211271.2634 | 2662629.118 | 1211269.8813 | 2662631.1355 | 1211268.8018 | 2662631.7315 | 1211268.4856 | 2662633.6824 | 1211267.2386 | 2662635.4248 | 1211266.3008 | 2662637.7327 | 1211265.7914 | 2662640.8266 | 1211265.6905 | 2662642.3054 | 1211265.9728 | 2662646.2189 | 1211266.7032
8 | 2662646.2189 | 1211266.7032 | 2662645.6614 | 1211269.1322 | 2662645.6699 | 1211271.2225 | 2662646.5528 | 1211276.1458 | 2662646.2611 | 1211278.5998 | 2662644.7722 | 1211283.6095 | 2662644.2917 | 1211285.6912
9 | 2662613.9546 | 1211273.0908 | 2662613.8473 | 1211273.9012 | 2662610.7181 | 1211286.3828
10 | 2662640.9907 | 1211299.9909 | 2662644.2917 | 1211285.6912
11 | 2662626.8725 | 1211371.5531 | 2662630.5764 | 1211369.0793 | 2662632.4434 | 1211369.2991
12 | 2662638.5043 | 1211375.3775 | 2662632.4434 | 1211369.2991
13 | 2662632.4434 | 1211369.2991 | 2662629.5898 | 1211384.8786 | 2662628.6318 | 1211391.4392 | 2662612.2842 | 1211392.3905 | 2662610.3517 | 1211392.6148
14 | 2662610.3517 | 1211392.6148 | 2662612.0139 | 1211403.6612 | 2662618.9679 | 1211404.2901
15 | 2662777.0427 | 1211418.4706 | 2662775.4366 | 1211418.7317 | 2662774.3648 | 1211418.7649 | 2662774.3723 | 1211419.4987 | 2662774.3795 | 1211423.1455 | 2662774.5078 | 1211429.006 | 2662777.9592 | 1211450.5221
16 | 2662777.0427 | 1211418.4706 | 2662779.6251 | 1211407.3977
17 | 2662777.9592 | 1211450.5221 | 2662786.3818 | 1211447.3421 | 2662791.3977 | 1211444.8951
18 | 2662777.9592 | 1211450.5221 | 2662779.8555 | 1211463.1164 | 2662779.9933 | 1211474.5693 | 2662778.4203 | 1211484.6811 | 2662774.2371 | 1211496.6 | 2662771.5965 | 1211501.6321
19 | 2662777.9592 | 1211450.5221 | 2662775.5597 | 1211451.075 | 2662763.5382 | 1211454.479
20 | 2662779.6251 | 1211407.3977 | 2662783.9941 | 1211388.6636
21 | 2662607.9703 | 1211297.3428 | 2662604.3862 | 1211309.3051
22 | 2662607.9703 | 1211297.3428 | 2662610.7181 | 1211286.3828
23 | 2662602.3319 | 1211316.1618 | 2662604.3862 | 1211309.3051
24 | 2662663.4795 | 1211341.6191 | 2662664.1003 | 1211338.2235 | 2662663.1677 | 1211338.0247
25 | 2662663.4795 | 1211341.6191 | 2662685.2076 | 1211345.7053 | 2662685.6702 | 1211345.7991 | 2662684.0417 | 1211353.2532
26 | 2662663.4795 | 1211341.6191 | 2662659.9143 | 1211361.0277
27 | 2662663.1677 | 1211338.0247 | 2662668.0697 | 1211316.7238
28 | 2662663.1677 | 1211338.0247 | 2662648.7925 | 1211335.6612
29 | 2662692.7236 | 1211355.0455 | 2662684.0417 | 1211353.2532
30 | 2662684.0417 | 1211353.2532 | 2662685.6702 | 1211345.7991 | 2662686.3171 | 1211342.8152 | 2662697.9106 | 1211345.2162
31 | 2662758.3713 | 1211359.3493 | 2662765.5196 | 1211361.0144 | 2662768.3546 | 1211361.6779 | 2662791.103 | 1211366.9982
32 | 2662791.103 | 1211366.9982 | 2662796.5467 | 1211342.1959
33 | 2662729.2628 | 1211352.5502 | 2662758.3713 | 1211359.3493
34 | 2662758.3713 | 1211359.3493 | 2662761.3999 | 1211349.564 | 2662764.999 | 1211341.8861 | 2662764.9123 | 1211336.404 | 2662767.4458 | 1211329.4096
35 | 2662758.3713 | 1211359.3493 | 2662765.5196 | 1211361.0144 | 2662764.7982 | 1211363.8529 | 2662758.4392 | 1211362.2851
36 | 2662771.5965 | 1211501.6321 | 2662762.1946 | 1211519.5489
37 | 2662763.5382 | 1211454.479 | 2662760.5059 | 1211455.3376
38 | 2662640.9907 | 1211299.9909 | 2662637.2752 | 1211316.0668
39 | 2662648.7925 | 1211335.6612 | 2662650.7035 | 1211328.0767 | 2662649.155 | 1211325.0252 | 2662636.0152 | 1211321.5185 | 2662637.2752 | 1211316.0668
40 | 2662712.8525 | 1211283.5689 | 2662721.3413 | 1211285.6705 | 2662742.1769 | 1211290.826
41 | 2662742.1769 | 1211290.826 | 2662747.0201 | 1211292.0221 | 2662763.0276 | 1211295.9818 | 2662772.9943 | 1211298.4548
42 | 2662712.8525 | 1211283.5689 | 2662707.747 | 1211304.6302
43 | 2662772.9943 | 1211298.4548 | 2662772.4827 | 1211300.1282 | 2662772.1921 | 1211314.0225 | 2662769.4688 | 1211318.63 | 2662768.2542 | 1211327.178 | 2662767.4458 | 1211329.4096
44 | 2662704.2258 | 1211319.1556 | 2662707.747 | 1211304.6302
45 | 2662758.4392 | 1211362.2851 | 2662764.7982 | 1211363.8529 | 2662772.7335 | 1211365.8265 | 2662783.992 | 1211368.2909
46 | 2662783.992 | 1211368.2909 | 2662782.7165 | 1211374.6814 | 2662786.9904 | 1211375.8159 | 2662783.9941 | 1211388.6636
47 | 2662758.4392 | 1211362.2851 | 2662753.5694 | 1211381.4994
48 | 2662749.1063 | 1211400.0281 | 2662751.3039 | 1211390.4384 | 2662753.5694 | 1211381.4994
49 | 2662726.6787 | 1211354.7688 | 2662727.2844 | 1211352.0847 | 2662729.2628 | 1211352.5502
50 | 2662729.2628 | 1211352.5502 | 2662733.8202 | 1211334.3582
51 | 2662618.9679 | 1211404.2901 | 2662621.5366 | 1211410.7766 | 2662624.8569 | 1211422.2157
52 | 2662627.3714 | 1211434.0409 | 2662626.4794 | 1211427.8055 | 2662624.8569 | 1211422.2157
53 | 2662714.9275 | 1211409.4856 | 2662714.3113 | 1211409.3388
54 | 2662714.3113 | 1211409.3388 | 2662718.0585 | 1211392.8043
55 | 2662672.3363 | 1211401.9823 | 2662700.2577 | 1211406.0336 | 2662714.3113 | 1211409.3388
56 | 2662672.3363 | 1211401.9823 | 2662672.0903 | 1211404.4256 | 2662674.6833 | 1211406.8518
57 | 2662688.0048 | 1211418.657 | 2662684.8525 | 1211416.3669 | 2662674.6833 | 1211406.8518
58 | 2662673.3234 | 1211293.8949 | 2662668.0697 | 1211316.7238
59 | 2662697.9106 | 1211345.2162 | 2662702.2743 | 1211327.209
60 | 2662704.2258 | 1211319.1556 | 2662702.2743 | 1211327.209
61 | 2662726.6787 | 1211354.7688 | 2662722.2959 | 1211374.1072
62 | 2662718.0585 | 1211392.8043 | 2662722.2959 | 1211374.1072
63 | 2662692.7236 | 1211355.0455 | 2662690.3595 | 1211366.8376
64 | 2662688.8823 | 1211374.2058 | 2662690.3595 | 1211366.8376
65 | 2662735.804 | 1211455.004 | 2662747.1929 | 1211457.614 | 2662750.2714 | 1211458.2356 | 2662760.5059 | 1211455.3376
66 | 2662704.2258 | 1211319.1556 | 2662715.9376 | 1211303.8137 | 2662717.6295 | 1211304.1488
67 | 2662637.363 | 1211445.6973 | 2662632.1164 | 1211438.7936 | 2662627.3714 | 1211434.0409
68 | 2662637.363 | 1211445.6973 | 2662641.268 | 1211450.8415 | 2662642.3796 | 1211452.1556
69 | 2662699.2951 | 1211487.4732 | 2662699.7909 | 1211504.6445 | 2662699.7547 | 1211504.8605
70 | 2662699.2951 | 1211487.4732 | 2662695.1286 | 1211482.6376 | 2662688.4827 | 1211478.7321 | 2662682.8137 | 1211476.5115
71 | 2662699.2951 | 1211487.4732 | 2662707.1407 | 1211486.3994 | 2662712.1695 | 1211483.6617 | 2662715.2233 | 1211478.6908 | 2662717.2604 | 1211471.8975
72 | 2662717.2604 | 1211471.8975 | 2662718.5106 | 1211467.7284
73 | 2662735.804 | 1211455.004 | 2662723.1928 | 1211452.1139 | 2662718.5106 | 1211467.7284
74 | 2662664.7057 | 1211469.3655 | 2662665.9084 | 1211469.8896 | 2662682.8137 | 1211476.5115
75 | 2662664.7057 | 1211469.3655 | 2662666.2151 | 1211462.3993
76 | 2662664.7057 | 1211469.3655 | 2662657.4666 | 1211466.232 | 2662651.5303 | 1211462.0449 | 2662649.6143 | 1211460.7018 | 2662648.7736 | 1211459.7146
77 | 2662648.7736 | 1211459.7146 | 2662642.3796 | 1211452.1556
78 | 2662688.8823 | 1211374.2058 | 2662686.5988 | 1211385.595
79 | 2662722.4592 | 1211305.1053 | 2662717.6295 | 1211304.1488

## bus_geodata
| x | y | coords
0 | 2662573.5894 | 1211369.7188
1 | 2662589.096 | 1211348.6952
2 | 2662590.8609 | 1211345.5149
3 | 2662598.3561 | 1211348.8845
4 | 2662608.4591 | 1211336.1938
5 | 2662583.9188 | 1211370.437
6 | 2662646.2189 | 1211266.7032
7 | 2662613.9546 | 1211273.0908
8 | 2662644.2917 | 1211285.6912
9 | 2662632.4434 | 1211369.2991
10 | 2662626.8725 | 1211371.5531
11 | 2662638.5043 | 1211375.3775
12 | 2662610.3517 | 1211392.6148
13 | 2662777.0427 | 1211418.4706
14 | 2662777.9592 | 1211450.5221
15 | 2662779.6251 | 1211407.3977
16 | 2662607.9703 | 1211297.3428
17 | 2662604.3862 | 1211309.3051
18 | 2662610.7181 | 1211286.3828
19 | 2662663.4795 | 1211341.6191
20 | 2662663.1677 | 1211338.0247
21 | 2662684.0417 | 1211353.2532
22 | 2662659.9143 | 1211361.0277
23 | 2662791.103 | 1211366.9982
24 | 2662758.3713 | 1211359.3493
25 | 2662796.5467 | 1211342.1959
26 | 2662791.3977 | 1211444.8951
27 | 2662771.5965 | 1211501.6321
28 | 2662763.5382 | 1211454.479
29 | 2662602.3319 | 1211316.1618
30 | 2662610.4127 | 1211353.8833
31 | 2662640.9907 | 1211299.9909
32 | 2662637.2752 | 1211316.0668
33 | 2662742.1769 | 1211290.826
34 | 2662712.8525 | 1211283.5689
35 | 2662772.9943 | 1211298.4548
36 | 2662707.747 | 1211304.6302
37 | 2662783.992 | 1211368.2909
38 | 2662758.4392 | 1211362.2851
39 | 2662783.9941 | 1211388.6636
40 | 2662767.4458 | 1211329.4096
41 | 2662753.5694 | 1211381.4994
42 | 2662729.2628 | 1211352.5502
43 | 2662648.7925 | 1211335.6612
44 | 2662618.9679 | 1211404.2901
45 | 2662624.8569 | 1211422.2157
46 | 2662749.1063 | 1211400.0281
47 | 2662714.9275 | 1211409.4856
48 | 2662714.3113 | 1211409.3388
49 | 2662672.3363 | 1211401.9823
50 | 2662674.6833 | 1211406.8518
51 | 2662668.0697 | 1211316.7238
52 | 2662697.9106 | 1211345.2162
53 | 2662702.2743 | 1211327.209
54 | 2662726.6787 | 1211354.7688
55 | 2662722.2959 | 1211374.1072
56 | 2662692.7236 | 1211355.0455
57 | 2662690.3595 | 1211366.8376
58 | 2662762.1946 | 1211519.5489
59 | 2662760.5059 | 1211455.3376
60 | 2662733.8202 | 1211334.3582
61 | 2662704.2258 | 1211319.1556
62 | 2662627.3714 | 1211434.0409
63 | 2662637.363 | 1211445.6973
64 | 2662699.7547 | 1211504.8605
65 | 2662699.2951 | 1211487.4732
66 | 2662718.0585 | 1211392.8043
67 | 2662688.0048 | 1211418.657
68 | 2662718.5106 | 1211467.7284
69 | 2662717.2604 | 1211471.8975
70 | 2662735.804 | 1211455.004
71 | 2662682.8137 | 1211476.5115
72 | 2662664.7057 | 1211469.3655
73 | 2662642.3796 | 1211452.1556
74 | 2662648.7736 | 1211459.7146
75 | 2662666.2151 | 1211462.3993
76 | 2662673.3234 | 1211293.8949
77 | 2662688.8823 | 1211374.2058
78 | 2662717.6295 | 1211304.1488
79 | 2662722.4592 | 1211305.1053
80 | 2662686.5988 | 1211385.595
81 | 2662688.8823 | 1211374.2058

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97923 | -0.39979 | 0.0097033 | 0.0024319
1 | 0.97947 | -0.39517 | 0.020929 | 0.0052454
2 | 0.97957 | -0.39315 | 0 | 0
3 | 0.9798 | -0.38858 | 0 | 0
4 | 0.98057 | -0.37362 | 0 | 0
5 | 0.97934 | -0.39762 | 0.019173 | 0.0048053
6 | 0.98729 | -0.2429 | 0 | 0
7 | 0.98494 | -0.28828 | 0 | 0
8 | 0.98853 | -0.21893 | 0.0010787 | 0.00027036
9 | 0.97133 | -0.55435 | 0 | 0
10 | 0.97126 | -0.55575 | 0.01195 | 0.0029949
11 | 0.97121 | -0.55666 | 0.014568 | 0.0036511
12 | 0.97234 | -0.53439 | 0 | 0
13 | 0.97993 | -0.38539 | 0 | 0
14 | 0.9791 | -0.4017 | 0 | 0
15 | 0.98021 | -0.38006 | 0.0073532 | 0.0018429
16 | 0.98336 | -0.31913 | 0 | 0
17 | 0.98257 | -0.33446 | 0.0077385 | 0.0019395
18 | 0.98407 | -0.30529 | 0.0011155 | 0.00027957
19 | 0.99439 | -0.10666 | 0 | 0
20 | 0.99398 | -0.11445 | 0 | 0
21 | 0.99758 | -0.045721 | 0 | 0
22 | 0.99412 | -0.11173 | 0.014569 | 0.0036514
23 | 0.98262 | -0.33301 | 0 | 0
24 | 0.98291 | -0.32737 | 0 | 0
25 | 0.9824 | -0.33727 | 0.0092918 | 0.0023287
26 | 0.97902 | -0.40328 | 0.0059592 | 0.0014935
27 | 0.97874 | -0.40878 | 0.0041144 | 0.0010312
28 | 0.9788 | -0.40752 | 0.0040172 | 0.0010068
29 | 0.98217 | -0.34225 | 0 | 0
30 | 0.9804 | -0.377 | 0.010465 | 0.0026228
31 | 0.98948 | -0.20057 | 0 | 0
32 | 0.99056 | -0.17997 | 0.012094 | 0.003031
33 | 0.98907 | -0.20811 | 0 | 0
34 | 0.99111 | -0.16902 | 0 | 0
35 | 0.98693 | -0.24936 | 0 | 0
36 | 0.99257 | -0.14108 | 0.014057 | 0.003523
37 | 0.98145 | -0.35579 | 0 | 0
38 | 0.98225 | -0.34014 | 0 | 0
39 | 0.98071 | -0.37019 | 0.014017 | 0.0035129
40 | 0.98477 | -0.29113 | 0.027513 | 0.0068953
41 | 0.98175 | -0.34992 | 0.01364 | 0.0034185
42 | 0.98138 | -0.35717 | 0 | 0
43 | 0.99287 | -0.13557 | 0 | 0
44 | 0.97279 | -0.52552 | 0 | 0
45 | 0.97326 | -0.5163 | 0.0031407 | 0.00078714
46 | 0.98151 | -0.35462 | 0.01364 | 0.0034185
47 | 0.97971 | -0.38993 | 0.0067329 | 0.0016874
48 | 0.97972 | -0.38986 | 0 | 0
49 | 0.97946 | -0.39496 | 0 | 0
50 | 0.97942 | -0.39568 | 0.0035373 | 0.00088654
51 | 0.99362 | -0.12137 | 0.016788 | 0.0042076
52 | 0.99577 | -0.080155 | 0 | 0
53 | 0.99427 | -0.10858 | 0.014302 | 0.0035845
54 | 0.9812 | -0.36084 | 0 | 0
55 | 0.98042 | -0.37606 | 0.014509 | 0.0036362
56 | 0.99861 | -0.026324 | 0 | 0
57 | 1 | 0 | -0.40043 | -0.10228
58 | 0.97868 | -0.40999 | 0.0032712 | 0.00081983
59 | 0.97874 | -0.40867 | 0.0063499 | 0.0015914
60 | 0.98116 | -0.36157 | 0.012954 | 0.0032465
61 | 0.99364 | -0.12062 | 0 | 0
62 | 0.97359 | -0.50968 | 0 | 0
63 | 0.97402 | -0.50131 | 0 | 0
64 | 0.9764 | -0.45447 | 0.0026026 | 0.00065227
65 | 0.97644 | -0.45364 | 0 | 0
66 | 0.97993 | -0.38575 | 0.014518 | 0.0036386
67 | 0.97937 | -0.39668 | 0.003068 | 0.00076891
68 | 0.97763 | -0.43044 | 0.0051422 | 0.0012888
69 | 0.97744 | -0.43405 | 0.0050089 | 0.0012554
70 | 0.97832 | -0.41698 | 0.0032602 | 0.00081707
71 | 0.97573 | -0.46759 | 0.0027518 | 0.00068966
72 | 0.9751 | -0.48008 | 0 | 0
73 | 0.97424 | -0.49685 | 0.0021864 | 0.00054797
74 | 0.97454 | -0.49106 | 0 | 0
75 | 0.97507 | -0.4805 | 0.0031789 | 0.00079672
76 | 0.9936 | -0.12184 | 0.0011441 | 0.00028674
77 | 0.99989 | -0.0021691 | 0 | 0
78 | 0.99336 | -0.12608 | 0.00081079 | 0.0002032
79 | 0.9933 | -0.12729 | 0.013904 | 0.0034846
80 | 0.99971 | -0.0055228 | 0.016558 | 0.0041499
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0097033 | -0.0024319 | 0.0097054 | 0.0024329 | 2.1362e-06 | 1.0375e-06 | 0.014745 | 0.014745 | 0.014745 | 0.97923 | -0.39979 | 0.97947 | -0.39517 | 4.0508
1 | -0.030635 | -0.0076783 | 0.030638 | 0.0076802 | 2.9543e-06 | 1.845e-06 | 0.046541 | 0.046541 | 0.046541 | 0.97947 | -0.39517 | 0.97957 | -0.39315 | 12.7859
2 | -0.030638 | -0.0076802 | 0.030644 | 0.0076843 | 6.6751e-06 | 4.1686e-06 | 0.046541 | 0.046541 | 0.046541 | 0.97957 | -0.39315 | 0.9798 | -0.38858 | 12.7859
3 | -0.049826 | -0.012495 | 0.049862 | 0.012517 | 3.5548e-05 | 2.2542e-05 | 0.075673 | 0.075673 | 0.075673 | 0.9798 | -0.38858 | 0.98057 | -0.37362 | 20.7892
4 | 0.019182 | 0.0048103 | -0.019173 | -0.0048053 | 8.2646e-06 | 4.9624e-06 | 0.029132 | 0.029132 | 0.029132 | 0.9798 | -0.38858 | 0.97934 | -0.39762 | 8.0033
5 | -0.060328 | -0.015141 | 0.060419 | 0.015198 | 9.04e-05 | 5.7493e-05 | 0.091556 | 0.091556 | 0.091556 | 0.98057 | -0.37362 | 0.98217 | -0.34225 | 25.1528
6 | 0.010467 | 0.0026236 | -0.010465 | -0.0026228 | 1.6867e-06 | 8.5463e-07 | 0.015883 | 0.015884 | 0.015884 | 0.98057 | -0.37362 | 0.9804 | -0.377 | 4.3636
7 | 0.069598 | 0.017625 | -0.069447 | -0.017528 | 0.0001513 | 9.6364e-05 | 0.10496 | 0.10496 | 0.10496 | 0.98729 | -0.2429 | 0.98494 | -0.28828 | 28.8357
8 | -0.069598 | -0.017625 | 0.069678 | 0.017676 | 8.0224e-05 | 5.1094e-05 | 0.10496 | 0.10496 | 0.10496 | 0.98729 | -0.2429 | 0.98853 | -0.21893 | 28.8356
9 | 0.069447 | 0.017528 | -0.06939 | -0.017492 | 5.6539e-05 | 3.6011e-05 | 0.10496 | 0.10496 | 0.10496 | 0.98494 | -0.28828 | 0.98407 | -0.30529 | 28.8357
10 | -0.070757 | -0.017946 | 0.07082 | 0.017986 | 6.2521e-05 | 3.9825e-05 | 0.10659 | 0.10659 | 0.10659 | 0.98853 | -0.21893 | 0.98948 | -0.20057 | 29.2817
11 | 0.011951 | 0.0029954 | -0.01195 | -0.0029949 | 7.9425e-07 | 4.3011e-07 | 0.018308 | 0.018308 | 0.018308 | 0.97133 | -0.55435 | 0.97126 | -0.55575 | 5.0296
12 | 0.01457 | 0.0036521 | -0.014568 | -0.0036511 | 1.6014e-06 | 9.1884e-07 | 0.02232 | 0.02232 | 0.02232 | 0.97133 | -0.55435 | 0.97121 | -0.55666 | 6.132
13 | -0.026521 | -0.0066474 | 0.026546 | 0.0066631 | 2.5248e-05 | 1.5654e-05 | 0.040628 | 0.040628 | 0.040628 | 0.97133 | -0.55435 | 0.97234 | -0.53439 | 11.1616
14 | -0.026546 | -0.0066631 | 0.026557 | 0.00667 | 1.1237e-05 | 6.9661e-06 | 0.040628 | 0.040628 | 0.040628 | 0.97234 | -0.53439 | 0.97279 | -0.52552 | 11.1615
15 | 0.077837 | 0.019631 | -0.077776 | -0.019593 | 6.0698e-05 | 3.7535e-05 | 0.11824 | 0.11824 | 0.11824 | 0.97993 | -0.38539 | 0.9791 | -0.4017 | 10.8278
16 | -0.077837 | -0.019631 | 0.077857 | 0.019643 | 1.987e-05 | 1.2287e-05 | 0.11824 | 0.11824 | 0.11824 | 0.97993 | -0.38539 | 0.98021 | -0.38006 | 10.8277
17 | 0.0059597 | 0.0014936 | -0.0059592 | -0.0014935 | 4.4866e-07 | 1.0374e-07 | 0.0090574 | 0.0090575 | 0.0090575 | 0.9791 | -0.4017 | 0.97902 | -0.40328 | 2.4883
18 | 0.0073882 | 0.0018518 | -0.0073857 | -0.0018509 | 2.4935e-06 | 9.3283e-07 | 0.011229 | 0.011229 | 0.011229 | 0.9791 | -0.4017 | 0.97874 | -0.40878 | 3.0848
19 | 0.064429 | 0.016248 | -0.064411 | -0.016237 | 1.7938e-05 | 1.0916e-05 | 0.097953 | 0.097954 | 0.097954 | 0.9791 | -0.4017 | 0.9788 | -0.40752 | 8.9701
20 | -0.08521 | -0.021486 | 0.085251 | 0.021511 | 4.0264e-05 | 2.5041e-05 | 0.1294 | 0.1294 | 0.1294 | 0.98021 | -0.38006 | 0.98071 | -0.37019 | 11.85
21 | 0.06823 | 0.017184 | -0.06818 | -0.017152 | 4.9946e-05 | 3.1807e-05 | 0.10328 | 0.10328 | 0.10328 | 0.98336 | -0.31913 | 0.98257 | -0.33446 | 28.3723
22 | -0.06823 | -0.017184 | 0.068275 | 0.017213 | 4.5193e-05 | 2.878e-05 | 0.10328 | 0.10328 | 0.10328 | 0.98336 | -0.31913 | 0.98407 | -0.30529 | 28.3723
23 | 0.060441 | 0.015213 | -0.060419 | -0.015198 | 2.25e-05 | 1.431e-05 | 0.091556 | 0.091556 | 0.091556 | 0.98257 | -0.33446 | 0.98217 | -0.34225 | 25.1527
24 | 0.10122 | 0.025751 | -0.10118 | -0.025727 | 3.7971e-05 | 2.4244e-05 | 0.15161 | 0.15161 | 0.15161 | 0.99439 | -0.10666 | 0.99398 | -0.11445 | 41.6504
25 | -0.1158 | -0.029404 | 0.11614 | 0.029622 | 0.0003407 | 0.00021765 | 0.17341 | 0.17341 | 0.17341 | 0.99439 | -0.10666 | 0.99758 | -0.045721 | 47.6414
26 | 0.014573 | 0.0036534 | -0.014569 | -0.0036514 | 3.5193e-06 | 1.9964e-06 | 0.021808 | 0.021808 | 0.021808 | 0.99439 | -0.10666 | 0.99412 | -0.11173 | 5.9911
27 | 0.017939 | 0.0044975 | -0.017933 | -0.004494 | 5.9114e-06 | 3.5001e-06 | 0.026855 | 0.026855 | 0.026855 | 0.99398 | -0.11445 | 0.99362 | -0.12137 | 7.3778
28 | 0.083246 | 0.021229 | -0.083162 | -0.021175 | 8.4782e-05 | 5.4073e-05 | 0.12475 | 0.12475 | 0.12475 | 0.99398 | -0.11445 | 0.99287 | -0.13557 | 34.2727
29 | -0.38137 | -0.097584 | 0.38173 | 0.097813 | 0.00035847 | 0.00022908 | 0.56957 | 0.56957 | 0.56957 | 0.99758 | -0.045721 | 0.99861 | -0.026324 | 52.1584
30 | 0.26523 | 0.067962 | -0.26479 | -0.06768 | 0.00044184 | 0.0002819 | 0.39616 | 0.39616 | 0.39616 | 0.99758 | -0.045721 | 0.99577 | -0.080155 | 36.278
31 | -0.0092937 | -0.0023296 | 0.0092962 | 0.0023308 | 2.4967e-06 | 1.172e-06 | 0.014074 | 0.014074 | 0.014074 | 0.98262 | -0.33301 | 0.98291 | -0.32737 | 3.8664
32 | 0.0092937 | 0.0023296 | -0.0092918 | -0.0023287 | 1.8861e-06 | 8.8553e-07 | 0.014074 | 0.014074 | 0.014074 | 0.98262 | -0.33301 | 0.9824 | -0.33727 | 3.8665
33 | 0.055456 | 0.01395 | -0.055377 | -0.0139 | 7.8823e-05 | 5.007e-05 | 0.083973 | 0.083973 | 0.083973 | 0.98291 | -0.32737 | 0.98138 | -0.35717 | 23.0694
34 | -0.19154 | -0.048289 | 0.19187 | 0.048501 | 0.00033282 | 0.0002118 | 0.29007 | 0.29007 | 0.29007 | 0.98291 | -0.32737 | 0.98477 | -0.29113 | 26.5628
35 | 0.12678 | 0.032009 | -0.12671 | -0.03196 | 7.7513e-05 | 4.8969e-05 | 0.19202 | 0.19202 | 0.19202 | 0.98291 | -0.32737 | 0.98225 | -0.34014 | 17.5842
36 | 0.0032713 | 0.00081969 | -0.0032712 | -0.00081983 | 1.8769e-07 | -1.3415e-07 | 0.0049735 | 0.0049736 | 0.0049736 | 0.97874 | -0.40878 | 0.97868 | -0.40999 | 1.3664
37 | 0.060393 | 0.01523 | -0.06039 | -0.015228 | 3.3232e-06 | 2.008e-06 | 0.091847 | 0.091847 | 0.091847 | 0.9788 | -0.40752 | 0.97874 | -0.40867 | 8.4109
38 | -0.07082 | -0.017986 | 0.07089 | 0.018031 | 7.0291e-05 | 4.4774e-05 | 0.10659 | 0.10659 | 0.10659 | 0.98948 | -0.20057 | 0.99056 | -0.17997 | 29.2817
39 | -0.082984 | -0.021062 | 0.083162 | 0.021175 | 0.00017765 | 0.0001133 | 0.12475 | 0.12475 | 0.12475 | 0.99056 | -0.17997 | 0.99287 | -0.13557 | 34.2727
40 | -0.22026 | -0.055955 | 0.22067 | 0.05622 | 0.00041531 | 0.00026463 | 0.33164 | 0.33164 | 0.33164 | 0.98907 | -0.20811 | 0.99111 | -0.16902 | 30.3697
41 | 0.22026 | 0.055955 | -0.21982 | -0.055677 | 0.00043646 | 0.00027812 | 0.33164 | 0.33164 | 0.33164 | 0.98907 | -0.20811 | 0.98693 | -0.24936 | 30.3697
42 | -0.22067 | -0.05622 | 0.22097 | 0.056409 | 0.00029793 | 0.00018984 | 0.33164 | 0.33164 | 0.33164 | 0.99111 | -0.16902 | 0.99257 | -0.14108 | 30.3696
43 | 0.21982 | 0.055677 | -0.21938 | -0.055396 | 0.00044003 | 0.00028039 | 0.33164 | 0.33164 | 0.33164 | 0.98693 | -0.24936 | 0.98477 | -0.29113 | 30.3697
44 | -0.23503 | -0.059932 | 0.23526 | 0.060081 | 0.00023242 | 0.00014817 | 0.35271 | 0.35271 | 0.35271 | 0.99257 | -0.14108 | 0.99364 | -0.12062 | 32.2994
45 | -0.099336 | -0.025067 | 0.09941 | 0.025113 | 7.4491e-05 | 4.6678e-05 | 0.15067 | 0.15067 | 0.15067 | 0.98145 | -0.35579 | 0.98225 | -0.34014 | 13.7974
46 | 0.099336 | 0.025067 | -0.099267 | -0.025024 | 6.8474e-05 | 4.2909e-05 | 0.15067 | 0.15067 | 0.15067 | 0.98145 | -0.35579 | 0.98071 | -0.37019 | 13.7975
47 | 0.027296 | 0.0068466 | -0.027283 | -0.0068387 | 1.2711e-05 | 7.8841e-06 | 0.041352 | 0.041352 | 0.041352 | 0.98225 | -0.34014 | 0.98175 | -0.34992 | 11.3605
48 | 0.013643 | 0.0034202 | -0.01364 | -0.0034185 | 3.0563e-06 | 1.7151e-06 | 0.020679 | 0.020679 | 0.020679 | 0.98175 | -0.34992 | 0.98151 | -0.35462 | 5.6809
49 | 0.042421 | 0.010652 | -0.042413 | -0.010647 | 7.4237e-06 | 4.6908e-06 | 0.064327 | 0.064327 | 0.064327 | 0.98138 | -0.35717 | 0.9812 | -0.36084 | 17.6723
50 | 0.012957 | 0.003248 | -0.012954 | -0.0032465 | 2.7143e-06 | 1.5002e-06 | 0.019646 | 0.019646 | 0.019646 | 0.98138 | -0.35717 | 0.98116 | -0.36157 | 5.3972
51 | -0.026557 | -0.00667 | 0.026569 | 0.0066773 | 1.1691e-05 | 7.2478e-06 | 0.040628 | 0.040628 | 0.040628 | 0.97279 | -0.52552 | 0.97326 | -0.5163 | 11.1615
52 | -0.029709 | -0.0074644 | 0.029719 | 0.0074703 | 9.3797e-06 | 5.8524e-06 | 0.04543 | 0.04543 | 0.04543 | 0.97326 | -0.5163 | 0.97359 | -0.50968 | 12.4807
53 | -0.0067329 | -0.0016874 | 0.0067329 | 0.0016874 | 2.4841e-08 | 7.9215e-09 | 0.010226 | 0.010226 | 0.010226 | 0.97971 | -0.38993 | 0.97972 | -0.38986 | 2.8094
54 | -0.01334 | -0.0033433 | 0.013343 | 0.0033448 | 2.61e-06 | 1.4568e-06 | 0.020261 | 0.020261 | 0.020261 | 0.97972 | -0.38986 | 0.97993 | -0.38575 | 5.5663
55 | 0.0066073 | 0.0016559 | -0.0066057 | -0.0016554 | 1.6062e-06 | 4.9254e-07 | 0.010035 | 0.010035 | 0.010035 | 0.97972 | -0.38986 | 0.97946 | -0.39496 | 2.757
56 | 0.0066057 | 0.0016554 | -0.0066055 | -0.0016553 | 2.2686e-07 | 6.9591e-08 | 0.010035 | 0.010036 | 0.010036 | 0.97946 | -0.39496 | 0.97942 | -0.39568 | 2.757
57 | 0.0030681 | 0.00076878 | -0.003068 | -0.00076891 | 1.4522e-07 | -1.3135e-07 | 0.0046613 | 0.0046614 | 0.0046614 | 0.97942 | -0.39568 | 0.97937 | -0.39668 | 1.2806
58 | 0.0011441 | 0.00028646 | -0.0011441 | -0.00028674 | 2.5789e-08 | -2.8691e-07 | 0.0017133 | 0.0017134 | 0.0017134 | 0.99362 | -0.12137 | 0.9936 | -0.12184 | 0.47072
59 | 0.26479 | 0.06768 | -0.26443 | -0.067448 | 0.00036348 | 0.00023191 | 0.39616 | 0.39616 | 0.39616 | 0.99577 | -0.080155 | 0.99427 | -0.10858 | 36.278
60 | 0.25012 | 0.063864 | -0.24998 | -0.063771 | 0.00014547 | 9.2777e-05 | 0.37475 | 0.37475 | 0.37475 | 0.99427 | -0.10858 | 0.99364 | -0.12062 | 34.3179
61 | 0.042413 | 0.010647 | -0.042382 | -0.010628 | 3.0769e-05 | 1.9442e-05 | 0.064327 | 0.064327 | 0.064327 | 0.9812 | -0.36084 | 0.98042 | -0.37606 | 17.6723
62 | 0.027874 | 0.0069913 | -0.027861 | -0.0069833 | 1.2868e-05 | 7.9938e-06 | 0.042307 | 0.042307 | 0.042307 | 0.98042 | -0.37606 | 0.97993 | -0.38575 | 11.6228
63 | -0.38173 | -0.097813 | 0.38221 | 0.098125 | 0.0004877 | 0.00031165 | 0.56957 | 0.56957 | 0.56957 | 0.99861 | -0.026324 | 1 | 0 | 52.1584
64 | 0.016562 | 0.0041524 | -0.016561 | -0.0041514 | 1.7117e-06 | 9.9693e-07 | 0.024646 | 0.024646 | 0.024646 | 1 | 0 | 0.99989 | -0.0021691 | 6.7708
65 | 0.05404 | 0.013636 | -0.054019 | -0.013624 | 2.1501e-05 | 1.2801e-05 | 0.082193 | 0.082193 | 0.082193 | 0.97874 | -0.40867 | 0.97832 | -0.41698 | 7.5268
66 | 0.014719 | 0.0036904 | -0.014715 | -0.0036882 | 3.8311e-06 | 2.1796e-06 | 0.022043 | 0.022043 | 0.022043 | 0.99364 | -0.12062 | 0.99336 | -0.12608 | 6.0557
67 | -0.029719 | -0.0074703 | 0.029731 | 0.0074777 | 1.1895e-05 | 7.4219e-06 | 0.04543 | 0.04543 | 0.04543 | 0.97359 | -0.50968 | 0.97402 | -0.50131 | 12.4807
68 | -0.029731 | -0.0074777 | 0.029737 | 0.0074817 | 6.3306e-06 | 3.9497e-06 | 0.04543 | 0.045429 | 0.04543 | 0.97402 | -0.50131 | 0.97424 | -0.49685 | 12.4806
69 | -0.0026026 | -0.00065227 | 0.0026027 | 0.00065212 | 1.0263e-07 | -1.5192e-07 | 0.0039663 | 0.0039662 | 0.0039663 | 0.9764 | -0.45447 | 0.97644 | -0.45364 | 1.0896
70 | 0.037926 | 0.0095611 | -0.037901 | -0.0095452 | 2.5296e-05 | 1.5937e-05 | 0.057816 | 0.057816 | 0.057816 | 0.97644 | -0.45364 | 0.97573 | -0.46759 | 15.8836
71 | -0.040529 | -0.010213 | 0.040567 | 0.010237 | 3.8033e-05 | 2.4009e-05 | 0.061783 | 0.061782 | 0.061783 | 0.97644 | -0.45364 | 0.97744 | -0.43405 | 16.9732
72 | 0.045584 | 0.011498 | -0.045576 | -0.011493 | 7.863e-06 | 4.9778e-06 | 0.069408 | 0.069408 | 0.069408 | 0.97763 | -0.43044 | 0.97744 | -0.43405 | 19.0681
73 | -0.050726 | -0.012786 | 0.050759 | 0.012807 | 3.2703e-05 | 2.0196e-05 | 0.077235 | 0.077234 | 0.077235 | 0.97763 | -0.43044 | 0.97832 | -0.41698 | 10.6091
74 | 0.035149 | 0.0088555 | -0.035128 | -0.0088423 | 2.0989e-05 | 1.319e-05 | 0.05362 | 0.05362 | 0.05362 | 0.97573 | -0.46759 | 0.9751 | -0.48008 | 14.7308
75 | 0.003179 | 0.00079667 | -0.0031789 | -0.00079672 | 6.2907e-08 | -4.8652e-08 | 0.0048512 | 0.0048512 | 0.0048512 | 0.9751 | -0.48008 | 0.97507 | -0.4805 | 1.3328
76 | 0.031949 | 0.0080456 | -0.031932 | -0.0080352 | 1.6758e-05 | 1.0491e-05 | 0.048769 | 0.048769 | 0.048769 | 0.9751 | -0.48008 | 0.97454 | -0.49106 | 13.398
77 | -0.031923 | -0.0080296 | 0.031932 | 0.0080352 | 8.8303e-06 | 5.5281e-06 | 0.048769 | 0.048769 | 0.048769 | 0.97424 | -0.49685 | 0.97454 | -0.49106 | 13.3981
78 | 0.016561 | 0.0041514 | -0.016558 | -0.0041499 | 2.6459e-06 | 1.541e-06 | 0.024646 | 0.024646 | 0.024646 | 0.99989 | -0.0021691 | 0.99971 | -0.0055228 | 6.7708
79 | 0.013904 | 0.003485 | -0.013904 | -0.0034846 | 8.0097e-07 | 4.4889e-07 | 0.020828 | 0.020828 | 0.020828 | 0.99336 | -0.12608 | 0.9933 | -0.12729 | 5.7221

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41699 | 0.10643

## res_load
| p_mw | q_mvar
0 | 0.0097033 | 0.0024319
1 | 0.020929 | 0.0052454
2 | 0.019173 | 0.0048053
3 | 0.0010787 | 0.00027036
4 | 0.01195 | 0.0029949
5 | 0.014568 | 0.0036511
6 | 0.0073532 | 0.0018429
7 | 0.0077385 | 0.0019395
8 | 0.0011155 | 0.00027957
9 | 0.014569 | 0.0036514
10 | 0.0092918 | 0.0023287
11 | 0.0059592 | 0.0014935
12 | 0.0041144 | 0.0010312
13 | 0.0040172 | 0.0010068
14 | 0.010465 | 0.0026228
15 | 0.012094 | 0.003031
16 | 0.014057 | 0.003523
17 | 0.014017 | 0.0035129
18 | 0.027513 | 0.0068953
19 | 0.01364 | 0.0034185
20 | 0.0031407 | 0.00078714
21 | 0.01364 | 0.0034185
22 | 0.0067329 | 0.0016874
23 | 0.0035373 | 0.00088654
24 | 0.016788 | 0.0042076
25 | 0.014302 | 0.0035845
26 | 0.014509 | 0.0036362
27 | 0.016566 | 0.0041519
28 | 0.0032712 | 0.00081983
29 | 0.0063499 | 0.0015914
30 | 0.012954 | 0.0032465
31 | 0.0026026 | 0.00065227
32 | 0.014518 | 0.0036386
33 | 0.003068 | 0.00076891
34 | 0.0051422 | 0.0012888
35 | 0.0050089 | 0.0012554
36 | 0.0032602 | 0.00081707
37 | 0.0027518 | 0.00068966
38 | 0.0021864 | 0.00054797
39 | 0.0031789 | 0.00079672
40 | 0.0011441 | 0.00028674
41 | 0.00081079 | 0.0002032
42 | 0.013904 | 0.0034846
43 | 0.016558 | 0.0041499

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1