## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-209_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-209_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-209_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-209_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-209_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-209_0_3_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1061-209_0_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1061-209_0_3_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_1061-209_0_3_node_68 | 0.4 | n |  | TRUE
9 | bus_LV_1061-209_0_3_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1061-209_0_3_node_132 | 0.4 | n |  | TRUE
11 | bus_LV_1061-209_0_3_node_78 | 0.4 | n |  | TRUE
12 | bus_LV_1061-209_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1061-209_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1061-209_0_3_node_147 | 0.4 | n |  | TRUE
15 | bus_LV_1061-209_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1061-209_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1061-209_0_3_node_60 | 0.4 | n |  | TRUE
18 | bus_LV_1061-209_0_3_node_130 | 0.4 | n |  | TRUE
19 | bus_LV_1061-209_0_3_node_59 | 0.4 | n |  | TRUE
20 | bus_LV_1061-209_0_3_node_134 | 0.4 | n |  | TRUE
21 | bus_LV_1061-209_0_3_node_131 | 0.4 | n |  | TRUE
22 | bus_LV_1061-209_0_3_node_144 | 0.4 | n |  | TRUE
23 | bus_LV_1061-209_0_3_node_146 | 0.4 | n |  | TRUE
24 | bus_LV_1061-209_0_3_node_128 | 0.4 | n |  | TRUE
25 | bus_LV_1061-209_0_3_node_129 | 0.4 | n |  | TRUE
26 | bus_LV_1061-209_0_3_node_9 | 0.4 | n |  | TRUE
27 | bus_LV_1061-209_0_3_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_1061-209_0_3_node_11 | 0.4 | n |  | TRUE
29 | bus_LV_1061-209_0_3_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_1061-209_0_3_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_1061-209_0_3_node_114 | 0.4 | n |  | TRUE
32 | bus_LV_1061-209_0_3_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_1061-209_0_3_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_1061-209_0_3_node_93 | 0.4 | n |  | TRUE
35 | bus_LV_1061-209_0_3_node_115 | 0.4 | n |  | TRUE
36 | bus_LV_1061-209_0_3_node_138 | 0.4 | n |  | TRUE
37 | bus_LV_1061-209_0_3_node_66 | 0.4 | n |  | TRUE
38 | bus_LV_1061-209_0_3_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1061-209_0_3_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_1061-209_0_3_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_1061-209_0_3_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_1061-209_0_3_node_89 | 0.4 | n |  | TRUE
43 | bus_LV_1061-209_0_3_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_1061-209_0_3_node_96 | 0.4 | n |  | TRUE
45 | bus_LV_1061-209_0_3_node_92 | 0.4 | n |  | TRUE
46 | bus_LV_1061-209_0_3_node_95 | 0.4 | n |  | TRUE
47 | bus_LV_1061-209_0_3_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_1061-209_0_3_node_61 | 0.4 | n |  | TRUE
49 | bus_LV_1061-209_0_3_node_67 | 0.4 | n |  | TRUE
50 | bus_LV_1061-209_0_3_node_90 | 0.4 | n |  | TRUE
51 | bus_LV_1061-209_0_3_node_19 | 0.4 | n |  | TRUE
52 | bus_LV_1061-209_0_3_node_20 | 0.4 | n |  | TRUE
53 | bus_LV_1061-209_0_3_node_21 | 0.4 | n |  | TRUE
54 | bus_LV_1061-209_0_3_node_22 | 0.4 | n |  | TRUE
55 | bus_LV_1061-209_0_3_node_23 | 0.4 | n |  | TRUE
56 | bus_LV_1061-209_0_3_node_24 | 0.4 | n |  | TRUE
57 | bus_LV_1061-209_0_3_node_30 | 0.4 | n |  | TRUE
58 | bus_LV_1061-209_0_3_node_137 | 0.4 | n |  | TRUE
59 | bus_LV_1061-209_0_3_node_82 | 0.4 | n |  | TRUE
60 | bus_LV_1061-209_0_3_node_140 | 0.4 | n |  | TRUE
61 | bus_LV_1061-209_0_3_node_25 | 0.4 | n |  | TRUE
62 | bus_LV_1061-209_0_3_node_26 | 0.4 | n |  | TRUE
63 | bus_LV_1061-209_0_3_node_27 | 0.4 | n |  | TRUE
64 | bus_LV_1061-209_0_3_node_28 | 0.4 | n |  | TRUE
65 | bus_LV_1061-209_0_3_node_29 | 0.4 | n |  | TRUE
66 | bus_LV_1061-209_0_3_node_133 | 0.4 | n |  | TRUE
67 | bus_LV_1061-209_0_3_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_1061-209_0_3_node_112 | 0.4 | n |  | TRUE
69 | bus_LV_1061-209_0_3_node_31 | 0.4 | n |  | TRUE
70 | bus_LV_1061-209_0_3_node_32 | 0.4 | n |  | TRUE
71 | bus_LV_1061-209_0_3_node_33 | 0.4 | n |  | TRUE
72 | bus_LV_1061-209_0_3_node_34 | 0.4 | n |  | TRUE
73 | bus_LV_1061-209_0_3_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_1061-209_0_3_node_35 | 0.4 | n |  | TRUE
75 | bus_LV_1061-209_0_3_node_36 | 0.4 | n |  | TRUE
76 | bus_LV_1061-209_0_3_node_37 | 0.4 | n |  | TRUE
77 | bus_LV_1061-209_0_3_node_38 | 0.4 | n |  | TRUE
78 | bus_LV_1061-209_0_3_node_39 | 0.4 | n |  | TRUE
79 | bus_LV_1061-209_0_3_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_1061-209_0_3_node_127 | 0.4 | n |  | TRUE
81 | bus_LV_1061-209_0_3_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_1061-209_0_3_node_126 | 0.4 | n |  | TRUE
83 | bus_LV_1061-209_0_3_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_1061-209_0_3_node_45 | 0.4 | n |  | TRUE
85 | bus_LV_1061-209_0_3_node_47 | 0.4 | n |  | TRUE
86 | bus_LV_1061-209_0_3_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_1061-209_0_3_node_124 | 0.4 | n |  | TRUE
88 | bus_LV_1061-209_0_3_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_1061-209_0_3_node_50 | 0.4 | n |  | TRUE
90 | bus_LV_1061-209_0_3_node_52 | 0.4 | n |  | TRUE
91 | bus_LV_1061-209_0_3_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_1061-209_0_3_node_113 | 0.4 | n |  | TRUE
93 | bus_LV_1061-209_0_3_node_53 | 0.4 | n |  | TRUE
94 | bus_LV_1061-209_0_3_node_54 | 0.4 | n |  | TRUE
95 | bus_LV_1061-209_0_3_node_55 | 0.4 | n |  | TRUE
96 | bus_LV_1061-209_0_3_node_56 | 0.4 | n |  | TRUE
97 | bus_LV_1061-209_0_3_node_57 | 0.4 | n |  | TRUE
98 | bus_LV_1061-209_0_3_node_71 | 0.4 | n |  | TRUE
99 | bus_LV_1061-209_0_3_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_1061-209_0_3_node_121 | 0.4 | n |  | TRUE
101 | bus_LV_1061-209_0_3_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_1061-209_0_3_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_1061-209_0_3_node_64 | 0.4 | n |  | TRUE
104 | bus_LV_1061-209_0_3_node_65 | 0.4 | n |  | TRUE
105 | bus_LV_1061-209_0_3_node_104 | 0.4 | n |  | TRUE
106 | bus_LV_1061-209_0_3_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_1061-209_0_3_node_74 | 0.4 | n |  | TRUE
108 | bus_LV_1061-209_0_3_node_75 | 0.4 | n |  | TRUE
109 | bus_LV_1061-209_0_3_node_118 | 0.4 | n |  | TRUE
110 | bus_LV_1061-209_0_3_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_1061-209_0_3_node_76 | 0.4 | n |  | TRUE
112 | bus_LV_1061-209_0_3_node_77 | 0.4 | n |  | TRUE
113 | bus_LV_1061-209_0_3_node_79 | 0.4 | n |  | TRUE
114 | bus_LV_1061-209_0_3_node_81 | 0.4 | n |  | TRUE
115 | bus_LV_1061-209_0_3_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_1061-209_0_3_node_143 | 0.4 | n |  | TRUE
117 | bus_LV_1061-209_0_3_node_100 | 0.4 | n |  | TRUE
118 | bus_LV_1061-209_0_3_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_1061-209_0_3_node_85 | 0.4 | n |  | TRUE
120 | bus_LV_1061-209_0_3_node_91 | 0.4 | n |  | TRUE
121 | bus_LV_1061-209_0_3_node_83 | 0.4 | n |  | TRUE
122 | bus_LV_1061-209_0_3_node_84 | 0.4 | n |  | TRUE
123 | bus_LV_1061-209_0_3_node_86 | 0.4 | n |  | TRUE
124 | bus_LV_1061-209_0_3_node_88 | 0.4 | n |  | TRUE
125 | bus_LV_1061-209_0_3_node_101 | 0.4 | n |  | TRUE
126 | bus_LV_1061-209_0_3_node_136 | 0.4 | n |  | TRUE
127 | bus_LV_1061-209_0_3_node_135 | 0.4 | n |  | TRUE
128 | bus_LV_1061-209_0_3_node_98 | 0.4 | n |  | TRUE
129 | bus_LV_1061-209_0_3_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_1061-209_0_3_node_116 | 0.4 | n |  | TRUE
131 | bus_LV_1061-209_0_3_node_117 | 0.4 | n |  | TRUE
132 | bus_LV_1061-209_0_3_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_1061-209_0_3_node_119 | 0.4 | n |  | TRUE
134 | bus_LV_1061-209_0_3_node_141 | 0.4 | n |  | TRUE
135 | bus_LV_1061-209_0_3_node_99 | 0.4 | n |  | TRUE
136 | bus_LV_1061-209_0_3_node_142 | 0.4 | n |  | TRUE
137 | bus_LV_1061-209_0_3_node_109 | 0.4 | n |  | TRUE
138 | bus_LV_1061-209_0_3_node_108 | 0.4 | n |  | TRUE
139 | bus_LV_1061-209_0_3_node_103 | 0.4 | n |  | TRUE
140 | bus_LV_1061-209_0_3_node_106 | 0.4 | n |  | TRUE
141 | bus_LV_1061-209_0_3_node_107 | 0.4 | n |  | TRUE
142 | bus_LV_1061-209_0_3_node_110 | 0.4 | n |  | TRUE
143 | bus_LV_1061-209_0_3_node_123 | 0.4 | n |  | TRUE
144 | bus_LV_1061-209_0_3_node_145 | 0.4 | n |  | TRUE
145 | bus_MV_218_0_node_4 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-209_0_3_load_0 | 0 | 0.0027059 | 0.00067816 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-209_0_3_load_1 | 1 | 0.0025824 | 0.00064722 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-209_0_3_load_2 | 2 | 0.0027084 | 0.00067879 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-209_0_3_load_4 | 4 | 0.0045499 | 0.0011403 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-209_0_3_load_18 | 5 | 0.0023518 | 0.00058942 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-209_0_3_load_16 | 6 | 0.002421 | 0.00060677 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-209_0_3_load_68 | 8 | 0.0021187 | 0.00053101 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-209_0_3_load_132 | 10 | 0.0021901 | 0.00054889 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-209_0_3_load_5 | 12 | 0.0025801 | 0.00064662 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-209_0_3_load_147 | 14 | 0.0027362 | 0.00068575 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-209_0_3_load_60 | 17 | 0.003715 | 0.00093106 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-209_0_3_load_59 | 19 | 0.003715 | 0.00093106 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-209_0_3_load_134 | 20 | 0.0028787 | 0.00072146 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-209_0_3_load_146 | 23 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-209_0_3_load_128 | 24 | 0.0032961 | 0.00082608 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-209_0_3_load_129 | 25 | 0.0035434 | 0.00088807 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-209_0_3_load_9 | 26 | 0.0036144 | 0.00090585 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-209_0_3_load_10 | 27 | 0.0021167 | 0.0005305 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-209_0_3_load_12 | 29 | 0.0021179 | 0.00053078 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-209_0_3_load_114 | 31 | 0.0029097 | 0.00072924 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-209_0_3_load_115 | 35 | 0.0041739 | 0.0010461 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-209_0_3_load_138 | 36 | 0.0027 | 0.00067669 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-209_0_3_load_66 | 37 | 0.0044721 | 0.0011208 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-209_0_3_load_43 | 38 | 0.0056889 | 0.0014258 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-209_0_3_load_69 | 41 | 0.0023503 | 0.00058904 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-209_0_3_load_89 | 42 | 0.0023504 | 0.00058906 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-209_0_3_load_46 | 43 | 0.0026051 | 0.00065291 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-209_0_3_load_96 | 44 | 0.0023246 | 0.0005826 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-209_0_3_load_92 | 45 | 0.002388 | 0.00059849 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-209_0_3_load_41 | 47 | 0.0027026 | 0.00067734 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-209_0_3_load_61 | 48 | 0.0023518 | 0.00058942 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-209_0_3_load_67 | 49 | 0.0021167 | 0.0005305 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-209_0_3_load_90 | 50 | 0.0025842 | 0.00064766 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1061-209_0_3_load_19 | 51 | 0.0022516 | 0.00056431 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1061-209_0_3_load_20 | 52 | 0.0025825 | 0.00064722 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1061-209_0_3_load_21 | 53 | 0.0025844 | 0.00064771 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1061-209_0_3_load_22 | 54 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1061-209_0_3_load_23 | 55 | 0.0025842 | 0.00064767 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1061-209_0_3_load_24 | 56 | 0.0025842 | 0.00064767 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1061-209_0_3_load_30 | 57 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1061-209_0_3_load_137 | 58 | 0.0017618 | 0.00044154 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1061-209_0_3_load_82 | 59 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1061-209_0_3_load_140 | 60 | 0.0017619 | 0.00044157 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1061-209_0_3_load_25 | 61 | 0.0016026 | 0.00040165 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1061-209_0_3_load_26 | 62 | 0.0014533 | 0.00036423 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1061-209_0_3_load_27 | 63 | 0.001636 | 0.00041003 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1061-209_0_3_load_28 | 64 | 0.001454 | 0.00036441 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1061-209_0_3_load_29 | 65 | 0.0024124 | 0.00060461 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1061-209_0_3_load_133 | 66 | 0.0014534 | 0.00036425 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1061-209_0_3_load_58 | 67 | 0.0037126 | 0.00093046 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1061-209_0_3_load_112 | 68 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1061-209_0_3_load_31 | 69 | 0.0050316 | 0.001261 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1061-209_0_3_load_33 | 71 | 0.0035022 | 0.00087773 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1061-209_0_3_load_34 | 72 | 0.003808 | 0.00095436 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1061-209_0_3_load_42 | 73 | 0.0043656 | 0.0010941 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1061-209_0_3_load_35 | 74 | 0.0024021 | 0.00060203 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1061-209_0_3_load_36 | 75 | 0.0020373 | 0.0005106 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1061-209_0_3_load_38 | 77 | 0.0020362 | 0.00051033 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1061-209_0_3_load_51 | 79 | 0.0018313 | 0.00045898 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1061-209_0_3_load_127 | 80 | 0.0021016 | 0.0005267 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1061-209_0_3_load_49 | 81 | 0.0022621 | 0.00056693 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1061-209_0_3_load_126 | 82 | 0.0021016 | 0.0005267 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1061-209_0_3_load_44 | 83 | 0.0026055 | 0.000653 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1061-209_0_3_load_45 | 84 | 0.0026055 | 0.000653 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1061-209_0_3_load_47 | 85 | 0.0026051 | 0.00065291 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1061-209_0_3_load_124 | 87 | 0.0047673 | 0.0011948 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1061-209_0_3_load_122 | 88 | 0.0049445 | 0.0012392 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1061-209_0_3_load_50 | 89 | 0.0023803 | 0.00059656 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1061-209_0_3_load_52 | 90 | 0.0022633 | 0.00056723 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1061-209_0_3_load_70 | 91 | 0.0026431 | 0.00066242 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1061-209_0_3_load_113 | 92 | 0.0046854 | 0.0011743 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1061-209_0_3_load_53 | 93 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1061-209_0_3_load_54 | 94 | 0.0017612 | 0.00044139 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1061-209_0_3_load_55 | 95 | 0.0017619 | 0.00044156 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1061-209_0_3_load_56 | 96 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1061-209_0_3_load_57 | 97 | 0.0025841 | 0.00064764 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1061-209_0_3_load_71 | 98 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1061-209_0_3_load_73 | 99 | 0.0025825 | 0.00064723 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1061-209_0_3_load_121 | 100 | 0.0017612 | 0.0004414 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1061-209_0_3_load_72 | 101 | 0.0025844 | 0.00064771 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1061-209_0_3_load_62 | 102 | 0.0023503 | 0.00058904 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1061-209_0_3_load_64 | 103 | 0.0027878 | 0.00069868 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1061-209_0_3_load_65 | 104 | 0.0025824 | 0.00064722 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1061-209_0_3_load_104 | 105 | 0.0025842 | 0.00064766 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1061-209_0_3_load_102 | 106 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1061-209_0_3_load_74 | 107 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1061-209_0_3_load_75 | 108 | 0.0025842 | 0.00064767 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1061-209_0_3_load_118 | 109 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1061-209_0_3_load_105 | 110 | 0.0025826 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1061-209_0_3_load_76 | 111 | 0.0023325 | 0.00058458 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1061-209_0_3_load_77 | 112 | 0.0023336 | 0.00058485 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1061-209_0_3_load_79 | 113 | 0.0023334 | 0.0005848 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1061-209_0_3_load_143 | 116 | 0.00099222 | 0.00024867 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1061-209_0_3_load_100 | 117 | 0.0042928 | 0.0010759 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1061-209_0_3_load_97 | 118 | 0.0057983 | 0.0014532 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1061-209_0_3_load_91 | 120 | 0.0025825 | 0.00064725 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1061-209_0_3_load_83 | 121 | 0.0037384 | 0.00093693 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1061-209_0_3_load_84 | 122 | 0.001218 | 0.00030525 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1061-209_0_3_load_88 | 124 | 0.0035274 | 0.00088404 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1061-209_0_3_load_101 | 125 | 0.0014532 | 0.00036421 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1061-209_0_3_load_136 | 126 | 0.003525 | 0.00088346 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1061-209_0_3_load_135 | 127 | 0.0043379 | 0.0010872 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1061-209_0_3_load_98 | 128 | 0.0017117 | 0.00042899 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1061-209_0_3_load_116 | 130 | 0.003166 | 0.00079349 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1061-209_0_3_load_117 | 131 | 0.0028949 | 0.00072553 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1061-209_0_3_load_119 | 133 | 0.0034901 | 0.0008747 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1061-209_0_3_load_141 | 134 | 0.0044871 | 0.0011246 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1061-209_0_3_load_99 | 135 | 0.0018142 | 0.00045467 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1061-209_0_3_load_142 | 136 | 0.0025842 | 0.00064766 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1061-209_0_3_load_109 | 137 | 0.0048964 | 0.0012271 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1061-209_0_3_load_103 | 139 | 0.0025842 | 0.00064767 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1061-209_0_3_load_106 | 140 | 0.0037066 | 0.00092896 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1061-209_0_3_load_107 | 141 | 0.003499 | 0.00087693 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1061-209_0_3_load_110 | 142 | 0.0033365 | 0.00083621 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1061-209_0_3_load_123 | 143 | 0.0035744 | 0.00089582 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1061-209_0_3_load_145 | 144 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-209_0_3_line_0 |  | 0 | 1 | 0.011066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-209_0_3_line_1 |  | 0 | 2 | 0.0077083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-209_0_3_line_2 |  | 1 | 3 | 0.023109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1061-209_0_3_line_3 |  | 2 | 4 | 0.021692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-209_0_3_line_4 |  | 3 | 5 | 0.0096319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1061-209_0_3_line_5 |  | 3 | 6 | 0.012453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-209_0_3_line_6 |  | 4 | 7 | 0.0069122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-209_0_3_line_7 |  | 5 | 8 | 0.003456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1061-209_0_3_line_8 |  | 6 | 9 | 0.030951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-209_0_3_line_9 |  | 7 | 10 | 0.01625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-209_0_3_line_10 |  | 7 | 11 | 0.00383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-209_0_3_line_11 |  | 8 | 49 | 6.8171e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-209_0_3_line_12 |  | 9 | 51 | 0.049752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-209_0_3_line_13 |  | 10 | 114 | 0.001835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-209_0_3_line_14 |  | 11 | 111 | 0.012486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-209_0_3_line_15 |  | 12 | 13 | 0.053594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-209_0_3_line_16 |  | 12 | 14 | 0.058373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-209_0_3_line_17 |  | 13 | 15 | 0.00455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-209_0_3_line_18 |  | 15 | 16 | 0.052329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-209_0_3_line_19 |  | 15 | 17 | 0.0067566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-209_0_3_line_20 |  | 16 | 18 | 0.005489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-209_0_3_line_21 |  | 17 | 19 | 0.016396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-209_0_3_line_22 |  | 18 | 20 | 0.022129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-209_0_3_line_23 |  | 19 | 67 | 0.019332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-209_0_3_line_24 |  | 20 | 142 | 0.022516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-209_0_3_line_25 |  | 21 | 22 | 0.004944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-209_0_3_line_26 |  | 21 | 23 | 0.037702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-209_0_3_line_27 |  | 22 | 144 | 0.010986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-209_0_3_line_28 |  | 22 | 100 | 0.011899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-209_0_3_line_29 |  | 23 | 60 | 5.5609e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-209_0_3_line_30 |  | 24 | 25 | 0.020451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-209_0_3_line_31 |  | 25 | 129 | 0.0072012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-209_0_3_line_32 |  | 26 | 27 | 0.00045342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-209_0_3_line_33 |  | 26 | 28 | 0.018778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1061-209_0_3_line_34 |  | 27 | 29 | 0.00014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1061-209_0_3_line_35 |  | 28 | 30 | 0.00246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1061-209_0_3_line_36 |  | 29 | 31 | 0.016489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1061-209_0_3_line_37 |  | 30 | 36 | 0.013248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1061-209_0_3_line_38 |  | 30 | 37 | 0.032083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1061-209_0_3_line_39 |  | 30 | 38 | 0.014492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1061-209_0_3_line_40 |  | 32 | 33 | 0.003503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1061-209_0_3_line_41 |  | 32 | 34 | 0.004898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1061-209_0_3_line_42 |  | 32 | 35 | 0.020144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1061-209_0_3_line_43 |  | 33 | 36 | 0.026133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1061-209_0_3_line_44 |  | 33 | 43 | 0.0090455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1061-209_0_3_line_45 |  | 34 | 44 | 0.012606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1061-209_0_3_line_46 |  | 34 | 45 | 0.017962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1061-209_0_3_line_47 |  | 35 | 46 | 0.0082772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1061-209_0_3_line_48 |  | 37 | 40 | 0.013858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1061-209_0_3_line_49 |  | 38 | 47 | 0.0037529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1061-209_0_3_line_50 |  | 39 | 40 | 0.003326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1061-209_0_3_line_51 |  | 39 | 41 | 0.015029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_1061-209_0_3_line_52 |  | 39 | 42 | 0.0093961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1061-209_0_3_line_53 |  | 40 | 48 | 0.010035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1061-209_0_3_line_54 |  | 41 | 49 | 0.00315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_1061-209_0_3_line_55 |  | 42 | 50 | 0.03162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1061-209_0_3_line_56 |  | 43 | 83 | 0.0071425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1061-209_0_3_line_57 |  | 44 | 132 | 0.014797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1061-209_0_3_line_58 |  | 46 | 130 | 0.006182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1061-209_0_3_line_59 |  | 46 | 131 | 0.017466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1061-209_0_3_line_60 |  | 47 | 73 | 0.017946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1061-209_0_3_line_61 |  | 48 | 102 | 0.0066759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1061-209_0_3_line_62 |  | 50 | 120 | 5.5601e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1061-209_0_3_line_63 |  | 52 | 53 | 0.027772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1061-209_0_3_line_64 |  | 52 | 54 | 5.4933e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1061-209_0_3_line_65 |  | 53 | 55 | 6.0664e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1061-209_0_3_line_66 |  | 54 | 56 | 5.5607e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1061-209_0_3_line_67 |  | 55 | 57 | 5.5613e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1061-209_0_3_line_68 |  | 56 | 58 | 0.027242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1061-209_0_3_line_69 |  | 57 | 59 | 0.02784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1061-209_0_3_line_70 |  | 58 | 60 | 5.4935e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1061-209_0_3_line_71 |  | 59 | 68 | 5.3136e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1061-209_0_3_line_72 |  | 61 | 62 | 0.018859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1061-209_0_3_line_73 |  | 61 | 63 | 0.018486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1061-209_0_3_line_74 |  | 62 | 64 | 0.021987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1061-209_0_3_line_75 |  | 63 | 65 | 0.017082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1061-209_0_3_line_76 |  | 64 | 66 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1061-209_0_3_line_77 |  | 65 | 67 | 0.020864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1061-209_0_3_line_78 |  | 68 | 120 | 0.028231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1061-209_0_3_line_79 |  | 69 | 70 | 0.0018046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1061-209_0_3_line_80 |  | 70 | 71 | 0.009275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1061-209_0_3_line_81 |  | 70 | 72 | 0.016048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1061-209_0_3_line_82 |  | 72 | 73 | 0.0024554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1061-209_0_3_line_83 |  | 74 | 75 | 0.017867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1061-209_0_3_line_84 |  | 74 | 76 | 0.072769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1061-209_0_3_line_85 |  | 75 | 77 | 0.023606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1061-209_0_3_line_86 |  | 76 | 78 | 0.011058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1061-209_0_3_line_87 |  | 77 | 79 | 0.0034323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1061-209_0_3_line_88 |  | 78 | 80 | 0.069748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1061-209_0_3_line_89 |  | 79 | 81 | 0.019382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1061-209_0_3_line_90 |  | 80 | 82 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1061-209_0_3_line_91 |  | 81 | 89 | 0.0011048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1061-209_0_3_line_92 |  | 82 | 116 | 0.010617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1061-209_0_3_line_93 |  | 82 | 113 | 0.022817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1061-209_0_3_line_94 |  | 83 | 84 | 0.017818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1061-209_0_3_line_95 |  | 84 | 85 | 0.007143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1061-209_0_3_line_96 |  | 85 | 86 | 0.0092799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1061-209_0_3_line_97 |  | 86 | 87 | 0.007298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1061-209_0_3_line_98 |  | 86 | 88 | 0.010994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1061-209_0_3_line_99 |  | 88 | 143 | 0.014135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1061-209_0_3_line_100 |  | 89 | 90 | 0.021548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1061-209_0_3_line_101 |  | 90 | 91 | 0.00054773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1061-209_0_3_line_102 |  | 91 | 92 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1061-209_0_3_line_103 |  | 93 | 94 | 7.1821e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1061-209_0_3_line_104 |  | 93 | 95 | 0.028257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1061-209_0_3_line_105 |  | 94 | 96 | 7.1021e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1061-209_0_3_line_106 |  | 95 | 97 | 1.3423e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1061-209_0_3_line_107 |  | 96 | 98 | 0.026622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1061-209_0_3_line_108 |  | 97 | 99 | 6.0989e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1061-209_0_3_line_109 |  | 98 | 100 | 9.9805e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1061-209_0_3_line_110 |  | 99 | 101 | 0.028228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1061-209_0_3_line_111 |  | 101 | 107 | 3.5796e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1061-209_0_3_line_112 |  | 102 | 103 | 0.0066722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1061-209_0_3_line_113 |  | 104 | 105 | 7.3873e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1061-209_0_3_line_114 |  | 105 | 106 | 7.2081e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1061-209_0_3_line_115 |  | 106 | 139 | 0.027645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1061-209_0_3_line_116 |  | 107 | 108 | 3.3213e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1061-209_0_3_line_117 |  | 108 | 109 | 0.028274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1061-209_0_3_line_118 |  | 109 | 110 | 9.8278e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1061-209_0_3_line_119 |  | 110 | 139 | 1.2294e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1061-209_0_3_line_120 |  | 111 | 112 | 0.023397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1061-209_0_3_line_121 |  | 112 | 113 | 0.022653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1061-209_0_3_line_122 |  | 114 | 115 | 0.034482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1061-209_0_3_line_123 |  | 115 | 117 | 0.010688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1061-209_0_3_line_124 |  | 115 | 118 | 0.029355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1061-209_0_3_line_125 |  | 115 | 119 | 0.00266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1061-209_0_3_line_126 |  | 118 | 128 | 0.017284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1061-209_0_3_line_127 |  | 119 | 124 | 0.012788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1061-209_0_3_line_128 |  | 119 | 121 | 0.0076118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1061-209_0_3_line_129 |  | 121 | 122 | 0.019394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1061-209_0_3_line_130 |  | 122 | 123 | 0.0058531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1061-209_0_3_line_131 |  | 123 | 125 | 0.018008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1061-209_0_3_line_132 |  | 124 | 126 | 0.020816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1061-209_0_3_line_133 |  | 125 | 127 | 0.02282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1061-209_0_3_line_134 |  | 126 | 129 | 0.013608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1061-209_0_3_line_135 |  | 128 | 135 | 0.0056843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1061-209_0_3_line_136 |  | 129 | 138 | 0.002577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1061-209_0_3_line_137 |  | 131 | 133 | 0.00088598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1061-209_0_3_line_138 |  | 132 | 134 | 0.016589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1061-209_0_3_line_139 |  | 135 | 136 | 0.0043048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1061-209_0_3_line_140 |  | 137 | 138 | 0.013646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1061-209_0_3_line_141 |  | 138 | 142 | 0.010473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1061-209_0_3_line_142 |  | 138 | 140 | 0.028021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1061-209_0_3_line_143 |  | 140 | 141 | 0.014999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-209_0_3_trafo_1 | 0.63 MVA 20/0.4 kV | 145 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2663566.734 | 1213214.7954 | 2663555.6753 | 1213214.3814
1 | 2663566.734 | 1213214.7954 | 2663574.437 | 1213215.0837
2 | 2663546.077 | 1213235.4032 | 2663555.6753 | 1213214.3814
3 | 2663574.437 | 1213215.0837 | 2663596.1139 | 1213215.8952
4 | 2663546.077 | 1213235.4032 | 2663537.2734 | 1213231.4955
5 | 2663546.077 | 1213235.4032 | 2663557.9091 | 1213239.2872
6 | 2663603.0213 | 1213216.1537 | 2663596.1139 | 1213215.8952
7 | 2663534.1147 | 1213230.0934 | 2663537.2734 | 1213231.4955
8 | 2663557.7007 | 1213270.2374 | 2663557.9091 | 1213239.2872
9 | 2663603.0213 | 1213216.1537 | 2663619.2604 | 1213216.7466
10 | 2663602.8665 | 1213219.9767 | 2663603.0151 | 1213218.1549 | 2663603.0213 | 1213216.1537
11 | 2663534.0523 | 1213230.0657 | 2663534.1147 | 1213230.0934
12 | 2663557.7007 | 1213270.2374 | 2663557.569 | 1213289.7146 | 2663555.0738 | 1213319.8856
13 | 2663621.0941 | 1213216.8135 | 2663619.2604 | 1213216.7466
14 | 2663602.8665 | 1213219.9767 | 2663602.367 | 1213232.4522
15 | 2663680.0831 | 1213124.2303 | 2663684.9692 | 1213131.9205 | 2663688.024 | 1213141.081 | 2663689.9885 | 1213175.8515
16 | 2663689.9885 | 1213175.8515 | 2663745.5422 | 1213157.9284
17 | 2663680.0831 | 1213124.2303 | 2663677.2871 | 1213127.8249
18 | 2663677.2871 | 1213127.8249 | 2663675.2111 | 1213123.7447 | 2663671.7379 | 1213120.3277 | 2663650.936 | 1213103.4509 | 2663638.9195 | 1213092.6272
19 | 2663677.2871 | 1213127.8249 | 2663675.4958 | 1213130.5185 | 2663675.1163 | 1213134.0198
20 | 2663634.8952 | 1213088.8819 | 2663638.9195 | 1213092.6272
21 | 2663675.1163 | 1213134.0198 | 2663674.906 | 1213135.96 | 2663677.6897 | 1213150.1337
22 | 2663634.8952 | 1213088.8819 | 2663633.9858 | 1213109.3182 | 2663633.9108 | 1213110.9887
23 | 2663680.311 | 1213169.2486 | 2663680.2648 | 1213166.247 | 2663679.3874 | 1213158.7775 | 2663677.6897 | 1213150.1337
24 | 2663632.9009 | 1213133.4824 | 2663633.9108 | 1213110.9887
25 | 2663599.1301 | 1213051.0884 | 2663596.187 | 1213047.1102
26 | 2663599.1301 | 1213051.0884 | 2663596.2325 | 1213054.2373 | 2663582.0711 | 1213084.512
27 | 2663596.187 | 1213047.1102 | 2663590.593 | 1213039.5348 | 2663589.8567 | 1213038.1498
28 | 2663596.187 | 1213047.1102 | 2663595.3551 | 1213050.3144 | 2663591.7683 | 1213058.1178
29 | 2663582.0476 | 1213084.5624 | 2663582.0711 | 1213084.512
30 | 2663636.5467 | 1213116.4516 | 2663635.4122 | 1213136.8715
31 | 2663635.0127 | 1213144.0616 | 2663635.4122 | 1213136.8715
32 | 2663514.1822 | 1213272.1939 | 2663513.7738 | 1213271.9969
33 | 2663496.8598 | 1213263.8411 | 2663513.7738 | 1213271.9969
34 | 2663514.3088 | 1213272.2549 | 2663514.1822 | 1213272.1939
35 | 2663494.6378 | 1213262.7723 | 2663496.8598 | 1213263.8411
36 | 2663529.1615 | 1213279.4168 | 2663514.3088 | 1213272.2549
37 | 2663494.6378 | 1213262.7723 | 2663490.7199 | 1213271.158 | 2663488.9815 | 1213274.7517
38 | 2663494.6378 | 1213262.7723 | 2663501.3619 | 1213248.4017 | 2663508.3951 | 1213233.7888
39 | 2663494.6378 | 1213262.7723 | 2663481.5831 | 1213256.4794
40 | 2663479.9021 | 1213299.0156 | 2663477.2185 | 1213297.7752 | 2663476.712 | 1213297.5474
41 | 2663479.9021 | 1213299.0156 | 2663477.7736 | 1213303.429
42 | 2663479.9021 | 1213299.0156 | 2663483.0997 | 1213300.4839 | 2663484.6838 | 1213302.9578 | 2663486.4803 | 1213304.7558 | 2663496.5595 | 1213309.5151
43 | 2663476.712 | 1213297.5474 | 2663478.5032 | 1213296.2657 | 2663481.7794 | 1213289.6409 | 2663488.9815 | 1213274.7517
44 | 2663476.712 | 1213297.5474 | 2663474.0099 | 1213298.0412 | 2663471.2494 | 1213297.6116 | 2663468.0996 | 1213296.0741
45 | 2663477.7736 | 1213303.429 | 2663466.3974 | 1213297.9992
46 | 2663477.7736 | 1213303.429 | 2663469.9715 | 1213319.6075
47 | 2663500.6218 | 1213314.3233 | 2663501.6804 | 1213311.9331 | 2663496.5595 | 1213309.5151
48 | 2663514.4052 | 1213221.3017 | 2663508.3951 | 1213233.7888
49 | 2663478.2025 | 1213254.8498 | 2663481.5831 | 1213256.4794
50 | 2663514.4052 | 1213221.3017 | 2663517.4366 | 1213222.6904
51 | 2663517.4366 | 1213222.6904 | 2663531.1732 | 1213228.7877
52 | 2663517.4366 | 1213222.6904 | 2663521.4178 | 1213214.1793
53 | 2663514.4052 | 1213221.3017 | 2663505.2785 | 1213217.1291
54 | 2663531.1732 | 1213228.7877 | 2663534.0523 | 1213230.0657
55 | 2663521.4178 | 1213214.1793 | 2663534.8153 | 1213185.5376
56 | 2663461.681 | 1213292.9409 | 2663468.0996 | 1213296.0741
57 | 2663453.0435 | 1213291.6253 | 2663466.3974 | 1213297.9992
58 | 2663500.6218 | 1213314.3233 | 2663497.8509 | 1213319.8528
59 | 2663500.6218 | 1213314.3233 | 2663516.3881 | 1213321.8393
60 | 2663478.2025 | 1213254.8498 | 2663462.0367 | 1213247.0572
61 | 2663505.2785 | 1213217.1291 | 2663499.2071 | 1213214.3534
62 | 2663534.8153 | 1213185.5376 | 2663534.8388 | 1213185.4872
63 | 2663570.4349 | 1213109.3884 | 2663558.668 | 1213134.5443
64 | 2663570.4349 | 1213109.3884 | 2663570.4582 | 1213109.3386
65 | 2663558.6423 | 1213134.5992 | 2663558.668 | 1213134.5443
66 | 2663570.4582 | 1213109.3386 | 2663570.4818 | 1213109.2883
67 | 2663558.6187 | 1213134.6496 | 2663558.6423 | 1213134.5992
68 | 2663582.0243 | 1213084.6121 | 2663570.4818 | 1213109.2883
69 | 2663546.8227 | 1213159.8675 | 2663558.6187 | 1213134.6496
70 | 2663582.0243 | 1213084.6121 | 2663582.0476 | 1213084.5624
71 | 2663546.8002 | 1213159.9157 | 2663546.8227 | 1213159.8675
72 | 2663676.1781 | 1213225.4608 | 2663675.785 | 1213229.3492 | 2663674.8718 | 1213244.2724
73 | 2663678.0379 | 1213207.0681 | 2663676.1781 | 1213225.4608
74 | 2663674.8718 | 1213244.2724 | 2663674.3769 | 1213252.3594 | 2663671.2725 | 1213252.115 | 2663660.5187 | 1213251.5171
75 | 2663678.0379 | 1213207.0681 | 2663679.7563 | 1213190.0728
76 | 2663645.7713 | 1213248.5185 | 2663645.5355 | 1213250.6839 | 2663660.5187 | 1213251.5171
77 | 2663680.311 | 1213169.2486 | 2663680.516 | 1213182.5597 | 2663679.7563 | 1213190.0728
78 | 2663534.8388 | 1213185.4872 | 2663546.8002 | 1213159.9157
79 | 2663445.3687 | 1213239.0224 | 2663443.7429 | 1213238.2393
80 | 2663445.3687 | 1213239.0224 | 2663441.3976 | 1213247.4076
81 | 2663445.3687 | 1213239.0224 | 2663459.8248 | 1213245.991
82 | 2663462.0367 | 1213247.0572 | 2663459.8248 | 1213245.991
83 | 2663573.8687 | 1213325.3422 | 2663573.2071 | 1213343.1971
84 | 2663595.2349 | 1213405.5763 | 2663580.4848 | 1213397.5474 | 2663577.0187 | 1213393.4746 | 2663575.4589 | 1213388.7329 | 2663573.001 | 1213357.7876 | 2663573.1361 | 1213345.1146 | 2663573.2071 | 1213343.1971
85 | 2663574.7427 | 1213301.7526 | 2663573.8687 | 1213325.3422
86 | 2663595.8767 | 1213394.543 | 2663595.6394 | 1213401.1223 | 2663595.2349 | 1213405.5763
87 | 2663574.7427 | 1213301.7526 | 2663574.8698 | 1213298.3226
88 | 2663595.8767 | 1213394.543 | 2663598.6673 | 1213324.8505
89 | 2663575.5874 | 1213278.9537 | 2663574.8698 | 1213298.3226
90 | 2663599.6116 | 1213301.2654 | 2663598.6673 | 1213324.8505
91 | 2663575.5874 | 1213278.9537 | 2663575.6283 | 1213277.8497
92 | 2663599.6116 | 1213301.2654 | 2663602.4298 | 1213291.0289
93 | 2663599.6116 | 1213301.2654 | 2663600.5245 | 1213278.4662
94 | 2663461.681 | 1213292.9409 | 2663456.8831 | 1213290.5989 | 2663445.6407 | 1213285.1817
95 | 2663445.6407 | 1213285.1817 | 2663439.2058 | 1213282.081
96 | 2663432.1301 | 1213281.6524 | 2663433.2651 | 1213279.2185 | 2663439.2058 | 1213282.081
97 | 2663432.1301 | 1213281.6524 | 2663428.923 | 1213288.2112
98 | 2663432.1301 | 1213281.6524 | 2663422.2066 | 1213276.921
99 | 2663409.448 | 1213270.8379 | 2663422.2066 | 1213276.921
100 | 2663575.6283 | 1213277.8497 | 2663576.4262 | 1213256.3164
101 | 2663576.4464 | 1213255.7691 | 2663576.4262 | 1213256.3164
102 | 2663576.9973 | 1213240.9027 | 2663576.4464 | 1213255.7691
103 | 2663580.4233 | 1213082.312 | 2663580.4236 | 1213082.3114
104 | 2663580.4233 | 1213082.312 | 2663573.1319 | 1213097.5733 | 2663568.2397 | 1213107.8075
105 | 2663580.4236 | 1213082.3114 | 2663580.4239 | 1213082.3107
106 | 2663568.2391 | 1213107.8087 | 2663568.2397 | 1213107.8075
107 | 2663591.7266 | 1213058.2085 | 2663586.3335 | 1213069.9414 | 2663580.4239 | 1213082.3107
108 | 2663568.2365 | 1213107.8142 | 2663568.2391 | 1213107.8087
109 | 2663591.7266 | 1213058.2085 | 2663591.7683 | 1213058.1178
110 | 2663556.1124 | 1213133.3053 | 2663560.8009 | 1213123.3689 | 2663568.2365 | 1213107.8142
111 | 2663556.0971 | 1213133.3377 | 2663556.1124 | 1213133.3053
112 | 2663493.1389 | 1213211.5791 | 2663499.2071 | 1213214.3534
113 | 2663532.1405 | 1213184.0872 | 2663532.1716 | 1213184.0202
114 | 2663532.1716 | 1213184.0202 | 2663532.202 | 1213183.9549
115 | 2663532.202 | 1213183.9549 | 2663537.1986 | 1213173.2037 | 2663543.9812 | 1213158.9451
116 | 2663556.0829 | 1213133.3677 | 2663556.0971 | 1213133.3377
117 | 2663543.9907 | 1213158.9252 | 2663548.0699 | 1213150.3499 | 2663556.0829 | 1213133.3677
118 | 2663543.9865 | 1213158.934 | 2663543.9907 | 1213158.9252
119 | 2663543.9812 | 1213158.9451 | 2663543.9865 | 1213158.934
120 | 2663602.367 | 1213232.4522 | 2663601.4309 | 1213255.8309
121 | 2663601.4309 | 1213255.8309 | 2663600.5245 | 1213278.4662
122 | 2663630.492 | 1213191.109 | 2663629.6148 | 1213217.0712 | 2663621.0941 | 1213216.8135
123 | 2663630.492 | 1213191.109 | 2663630.9311 | 1213180.4296
124 | 2663630.492 | 1213191.109 | 2663601.1688 | 1213189.753
125 | 2663630.492 | 1213191.109 | 2663633.157 | 1213191.2375
126 | 2663583.9034 | 1213188.9547 | 2663601.1688 | 1213189.753
127 | 2663633.157 | 1213191.2375 | 2663633.6597 | 1213178.4589
128 | 2663633.157 | 1213191.2375 | 2663632.8202 | 1213198.8418
129 | 2663632.8202 | 1213198.8418 | 2663632.0061 | 1213217.219 | 2663631.9622 | 1213218.217
130 | 2663631.7052 | 1213224.0645 | 2663631.9622 | 1213218.217
131 | 2663631.7052 | 1213224.0645 | 2663630.3054 | 1213242.0176
132 | 2663634.4779 | 1213157.6593 | 2663633.6597 | 1213178.4589
133 | 2663637.3361 | 1213262.4195 | 2663631.4822 | 1213254.9255 | 2663629.6369 | 1213250.5921 | 2663630.3054 | 1213242.0176
134 | 2663635.0127 | 1213144.0616 | 2663634.4779 | 1213157.6593
135 | 2663578.2252 | 1213188.6921 | 2663583.9034 | 1213188.9547
136 | 2663632.4311 | 1213143.9451 | 2663635.0127 | 1213144.0616
137 | 2663517.1878 | 1213322.2206 | 2663516.3881 | 1213321.8393
138 | 2663453.0435 | 1213291.6253 | 2663445.9936 | 1213306.6485
139 | 2663573.9249 | 1213188.4932 | 2663578.2252 | 1213188.6921
140 | 2663632.4311 | 1213143.9451 | 2663631.8705 | 1213157.5797
141 | 2663632.4311 | 1213143.9451 | 2663632.9009 | 1213133.4824
142 | 2663632.4311 | 1213143.9451 | 2663607.123 | 1213142.8523 | 2663604.434 | 1213142.8236
143 | 2663600.7435 | 1213154.7917 | 2663604.0743 | 1213154.4714 | 2663604.434 | 1213142.8236

## bus_geodata
| x | y | coords
0 | 2663566.734 | 1213214.7954
1 | 2663555.6753 | 1213214.3814
2 | 2663574.437 | 1213215.0837
3 | 2663546.077 | 1213235.4032
4 | 2663596.1139 | 1213215.8952
5 | 2663537.2734 | 1213231.4955
6 | 2663557.9091 | 1213239.2872
7 | 2663603.0213 | 1213216.1537
8 | 2663534.1147 | 1213230.0934
9 | 2663557.7007 | 1213270.2374
10 | 2663619.2604 | 1213216.7466
11 | 2663602.8665 | 1213219.9766
12 | 2663689.9885 | 1213175.8515
13 | 2663680.0831 | 1213124.2303
14 | 2663745.5422 | 1213157.9284
15 | 2663677.2871 | 1213127.8249
16 | 2663638.9195 | 1213092.6272
17 | 2663675.1163 | 1213134.0198
18 | 2663634.8952 | 1213088.8819
19 | 2663677.6897 | 1213150.1337
20 | 2663633.9108 | 1213110.9887
21 | 2663599.1301 | 1213051.0884
22 | 2663596.187 | 1213047.1102
23 | 2663582.0711 | 1213084.512
24 | 2663636.5467 | 1213116.4516
25 | 2663635.4122 | 1213136.8715
26 | 2663513.7738 | 1213271.9969
27 | 2663514.1822 | 1213272.1939
28 | 2663496.8598 | 1213263.8411
29 | 2663514.3088 | 1213272.2549
30 | 2663494.6378 | 1213262.7723
31 | 2663529.1615 | 1213279.4168
32 | 2663479.9021 | 1213299.0156
33 | 2663476.712 | 1213297.5474
34 | 2663477.7736 | 1213303.429
35 | 2663496.5595 | 1213309.5151
36 | 2663488.9815 | 1213274.7517
37 | 2663508.3951 | 1213233.7888
38 | 2663481.5831 | 1213256.4794
39 | 2663517.4366 | 1213222.6904
40 | 2663514.4052 | 1213221.3017
41 | 2663531.1732 | 1213228.7877
42 | 2663521.4178 | 1213214.1793
43 | 2663468.0996 | 1213296.0741
44 | 2663466.3974 | 1213297.9992
45 | 2663469.9715 | 1213319.6075
46 | 2663500.6218 | 1213314.3233
47 | 2663478.2025 | 1213254.8498
48 | 2663505.2785 | 1213217.1291
49 | 2663534.0523 | 1213230.0657
50 | 2663534.8153 | 1213185.5376
51 | 2663555.0738 | 1213319.8856
52 | 2663570.4349 | 1213109.3884
53 | 2663558.668 | 1213134.5443
54 | 2663570.4582 | 1213109.3386
55 | 2663558.6423 | 1213134.5992
56 | 2663570.4818 | 1213109.2883
57 | 2663558.6187 | 1213134.6496
58 | 2663582.0243 | 1213084.6121
59 | 2663546.8227 | 1213159.8675
60 | 2663582.0476 | 1213084.5624
61 | 2663676.1781 | 1213225.4608
62 | 2663674.8718 | 1213244.2724
63 | 2663678.0379 | 1213207.0681
64 | 2663660.5187 | 1213251.5171
65 | 2663679.7563 | 1213190.0728
66 | 2663645.7713 | 1213248.5185
67 | 2663680.311 | 1213169.2486
68 | 2663546.8002 | 1213159.9157
69 | 2663443.7429 | 1213238.2393
70 | 2663445.3687 | 1213239.0224
71 | 2663441.3976 | 1213247.4076
72 | 2663459.8248 | 1213245.991
73 | 2663462.0367 | 1213247.0572
74 | 2663573.2071 | 1213343.1971
75 | 2663573.8687 | 1213325.3422
76 | 2663595.2349 | 1213405.5763
77 | 2663574.7427 | 1213301.7526
78 | 2663595.8767 | 1213394.543
79 | 2663574.8698 | 1213298.3226
80 | 2663598.6673 | 1213324.8505
81 | 2663575.5874 | 1213278.9537
82 | 2663599.6116 | 1213301.2654
83 | 2663461.681 | 1213292.9409
84 | 2663445.6407 | 1213285.1817
85 | 2663439.2058 | 1213282.081
86 | 2663432.1301 | 1213281.6524
87 | 2663428.923 | 1213288.2112
88 | 2663422.2066 | 1213276.921
89 | 2663575.6283 | 1213277.8497
90 | 2663576.4262 | 1213256.3164
91 | 2663576.4464 | 1213255.7691
92 | 2663576.9973 | 1213240.9027
93 | 2663580.4233 | 1213082.312
94 | 2663580.4236 | 1213082.3114
95 | 2663568.2397 | 1213107.8075
96 | 2663580.4239 | 1213082.3107
97 | 2663568.2391 | 1213107.8087
98 | 2663591.7266 | 1213058.2085
99 | 2663568.2365 | 1213107.8142
100 | 2663591.7683 | 1213058.1178
101 | 2663556.1124 | 1213133.3053
102 | 2663499.2071 | 1213214.3534
103 | 2663493.1389 | 1213211.5791
104 | 2663532.1405 | 1213184.0872
105 | 2663532.1716 | 1213184.0202
106 | 2663532.202 | 1213183.9549
107 | 2663556.0971 | 1213133.3377
108 | 2663556.0829 | 1213133.3677
109 | 2663543.9907 | 1213158.9252
110 | 2663543.9865 | 1213158.934
111 | 2663602.367 | 1213232.4522
112 | 2663601.4309 | 1213255.8309
113 | 2663600.5245 | 1213278.4662
114 | 2663621.0941 | 1213216.8135
115 | 2663630.492 | 1213191.109
116 | 2663602.4298 | 1213291.0289
117 | 2663630.9311 | 1213180.4296
118 | 2663601.1688 | 1213189.753
119 | 2663633.157 | 1213191.2375
120 | 2663534.8388 | 1213185.4872
121 | 2663632.8202 | 1213198.8418
122 | 2663631.9622 | 1213218.217
123 | 2663631.7052 | 1213224.0645
124 | 2663633.6597 | 1213178.4589
125 | 2663630.3054 | 1213242.0176
126 | 2663634.4779 | 1213157.6593
127 | 2663637.3361 | 1213262.4195
128 | 2663583.9034 | 1213188.9547
129 | 2663635.0127 | 1213144.0616
130 | 2663497.8509 | 1213319.8528
131 | 2663516.3881 | 1213321.8393
132 | 2663453.0435 | 1213291.6253
133 | 2663517.1878 | 1213322.2206
134 | 2663445.9936 | 1213306.6485
135 | 2663578.2252 | 1213188.6921
136 | 2663573.9249 | 1213188.4932
137 | 2663631.8705 | 1213157.5797
138 | 2663632.4311 | 1213143.9451
139 | 2663543.9812 | 1213158.9451
140 | 2663604.434 | 1213142.8236
141 | 2663600.7435 | 1213154.7917
142 | 2663632.9009 | 1213133.4824
143 | 2663409.448 | 1213270.8379
144 | 2663589.8567 | 1213038.1498
145 | 2663546.077 | 1213235.4032

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99865 | -0.025602 | 0.0027059 | 0.00067816
1 | 1 | 0 | -0.32238 | -0.081612
2 | 0.99773 | -0.043111 | 0.0027084 | 0.00067879
3 | 0.99804 | -0.037334 | 0 | 0
4 | 0.9952 | -0.091522 | 0.0045499 | 0.0011403
5 | 0.99724 | -0.052543 | 0.0023518 | 0.00058942
6 | 0.99799 | -0.038353 | 0.002421 | 0.00060677
7 | 0.99443 | -0.10645 | 0 | 0
8 | 0.99696 | -0.057935 | 0.0021187 | 0.00053101
9 | 0.99792 | -0.039573 | 0 | 0
10 | 0.99311 | -0.13164 | 0.0021901 | 0.00054889
11 | 0.9943 | -0.10879 | 0 | 0
12 | 0.98443 | -0.29997 | 0.0025801 | 0.00064662
13 | 0.98469 | -0.29485 | 0 | 0
14 | 0.98428 | -0.30285 | 0.0027362 | 0.00068575
15 | 0.98472 | -0.29441 | 0 | 0
16 | 0.98599 | -0.26954 | 0 | 0
17 | 0.98458 | -0.29698 | 0.003715 | 0.00093106
18 | 0.98613 | -0.26693 | 0 | 0
19 | 0.98432 | -0.30213 | 0.003715 | 0.00093106
20 | 0.98667 | -0.25643 | 0.0028787 | 0.00072146
21 | 0.9855 | -0.27869 | 0 | 0
22 | 0.98532 | -0.28231 | 0 | 0
23 | 0.98692 | -0.25116 | 0.001763 | 0.00044185
24 | 0.98759 | -0.23851 | 0.0032961 | 0.00082608
25 | 0.98765 | -0.2373 | 0.0035434 | 0.00088807
26 | 0.99138 | -0.16543 | 0.0036144 | 0.00090585
27 | 0.99137 | -0.16549 | 0.0021167 | 0.0005305
28 | 0.99156 | -0.16185 | 0 | 0
29 | 0.99137 | -0.1655 | 0.0021179 | 0.00053078
30 | 0.99159 | -0.16138 | 0 | 0
31 | 0.99133 | -0.16635 | 0.0029097 | 0.00072924
32 | 0.9898 | -0.19606 | 0 | 0
33 | 0.98987 | -0.19463 | 0 | 0
34 | 0.98975 | -0.19686 | 0 | 0
35 | 0.98954 | -0.20098 | 0.0041739 | 0.0010461
36 | 0.99099 | -0.17297 | 0.0027 | 0.00067669
37 | 0.99409 | -0.11304 | 0.0044721 | 0.0011208
38 | 0.99125 | -0.16783 | 0.0056889 | 0.0014258
39 | 0.99552 | -0.085464 | 0 | 0
40 | 0.99523 | -0.091149 | 0 | 0
41 | 0.9967 | -0.06284 | 0.0023503 | 0.00058904
42 | 0.99488 | -0.097739 | 0.0023504 | 0.00058906
43 | 0.98967 | -0.19844 | 0.0026051 | 0.00065291
44 | 0.98968 | -0.19839 | 0.0023246 | 0.0005826
45 | 0.98972 | -0.19762 | 0.002388 | 0.00059849
46 | 0.98947 | -0.20238 | 0 | 0
47 | 0.99119 | -0.16912 | 0.0027026 | 0.00067734
48 | 0.99516 | -0.092472 | 0.0023518 | 0.00058942
49 | 0.99696 | -0.05804 | 0.0021167 | 0.0005305
50 | 0.99279 | -0.13785 | 0.0025842 | 0.00064766
51 | 0.99782 | -0.041535 | 0.0022516 | 0.00056431
52 | 0.98809 | -0.22855 | 0.0025825 | 0.00064722
53 | 0.98946 | -0.20192 | 0.0025844 | 0.00064771
54 | 0.98808 | -0.2286 | 0.0025826 | 0.00064725
55 | 0.98947 | -0.20186 | 0.0025842 | 0.00064767
56 | 0.98808 | -0.22865 | 0.0025842 | 0.00064767
57 | 0.98947 | -0.2018 | 0.0025826 | 0.00064725
58 | 0.98693 | -0.25107 | 0.0017618 | 0.00044154
59 | 0.99105 | -0.17134 | 0.0025826 | 0.00064725
60 | 0.98692 | -0.25111 | 0.0017619 | 0.00044157
61 | 0.98366 | -0.31499 | 0.0016026 | 0.00040165
62 | 0.98359 | -0.31647 | 0.0014533 | 0.00036423
63 | 0.98376 | -0.313 | 0.001636 | 0.00041003
64 | 0.98353 | -0.31762 | 0.001454 | 0.00036441
65 | 0.98388 | -0.31066 | 0.0024124 | 0.00060461
66 | 0.9835 | -0.31807 | 0.0014534 | 0.00036425
67 | 0.98408 | -0.3069 | 0.0037126 | 0.00093046
68 | 0.99105 | -0.17128 | 0.0025826 | 0.00064725
69 | 0.99075 | -0.17757 | 0.0050316 | 0.001261
70 | 0.99076 | -0.17741 | 0 | 0
71 | 0.99073 | -0.17799 | 0.0035022 | 0.00087773
72 | 0.99088 | -0.17498 | 0.003808 | 0.00095436
73 | 0.99091 | -0.17444 | 0.0043656 | 0.0010941
74 | 0.98829 | -0.22499 | 0.0024021 | 0.00060203
75 | 0.98796 | -0.23142 | 0.0020373 | 0.0005106
76 | 0.9898 | -0.19576 | 0 | 0
77 | 0.98757 | -0.23905 | 0.0020362 | 0.00051033
78 | 0.99003 | -0.19132 | 0 | 0
79 | 0.98752 | -0.24004 | 0.0018313 | 0.00045898
80 | 0.99147 | -0.1634 | 0.0021016 | 0.0005267
81 | 0.98726 | -0.24497 | 0.0022621 | 0.00056693
82 | 0.992 | -0.15309 | 0.0021016 | 0.0005267
83 | 0.98953 | -0.20113 | 0.0026055 | 0.000653
84 | 0.98923 | -0.20699 | 0.0026055 | 0.000653
85 | 0.98913 | -0.20902 | 0.0026051 | 0.00065291
86 | 0.98902 | -0.21121 | 0 | 0
87 | 0.98898 | -0.21183 | 0.0047673 | 0.0011948
88 | 0.98893 | -0.21288 | 0.0049445 | 0.0012392
89 | 0.98725 | -0.2452 | 0.0023803 | 0.00059656
90 | 0.98706 | -0.2489 | 0.0022633 | 0.00056723
91 | 0.98706 | -0.24897 | 0.0026431 | 0.00066242
92 | 0.98699 | -0.25022 | 0.0046854 | 0.0011743
93 | 0.98402 | -0.30769 | 0.001763 | 0.00044185
94 | 0.98402 | -0.30769 | 0.0017612 | 0.00044139
95 | 0.98323 | -0.32306 | 0.0017619 | 0.00044156
96 | 0.98402 | -0.30769 | 0.001763 | 0.00044185
97 | 0.98323 | -0.32306 | 0.0025841 | 0.00064764
98 | 0.98489 | -0.29071 | 0.001763 | 0.00044185
99 | 0.98323 | -0.32306 | 0.0025825 | 0.00064723
100 | 0.98489 | -0.29064 | 0.0017612 | 0.0004414
101 | 0.98262 | -0.3349 | 0.0025844 | 0.00064771
102 | 0.99513 | -0.093076 | 0.0023503 | 0.00058904
103 | 0.99511 | -0.093403 | 0.0027878 | 0.00069868
104 | 0.98202 | -0.34673 | 0.0025824 | 0.00064722
105 | 0.98202 | -0.34672 | 0.0025842 | 0.00064766
106 | 0.98202 | -0.34671 | 0.0025826 | 0.00064725
107 | 0.98262 | -0.33491 | 0.0025826 | 0.00064725
108 | 0.98262 | -0.33492 | 0.0025842 | 0.00064767
109 | 0.98222 | -0.34284 | 0.0025826 | 0.00064725
110 | 0.98222 | -0.34284 | 0.0025826 | 0.00064725
111 | 0.99391 | -0.11644 | 0.0023325 | 0.00058458
112 | 0.99321 | -0.12983 | 0.0023336 | 0.00058485
113 | 0.99259 | -0.14188 | 0.0023334 | 0.0005848
114 | 0.99297 | -0.13441 | 0 | 0
115 | 0.99026 | -0.18677 | 0 | 0
116 | 0.99199 | -0.15327 | 0.00099222 | 0.00024867
117 | 0.99022 | -0.18758 | 0.0042928 | 0.0010759
118 | 0.98994 | -0.19298 | 0.0057983 | 0.0014532
119 | 0.99009 | -0.19005 | 0 | 0
120 | 0.99279 | -0.13792 | 0.0025825 | 0.00064725
121 | 0.99001 | -0.1915 | 0.0037384 | 0.00093693
122 | 0.98989 | -0.19392 | 0.001218 | 0.00030525
123 | 0.98986 | -0.19453 | 0 | 0
124 | 0.9894 | -0.20341 | 0.0035274 | 0.00088404
125 | 0.98976 | -0.19638 | 0.0014532 | 0.00036421
126 | 0.98834 | -0.22387 | 0.003525 | 0.00088346
127 | 0.98967 | -0.19814 | 0.0043379 | 0.0010872
128 | 0.98984 | -0.19486 | 0.0017117 | 0.00042899
129 | 0.9877 | -0.23642 | 0 | 0
130 | 0.98945 | -0.20273 | 0.003166 | 0.00079349
131 | 0.98937 | -0.20437 | 0.0028949 | 0.00072553
132 | 0.98962 | -0.19957 | 0 | 0
133 | 0.98937 | -0.20442 | 0.0034901 | 0.0008747
134 | 0.98955 | -0.20089 | 0.0044871 | 0.0011246
135 | 0.98982 | -0.1953 | 0.0018142 | 0.00045467
136 | 0.98981 | -0.1955 | 0.0025842 | 0.00064766
137 | 0.98753 | -0.23968 | 0.0048964 | 0.0012271
138 | 0.98759 | -0.23848 | 0 | 0
139 | 0.98222 | -0.34284 | 0.0025842 | 0.00064767
140 | 0.9874 | -0.24209 | 0.0037066 | 0.00092896
141 | 0.98736 | -0.24303 | 0.003499 | 0.00087693
142 | 0.98727 | -0.24461 | 0.0033365 | 0.00083621
143 | 0.98888 | -0.21378 | 0.0035744 | 0.00089582
144 | 0.9853 | -0.28266 | 0.001763 | 0.00044185
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13375 | -0.033988 | 0.13392 | 0.034093 | 0.0001651 | 0.00010552 | 0.19946 | 0.19946 | 0.19946 | 0.99865 | -0.025602 | 1 | 0 | 54.7967
1 | 0.13105 | 0.03331 | -0.13094 | -0.033239 | 0.0001104 | 7.0555e-05 | 0.19543 | 0.19543 | 0.19543 | 0.99865 | -0.025602 | 0.99773 | -0.043111 | 53.6891
2 | 0.18681 | 0.047518 | -0.18648 | -0.047304 | 0.00033542 | 0.00021406 | 0.27823 | 0.27823 | 0.27823 | 1 | 0 | 0.99804 | -0.037334 | 38.2178
3 | 0.12823 | 0.03256 | -0.12793 | -0.03237 | 0.00029797 | 0.00019042 | 0.19139 | 0.19139 | 0.19139 | 0.99773 | -0.043111 | 0.9952 | -0.091522 | 52.5794
4 | 0.1818 | 0.046134 | -0.18167 | -0.046049 | 0.00013289 | 8.4796e-05 | 0.27126 | 0.27126 | 0.27126 | 0.99804 | -0.037334 | 0.99724 | -0.052543 | 37.2608
5 | 0.0046732 | 0.0011702 | -0.004673 | -0.0011702 | 2.2669e-07 | -1.765e-08 | 0.0069671 | 0.0069672 | 0.0069672 | 0.99804 | -0.037334 | 0.99799 | -0.038353 | 1.9141
6 | 0.12338 | 0.03123 | -0.12329 | -0.031173 | 8.8317e-05 | 5.6433e-05 | 0.18459 | 0.18459 | 0.18459 | 0.9952 | -0.091522 | 0.99443 | -0.10645 | 50.7105
7 | 0.17932 | 0.04546 | -0.17927 | -0.04543 | 4.6455e-05 | 2.9641e-05 | 0.26775 | 0.26775 | 0.26775 | 0.99724 | -0.052543 | 0.99696 | -0.057935 | 36.7788
8 | 0.002252 | 0.00056347 | -0.0022518 | -0.00056379 | 1.3083e-07 | -3.2066e-07 | 0.0033574 | 0.0033575 | 0.0033575 | 0.99799 | -0.038353 | 0.99792 | -0.039573 | 0.9224
9 | 0.088389 | 0.022365 | -0.088282 | -0.022297 | 0.00010672 | 6.809e-05 | 0.13234 | 0.13234 | 0.13234 | 0.99443 | -0.10645 | 0.99311 | -0.13164 | 36.3563
10 | 0.034904 | 0.0088081 | -0.0349 | -0.0088056 | 3.921e-06 | 2.4597e-06 | 0.05225 | 0.05225 | 0.05225 | 0.99443 | -0.10645 | 0.9943 | -0.10879 | 14.3543
11 | 0.17715 | 0.044899 | -0.17715 | -0.044899 | 8.9483e-07 | 5.7091e-07 | 0.26459 | 0.26459 | 0.26459 | 0.99696 | -0.057935 | 0.99696 | -0.05804 | 36.3444
12 | 0.0022518 | 0.00056379 | -0.0022516 | -0.00056431 | 2.1033e-07 | -5.1532e-07 | 0.0033575 | 0.0033578 | 0.0033578 | 0.99792 | -0.039573 | 0.99782 | -0.041535 | 0.92246
13 | 0.086092 | 0.021748 | -0.086081 | -0.021741 | 1.1461e-05 | 7.3111e-06 | 0.12906 | 0.12906 | 0.12906 | 0.99311 | -0.13164 | 0.99297 | -0.13441 | 35.4548
14 | 0.0349 | 0.0088056 | -0.034887 | -0.0087976 | 1.2782e-05 | 8.0187e-06 | 0.05225 | 0.05225 | 0.05225 | 0.9943 | -0.10879 | 0.99391 | -0.11644 | 14.3543
15 | -0.0053166 | -0.0013319 | 0.0053179 | 0.001332 | 1.2978e-06 | 1.4905e-07 | 0.0080361 | 0.0080358 | 0.0080361 | 0.98443 | -0.29997 | 0.98469 | -0.29485 | 2.2077
16 | 0.0027365 | 0.00068524 | -0.0027362 | -0.00068575 | 3.7452e-07 | -5.0235e-07 | 0.0041362 | 0.0041365 | 0.0041365 | 0.98443 | -0.29997 | 0.98428 | -0.30285 | 1.1364
17 | -0.0053179 | -0.001332 | 0.005318 | 0.001332 | 1.1018e-07 | 1.2635e-08 | 0.0080358 | 0.0080358 | 0.0080358 | 0.98469 | -0.29485 | 0.98472 | -0.29441 | 2.2076
18 | -0.026486 | -0.0066406 | 0.026517 | 0.00666 | 3.1435e-05 | 1.9452e-05 | 0.040024 | 0.040024 | 0.040024 | 0.98472 | -0.29441 | 0.98599 | -0.26954 | 10.9957
19 | 0.021168 | 0.0053085 | -0.021165 | -0.005307 | 2.5927e-06 | 1.5734e-06 | 0.031988 | 0.031988 | 0.031988 | 0.98472 | -0.29441 | 0.98458 | -0.29698 | 8.788
20 | -0.026517 | -0.00666 | 0.026521 | 0.0066621 | 3.2973e-06 | 2.0403e-06 | 0.040024 | 0.040024 | 0.040024 | 0.98599 | -0.26954 | 0.98613 | -0.26693 | 10.9956
21 | 0.01745 | 0.0043759 | -0.017446 | -0.0043734 | 4.2768e-06 | 2.5287e-06 | 0.026374 | 0.026374 | 0.026374 | 0.98458 | -0.29698 | 0.98432 | -0.30213 | 7.2456
22 | -0.026521 | -0.0066621 | 0.026534 | 0.0066703 | 1.3293e-05 | 8.2251e-06 | 0.040024 | 0.040024 | 0.040024 | 0.98613 | -0.26693 | 0.98667 | -0.25643 | 10.9956
23 | 0.013731 | 0.0034423 | -0.013728 | -0.0034406 | 3.1237e-06 | 1.7535e-06 | 0.020758 | 0.020758 | 0.020758 | 0.98432 | -0.30213 | 0.98408 | -0.3069 | 5.7028
24 | -0.029413 | -0.0073917 | 0.029429 | 0.0074021 | 1.6619e-05 | 1.0349e-05 | 0.044365 | 0.044365 | 0.044365 | 0.98667 | -0.25643 | 0.98727 | -0.24461 | 12.1883
25 | 0.040847 | 0.010272 | -0.04084 | -0.010267 | 7.055e-06 | 4.4522e-06 | 0.061687 | 0.061687 | 0.061687 | 0.9855 | -0.27869 | 0.98532 | -0.28231 | 16.947
26 | -0.040847 | -0.010272 | 0.040901 | 0.010306 | 5.38e-05 | 3.3951e-05 | 0.061687 | 0.061687 | 0.061687 | 0.9855 | -0.27869 | 0.98692 | -0.25116 | 16.947
27 | 0.001763 | 0.00044173 | -0.001763 | -0.00044185 | 2.9203e-08 | -1.2123e-07 | 0.0026625 | 0.0026625 | 0.0026625 | 0.98532 | -0.28231 | 0.9853 | -0.28266 | 0.73146
28 | 0.039077 | 0.0098255 | -0.039061 | -0.0098157 | 1.5545e-05 | 9.7975e-06 | 0.059024 | 0.059025 | 0.059025 | 0.98532 | -0.28231 | 0.98489 | -0.29064 | 16.2155
29 | -0.042664 | -0.010747 | 0.042664 | 0.010748 | 8.6339e-08 | 5.4544e-08 | 0.064345 | 0.064345 | 0.064345 | 0.98692 | -0.25116 | 0.98692 | -0.25111 | 17.6772
30 | -0.0032961 | -0.00082608 | 0.0032963 | 0.00082594 | 1.8915e-07 | -1.4065e-07 | 0.0049663 | 0.0049662 | 0.0049663 | 0.98759 | -0.23851 | 0.98765 | -0.2373 | 1.3644
31 | -0.0068397 | -0.001714 | 0.00684 | 0.0017141 | 2.8676e-07 | 9.1365e-08 | 0.010305 | 0.010305 | 0.010305 | 0.98765 | -0.2373 | 0.9877 | -0.23642 | 2.831
32 | 0.0071444 | 0.0017904 | -0.0071444 | -0.0017904 | 1.9552e-08 | 6.6672e-09 | 0.010723 | 0.010723 | 0.010723 | 0.99138 | -0.16543 | 0.99137 | -0.16549 | 2.946
33 | -0.010759 | -0.0026962 | 0.010761 | 0.0026972 | 1.8363e-06 | 9.3305e-07 | 0.016149 | 0.016148 | 0.016149 | 0.99138 | -0.16543 | 0.99156 | -0.16185 | 4.4364
34 | 0.0050277 | 0.0012599 | -0.0050277 | -0.0012599 | 3.0018e-09 | 1.0779e-10 | 0.0075463 | 0.0075463 | 0.0075463 | 0.99137 | -0.16549 | 0.99137 | -0.1655 | 2.0732
35 | -0.010761 | -0.0026972 | 0.010761 | 0.0026973 | 2.4056e-07 | 1.2223e-07 | 0.016148 | 0.016148 | 0.016148 | 0.99156 | -0.16185 | 0.99159 | -0.16138 | 4.4364
36 | 0.0029098 | 0.00072911 | -0.0029097 | -0.00072924 | 1.1795e-07 | -1.3711e-07 | 0.0043675 | 0.0043676 | 0.0043676 | 0.99137 | -0.1655 | 0.99133 | -0.16635 | 1.1999
37 | 0.049431 | 0.012424 | -0.049404 | -0.012407 | 2.7345e-05 | 1.733e-05 | 0.074191 | 0.074191 | 0.074191 | 0.99159 | -0.16138 | 0.99099 | -0.17297 | 20.3823
38 | -0.085306 | -0.02142 | 0.085503 | 0.021546 | 0.00019721 | 0.0001258 | 0.12803 | 0.12803 | 0.12803 | 0.99159 | -0.16138 | 0.99409 | -0.11304 | 35.1725
39 | 0.025113 | 0.0062988 | -0.025106 | -0.0062941 | 7.7192e-06 | 4.7534e-06 | 0.037688 | 0.037688 | 0.037688 | 0.99159 | -0.16138 | 0.99125 | -0.16783 | 10.3539
40 | -0.022931 | -0.0057478 | 0.022932 | 0.0057487 | 1.5611e-06 | 9.5408e-07 | 0.034473 | 0.034473 | 0.034473 | 0.9898 | -0.19606 | 0.98987 | -0.19463 | 9.4707
41 | 0.0092012 | 0.0023057 | -0.0092008 | -0.0023056 | 3.5144e-07 | 1.6197e-07 | 0.013833 | 0.013833 | 0.013833 | 0.9898 | -0.19606 | 0.98975 | -0.19686 | 3.8002
42 | 0.013729 | 0.003442 | -0.013726 | -0.0034402 | 3.2183e-06 | 1.8009e-06 | 0.020641 | 0.020641 | 0.020641 | 0.9898 | -0.19606 | 0.98954 | -0.20098 | 5.6705
43 | -0.046656 | -0.0117 | 0.046704 | 0.01173 | 4.8207e-05 | 3.0516e-05 | 0.070137 | 0.070137 | 0.070137 | 0.98987 | -0.19463 | 0.99099 | -0.17297 | 19.2685
44 | 0.023724 | 0.0059509 | -0.023719 | -0.0059482 | 4.3145e-06 | 2.645e-06 | 0.035664 | 0.035664 | 0.035664 | 0.98987 | -0.19463 | 0.98967 | -0.19844 | 9.7978
45 | 0.0068128 | 0.0017073 | -0.0068123 | -0.0017071 | 4.9591e-07 | 1.5539e-07 | 0.010242 | 0.010242 | 0.010242 | 0.98975 | -0.19686 | 0.98968 | -0.19839 | 2.8139
46 | 0.0023881 | 0.00059831 | -0.002388 | -0.00059849 | 8.6821e-08 | -1.7526e-07 | 0.0035902 | 0.0035903 | 0.0035903 | 0.98975 | -0.19686 | 0.98972 | -0.19762 | 0.98634
47 | 0.0095523 | 0.0023941 | -0.0095517 | -0.0023938 | 6.4044e-07 | 3.0356e-07 | 0.014364 | 0.014364 | 0.014364 | 0.98954 | -0.20098 | 0.98947 | -0.20238 | 3.9462
48 | -0.089975 | -0.022667 | 0.090069 | 0.022727 | 9.4322e-05 | 6.0186e-05 | 0.13472 | 0.13472 | 0.13472 | 0.99409 | -0.11304 | 0.99523 | -0.091149 | 37.0115
49 | 0.019417 | 0.0048683 | -0.019416 | -0.0048676 | 1.1957e-06 | 7.1687e-07 | 0.029148 | 0.029148 | 0.029148 | 0.99125 | -0.16783 | 0.99119 | -0.16912 | 8.0078
50 | 0.097586 | 0.024621 | -0.09756 | -0.024604 | 2.6558e-05 | 1.6954e-05 | 0.14592 | 0.14592 | 0.14592 | 0.99552 | -0.085464 | 0.99523 | -0.091149 | 40.0882
51 | -0.17246 | -0.043634 | 0.17264 | 0.043753 | 0.00018746 | 0.00011958 | 0.25792 | 0.25792 | 0.25792 | 0.99552 | -0.085464 | 0.9967 | -0.06284 | 35.4285
52 | 0.074871 | 0.019013 | -0.074827 | -0.018984 | 4.4198e-05 | 2.8165e-05 | 0.112 | 0.112 | 0.112 | 0.99552 | -0.085464 | 0.99488 | -0.097739 | 30.7688
53 | 0.0074905 | 0.0018773 | -0.0074901 | -0.0018771 | 4.7202e-07 | 1.717e-07 | 0.011199 | 0.0112 | 0.0112 | 0.99523 | -0.091149 | 0.99516 | -0.092472 | 3.0768
54 | -0.175 | -0.044342 | 0.17504 | 0.044368 | 4.0366e-05 | 2.5752e-05 | 0.26143 | 0.26143 | 0.26143 | 0.9967 | -0.06284 | 0.99696 | -0.05804 | 35.9104
55 | 0.072476 | 0.018395 | -0.072337 | -0.018306 | 0.00013955 | 8.89e-05 | 0.10848 | 0.10848 | 0.10848 | 0.99488 | -0.097739 | 0.99279 | -0.13785 | 29.803
56 | 0.021114 | 0.0052953 | -0.021111 | -0.0052937 | 2.6996e-06 | 1.636e-06 | 0.031747 | 0.031747 | 0.031747 | 0.98967 | -0.19844 | 0.98953 | -0.20113 | 8.7218
57 | 0.0044877 | 0.0011245 | -0.0044874 | -0.0011246 | 2.5262e-07 | -2.8448e-08 | 0.0067473 | 0.0067474 | 0.0067474 | 0.98968 | -0.19839 | 0.98962 | -0.19957 | 1.8537
58 | 0.0031661 | 0.00079344 | -0.003166 | -0.00079349 | 5.2555e-08 | -4.5768e-08 | 0.0047613 | 0.0047613 | 0.0047613 | 0.98947 | -0.20238 | 0.98945 | -0.20273 | 1.3081
59 | 0.0063856 | 0.0016004 | -0.006385 | -0.0016002 | 6.0401e-07 | 1.6225e-07 | 0.009603 | 0.0096031 | 0.0096031 | 0.98947 | -0.20238 | 0.98937 | -0.20437 | 2.6382
60 | 0.016713 | 0.0041903 | -0.016709 | -0.0041878 | 4.2368e-06 | 2.4803e-06 | 0.025091 | 0.025091 | 0.025091 | 0.99119 | -0.16912 | 0.99091 | -0.17444 | 6.8931
61 | 0.0051383 | 0.0012877 | -0.0051381 | -0.0012877 | 1.4778e-07 | 7.8422e-09 | 0.007683 | 0.007683 | 0.007683 | 0.99516 | -0.092472 | 0.99513 | -0.093076 | 2.1107
62 | 0.069753 | 0.017659 | -0.069752 | -0.017659 | 2.2817e-07 | 1.4531e-07 | 0.10461 | 0.10461 | 0.10461 | 0.99279 | -0.13785 | 0.99279 | -0.13792 | 28.739
63 | -0.053986 | -0.013604 | 0.054055 | 0.013648 | 6.8883e-05 | 4.3729e-05 | 0.081328 | 0.081327 | 0.081328 | 0.98809 | -0.22855 | 0.98946 | -0.20192 | 22.3427
64 | 0.051404 | 0.012957 | -0.051404 | -0.012957 | 1.2353e-07 | 7.8356e-08 | 0.077439 | 0.077439 | 0.077439 | 0.98809 | -0.22855 | 0.98808 | -0.2286 | 21.2743
65 | -0.05664 | -0.014296 | 0.05664 | 0.014296 | 1.6519e-07 | 1.0494e-07 | 0.085214 | 0.085214 | 0.085214 | 0.98946 | -0.20192 | 0.98947 | -0.20186 | 23.4104
66 | 0.048821 | 0.01231 | -0.048821 | -0.01231 | 1.128e-07 | 7.148e-08 | 0.073549 | 0.073549 | 0.073549 | 0.98808 | -0.2286 | 0.98808 | -0.22865 | 20.2058
67 | -0.059224 | -0.014944 | 0.059224 | 0.014944 | 1.6556e-07 | 1.0524e-07 | 0.0891 | 0.0891 | 0.0891 | 0.98947 | -0.20186 | 0.98947 | -0.2018 | 24.4781
68 | 0.046237 | 0.011662 | -0.046187 | -0.011631 | 4.9569e-05 | 3.1376e-05 | 0.069657 | 0.069658 | 0.069658 | 0.98808 | -0.22865 | 0.98693 | -0.25107 | 19.1367
69 | -0.061807 | -0.015591 | 0.061897 | 0.015648 | 9.0266e-05 | 5.7412e-05 | 0.092984 | 0.092984 | 0.092984 | 0.98947 | -0.2018 | 0.99105 | -0.17134 | 25.5451
70 | 0.044426 | 0.011189 | -0.044425 | -0.011189 | 9.2479e-08 | 5.8487e-08 | 0.067001 | 0.067001 | 0.067001 | 0.98693 | -0.25107 | 0.98692 | -0.25111 | 18.407
71 | -0.06448 | -0.016296 | 0.06448 | 0.016296 | 1.8695e-07 | 1.1896e-07 | 0.096862 | 0.096862 | 0.096862 | 0.99105 | -0.17134 | 0.99105 | -0.17128 | 26.6103
72 | 0.0043612 | 0.0010925 | -0.0043609 | -0.0010925 | 3.078e-07 | -4.2391e-08 | 0.0065971 | 0.0065972 | 0.0065972 | 0.98366 | -0.31499 | 0.98359 | -0.31647 | 1.8124
73 | -0.0059638 | -0.0014941 | 0.0059644 | 0.0014943 | 5.642e-07 | 1.2639e-07 | 0.0090214 | 0.0090213 | 0.0090214 | 0.98366 | -0.31499 | 0.98376 | -0.313 | 2.4784
74 | 0.0029076 | 0.00072829 | -0.0029074 | -0.00072846 | 1.5952e-07 | -1.7695e-07 | 0.0043986 | 0.0043987 | 0.0043987 | 0.98359 | -0.31647 | 0.98353 | -0.31762 | 1.2084
75 | -0.0076004 | -0.0019043 | 0.0076012 | 0.0019046 | 8.4656e-07 | 3.2489e-07 | 0.011496 | 0.011496 | 0.011496 | 0.98376 | -0.313 | 0.98388 | -0.31066 | 3.1582
76 | 0.0014534 | 0.00036406 | -0.0014534 | -0.00036425 | 3.1159e-08 | -1.9814e-07 | 0.0021989 | 0.0021989 | 0.0021989 | 0.98353 | -0.31762 | 0.9835 | -0.31807 | 0.60411
77 | -0.010014 | -0.0025092 | 0.010015 | 0.0025101 | 1.7945e-06 | 8.8343e-07 | 0.015144 | 0.015144 | 0.015144 | 0.98388 | -0.31066 | 0.98408 | -0.3069 | 4.1605
78 | -0.067062 | -0.016943 | 0.06717 | 0.017011 | 0.00010744 | 6.8395e-05 | 0.10074 | 0.10074 | 0.10074 | 0.99105 | -0.17128 | 0.99279 | -0.13792 | 27.6756
79 | -0.0050316 | -0.001261 | 0.0050316 | 0.001261 | 3.8645e-08 | 1.4942e-09 | 0.007557 | 0.007557 | 0.007557 | 0.99075 | -0.17757 | 0.99076 | -0.17741 | 2.0761
80 | 0.0035023 | 0.00087767 | -0.0035022 | -0.00087773 | 9.6233e-08 | -5.785e-08 | 0.00526 | 0.0052601 | 0.0052601 | 0.99076 | -0.17741 | 0.99073 | -0.17799 | 1.4451
81 | -0.0085339 | -0.0021387 | 0.0085349 | 0.0021391 | 9.886e-07 | 4.2602e-07 | 0.012817 | 0.012817 | 0.012817 | 0.99076 | -0.17741 | 0.99088 | -0.17498 | 3.5211
82 | -0.012343 | -0.0030935 | 0.012343 | 0.0030937 | 3.1635e-07 | 1.7083e-07 | 0.018535 | 0.018535 | 0.018535 | 0.99088 | -0.17498 | 0.99091 | -0.17444 | 5.0921
83 | 0.020158 | 0.0050582 | -0.020152 | -0.0050544 | 6.1729e-06 | 3.7218e-06 | 0.030353 | 0.030353 | 0.030353 | 0.98829 | -0.22499 | 0.98796 | -0.23142 | 8.3388
84 | -0.02256 | -0.0056602 | 0.022592 | 0.0056794 | 3.1489e-05 | 1.9219e-05 | 0.03397 | 0.033969 | 0.03397 | 0.98829 | -0.22499 | 0.9898 | -0.19576 | 9.3323
85 | 0.018115 | 0.0045438 | -0.018108 | -0.0045399 | 6.59e-06 | 3.9155e-06 | 0.027285 | 0.027285 | 0.027285 | 0.98796 | -0.23142 | 0.98757 | -0.23905 | 7.4958
86 | -0.022592 | -0.0056794 | 0.022596 | 0.0056823 | 4.785e-06 | 2.9202e-06 | 0.033969 | 0.033969 | 0.033969 | 0.9898 | -0.19576 | 0.99003 | -0.19132 | 9.3323
87 | 0.016072 | 0.0040296 | -0.016071 | -0.0040292 | 7.5482e-07 | 4.3917e-07 | 0.024217 | 0.024217 | 0.024217 | 0.98757 | -0.23905 | 0.98752 | -0.24004 | 6.6529
88 | -0.022596 | -0.0056823 | 0.022627 | 0.0057007 | 3.0181e-05 | 1.8418e-05 | 0.033969 | 0.033969 | 0.033969 | 0.99003 | -0.19132 | 0.99147 | -0.1634 | 9.3322
89 | 0.01424 | 0.0035702 | -0.014236 | -0.0035683 | 3.3464e-06 | 1.8938e-06 | 0.021457 | 0.021457 | 0.021457 | 0.98752 | -0.24004 | 0.98726 | -0.24497 | 5.8948
90 | -0.024728 | -0.0062274 | 0.02474 | 0.0062349 | 1.2198e-05 | 7.5024e-06 | 0.037123 | 0.037123 | 0.037123 | 0.99147 | -0.1634 | 0.992 | -0.15309 | 10.1986
91 | 0.011974 | 0.0030014 | -0.011974 | -0.0030013 | 1.3494e-07 | 7.2237e-08 | 0.018048 | 0.018048 | 0.018048 | 0.98726 | -0.24497 | 0.98725 | -0.2452 | 4.9582
92 | 0.00099223 | 0.00024854 | -0.00099222 | -0.00024867 | 8.8196e-09 | -1.3143e-07 | 0.0014883 | 0.0014884 | 0.0014884 | 0.992 | -0.15309 | 0.99199 | -0.15327 | 0.40889
93 | -0.027834 | -0.0070102 | 0.027849 | 0.0070195 | 1.4924e-05 | 9.2568e-06 | 0.041764 | 0.041764 | 0.041764 | 0.992 | -0.15309 | 0.99259 | -0.14188 | 11.4735
94 | 0.018506 | 0.0046407 | -0.018501 | -0.0046376 | 5.175e-06 | 3.0831e-06 | 0.027829 | 0.027829 | 0.027829 | 0.98953 | -0.20113 | 0.98923 | -0.20699 | 7.6454
95 | 0.015895 | 0.0039846 | -0.015894 | -0.0039837 | 1.5314e-06 | 8.8837e-07 | 0.02391 | 0.02391 | 0.02391 | 0.98923 | -0.20699 | 0.98913 | -0.20902 | 6.5687
96 | 0.013289 | 0.0033308 | -0.013287 | -0.00333 | 1.3907e-06 | 7.7098e-07 | 0.019991 | 0.019991 | 0.019991 | 0.98913 | -0.20902 | 0.98902 | -0.21121 | 5.4921
97 | 0.0047675 | 0.0011948 | -0.0047673 | -0.0011948 | 1.4081e-07 | -3.5336e-09 | 0.0071729 | 0.0071729 | 0.0071729 | 0.98902 | -0.21121 | 0.98898 | -0.21183 | 1.9706
98 | 0.0085197 | 0.0021352 | -0.008519 | -0.0021349 | 6.7739e-07 | 2.9246e-07 | 0.012818 | 0.012818 | 0.012818 | 0.98902 | -0.21121 | 0.98893 | -0.21288 | 3.5215
99 | 0.0035745 | 0.00089574 | -0.0035744 | -0.00089582 | 1.5333e-07 | -8.3212e-08 | 0.0053784 | 0.0053785 | 0.0053785 | 0.98893 | -0.21288 | 0.98888 | -0.21378 | 1.4776
100 | 0.0095937 | 0.0024047 | -0.009592 | -0.0024039 | 1.6896e-06 | 8.0586e-07 | 0.01446 | 0.01446 | 0.01446 | 0.98725 | -0.2452 | 0.98706 | -0.2489 | 3.9726
101 | 0.0073288 | 0.0018367 | -0.0073287 | -0.0018367 | 2.5072e-08 | 9.0445e-09 | 0.011048 | 0.011048 | 0.011048 | 0.98706 | -0.2489 | 0.98706 | -0.24897 | 3.0352
102 | 0.0046857 | 0.0011743 | -0.0046854 | -0.0011743 | 2.7836e-07 | -1.1989e-08 | 0.0070637 | 0.0070638 | 0.0070638 | 0.98706 | -0.24897 | 0.98699 | -0.25022 | 1.9406
103 | -0.031984 | -0.008031 | 0.031984 | 0.008031 | 6.3016e-10 | 4.033e-10 | 0.048371 | 0.048371 | 0.048371 | 0.98402 | -0.30769 | 0.98402 | -0.30769 | 13.2887
104 | 0.030221 | 0.0075892 | -0.030199 | -0.0075754 | 2.2135e-05 | 1.3808e-05 | 0.045705 | 0.045705 | 0.045705 | 0.98402 | -0.30769 | 0.98323 | -0.32306 | 12.5563
105 | -0.033745 | -0.0084724 | 0.033745 | 0.0084724 | 6.9365e-10 | 4.4394e-10 | 0.051034 | 0.051034 | 0.051034 | 0.98402 | -0.30769 | 0.98402 | -0.30769 | 14.0204
106 | 0.028437 | 0.0071338 | -0.028437 | -0.0071338 | 9.3241e-10 | 5.9674e-10 | 0.043039 | 0.043039 | 0.043039 | 0.98323 | -0.32306 | 0.98323 | -0.32306 | 11.8238
107 | -0.035508 | -0.0089143 | 0.035537 | 0.0089324 | 2.8788e-05 | 1.8086e-05 | 0.0537 | 0.0537 | 0.0537 | 0.98402 | -0.30769 | 0.98489 | -0.29071 | 14.7528
108 | 0.025853 | 0.0064862 | -0.025853 | -0.0064862 | 3.501e-09 | 2.1551e-09 | 0.039128 | 0.039128 | 0.039128 | 0.98323 | -0.32306 | 0.98323 | -0.32306 | 10.7494
109 | -0.0373 | -0.0093742 | 0.0373 | 0.0093743 | 1.189e-07 | 7.4825e-08 | 0.056364 | 0.056364 | 0.056364 | 0.98489 | -0.29071 | 0.98489 | -0.29064 | 15.4845
110 | 0.02327 | 0.0058389 | -0.023257 | -0.0058309 | 1.313e-05 | 8.0456e-06 | 0.03522 | 0.03522 | 0.03522 | 0.98323 | -0.32306 | 0.98262 | -0.3349 | 9.6757
111 | 0.020673 | 0.0051832 | -0.020673 | -0.0051832 | 1.3157e-08 | 7.9658e-09 | 0.031306 | 0.031306 | 0.031306 | 0.98262 | -0.3349 | 0.98262 | -0.33491 | 8.6005
112 | 0.0027878 | 0.00069862 | -0.0027878 | -0.00069868 | 4.348e-08 | -5.8855e-08 | 0.0041686 | 0.0041686 | 0.0041686 | 0.99513 | -0.093076 | 0.99511 | -0.093403 | 1.1452
113 | -0.0025824 | -0.00064722 | 0.0025824 | 0.00064722 | 4.2388e-10 | -6.6455e-10 | 0.0039131 | 0.0039131 | 0.0039131 | 0.98202 | -0.34673 | 0.98202 | -0.34672 | 1.075
114 | -0.0051666 | -0.0012949 | 0.0051666 | 0.0012949 | 1.6566e-09 | 1.4927e-10 | 0.0078288 | 0.0078288 | 0.0078288 | 0.98202 | -0.34672 | 0.98202 | -0.34671 | 2.1508
115 | -0.0077492 | -0.0019421 | 0.0077506 | 0.0019427 | 1.4293e-06 | 5.6494e-07 | 0.011742 | 0.011742 | 0.011742 | 0.98202 | -0.34671 | 0.98222 | -0.34284 | 3.2258
116 | 0.01809 | 0.0045359 | -0.01809 | -0.0045359 | 9.3447e-09 | 5.5604e-09 | 0.027395 | 0.027395 | 0.027395 | 0.98262 | -0.33491 | 0.98262 | -0.33492 | 7.5261
117 | 0.015506 | 0.0038882 | -0.0155 | -0.0038849 | 5.8463e-06 | 3.3836e-06 | 0.023482 | 0.023482 | 0.023482 | 0.98262 | -0.33492 | 0.98222 | -0.34284 | 6.4511
118 | 0.012917 | 0.0032376 | -0.012917 | -0.0032376 | 1.4106e-09 | 7.7465e-10 | 0.019569 | 0.019569 | 0.019569 | 0.98222 | -0.34284 | 0.98222 | -0.34284 | 5.3762
119 | 0.010335 | 0.0025904 | -0.010335 | -0.0025904 | 1.1292e-09 | 5.6605e-10 | 0.015657 | 0.015657 | 0.015657 | 0.98222 | -0.34284 | 0.98222 | -0.34284 | 4.3014
120 | 0.032554 | 0.008213 | -0.032533 | -0.0081999 | 2.0858e-05 | 1.3046e-05 | 0.048758 | 0.048758 | 0.048758 | 0.99391 | -0.11644 | 0.99321 | -0.12983 | 13.395
121 | 0.0302 | 0.0076151 | -0.030182 | -0.0076043 | 1.7403e-05 | 1.0845e-05 | 0.045261 | 0.045262 | 0.045262 | 0.99321 | -0.12983 | 0.99259 | -0.14188 | 12.4345
122 | 0.086081 | 0.021741 | -0.085865 | -0.021604 | 0.00021537 | 0.00013739 | 0.12906 | 0.12906 | 0.12906 | 0.99297 | -0.13441 | 0.99026 | -0.18677 | 35.4548
123 | 0.004293 | 0.0010759 | -0.0042928 | -0.0010759 | 1.668e-07 | -3.075e-08 | 0.0064509 | 0.0064509 | 0.0064509 | 0.99026 | -0.18677 | 0.99022 | -0.18758 | 1.7722
124 | 0.011913 | 0.0029865 | -0.011909 | -0.0029846 | 3.5274e-06 | 1.88e-06 | 0.017901 | 0.017901 | 0.017901 | 0.99026 | -0.18677 | 0.98994 | -0.19298 | 4.9179
125 | 0.06966 | 0.017541 | -0.069649 | -0.017534 | 1.0935e-05 | 6.9645e-06 | 0.1047 | 0.1047 | 0.1047 | 0.99026 | -0.18677 | 0.99009 | -0.19005 | 28.7648
126 | 0.0061108 | 0.0015314 | -0.0061102 | -0.0015313 | 5.4684e-07 | 1.2779e-07 | 0.0091853 | 0.0091854 | 0.0091854 | 0.98994 | -0.19298 | 0.98984 | -0.19486 | 2.5235
127 | 0.058899 | 0.01484 | -0.058861 | -0.014816 | 3.7601e-05 | 2.39e-05 | 0.088547 | 0.088547 | 0.088547 | 0.99009 | -0.19005 | 0.9894 | -0.20341 | 24.3262
128 | 0.01075 | 0.0026943 | -0.010749 | -0.0026939 | 7.4509e-07 | 3.7897e-07 | 0.016156 | 0.016156 | 0.016156 | 0.99009 | -0.19005 | 0.99001 | -0.1915 | 4.4386
129 | 0.0070109 | 0.001757 | -0.0070101 | -0.0017567 | 8.0758e-07 | 2.675e-07 | 0.010538 | 0.010538 | 0.010538 | 0.99001 | -0.1915 | 0.98989 | -0.19392 | 2.895
130 | 0.0057922 | 0.0014515 | -0.005792 | -0.0014514 | 1.6639e-07 | 3.1251e-08 | 0.0087068 | 0.0087068 | 0.0087068 | 0.98989 | -0.19392 | 0.98986 | -0.19453 | 2.392
131 | 0.005792 | 0.0014514 | -0.0057915 | -0.0014513 | 5.1193e-07 | 9.618e-08 | 0.0087068 | 0.0087069 | 0.0087069 | 0.98986 | -0.19453 | 0.98976 | -0.19638 | 2.392
132 | 0.055334 | 0.013932 | -0.055279 | -0.013898 | 5.409e-05 | 3.435e-05 | 0.083242 | 0.083242 | 0.083242 | 0.9894 | -0.20341 | 0.98834 | -0.22387 | 22.8688
133 | 0.0043383 | 0.0010871 | -0.0043379 | -0.0010872 | 3.6402e-07 | -6.0279e-08 | 0.0065221 | 0.0065222 | 0.0065222 | 0.98976 | -0.19638 | 0.98967 | -0.19814 | 1.7918
134 | 0.051754 | 0.013014 | -0.051723 | -0.012995 | 3.0996e-05 | 1.9663e-05 | 0.077935 | 0.077935 | 0.077935 | 0.98834 | -0.22387 | 0.9877 | -0.23642 | 21.4108
135 | 0.0043985 | 0.0011023 | -0.0043984 | -0.0011023 | 9.3197e-08 | -1.3419e-08 | 0.0066122 | 0.0066122 | 0.0066122 | 0.98984 | -0.19486 | 0.98982 | -0.1953 | 1.8165
136 | 0.044883 | 0.01128 | -0.044879 | -0.011278 | 4.4201e-06 | 2.7959e-06 | 0.067631 | 0.067631 | 0.067631 | 0.9877 | -0.23642 | 0.98759 | -0.23848 | 18.5798
137 | 0.0034901 | 0.00087469 | -0.0034901 | -0.0008747 | 9.1545e-09 | -5.5187e-09 | 0.0052491 | 0.0052491 | 0.0052491 | 0.98937 | -0.20437 | 0.98937 | -0.20442 | 1.4421
138 | 0.0044874 | 0.0011246 | -0.0044871 | -0.0011246 | 2.8322e-07 | -3.1861e-08 | 0.0067474 | 0.0067475 | 0.0067475 | 0.98962 | -0.19957 | 0.98955 | -0.20089 | 1.8537
139 | 0.0025842 | 0.00064763 | -0.0025842 | -0.00064766 | 2.4364e-08 | -3.9738e-08 | 0.0038849 | 0.0038849 | 0.0038849 | 0.98982 | -0.1953 | 0.98981 | -0.1955 | 1.0673
140 | -0.0048964 | -0.0012271 | 0.0048966 | 0.0012271 | 2.7855e-07 | 3.6705e-09 | 0.0073779 | 0.0073778 | 0.0073779 | 0.98753 | -0.23968 | 0.98759 | -0.23848 | 2.0269
141 | 0.032775 | 0.0082443 | -0.032766 | -0.0082383 | 9.582e-06 | 5.9985e-06 | 0.049394 | 0.049394 | 0.049394 | 0.98759 | -0.23848 | 0.98727 | -0.24461 | 13.5698
142 | 0.007207 | 0.0018062 | -0.0072058 | -0.0018058 | 1.239e-06 | 4.3451e-07 | 0.010859 | 0.010859 | 0.010859 | 0.98759 | -0.23848 | 0.9874 | -0.24209 | 2.9832
143 | 0.0034991 | 0.00087684 | -0.003499 | -0.00087693 | 1.5641e-07 | -9.1746e-08 | 0.0052732 | 0.0052732 | 0.0052732 | 0.9874 | -0.24209 | 0.98736 | -0.24303 | 1.4487

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32496 | 0.082259

## res_load
| p_mw | q_mvar
0 | 0.0027059 | 0.00067816
1 | 0.0025824 | 0.00064722
2 | 0.0027084 | 0.00067879
3 | 0.0045499 | 0.0011403
4 | 0.0023518 | 0.00058942
5 | 0.002421 | 0.00060677
6 | 0.0021187 | 0.00053101
7 | 0.0021901 | 0.00054889
8 | 0.0025801 | 0.00064662
9 | 0.0027362 | 0.00068575
10 | 0.003715 | 0.00093106
11 | 0.003715 | 0.00093106
12 | 0.0028787 | 0.00072146
13 | 0.001763 | 0.00044185
14 | 0.0032961 | 0.00082608
15 | 0.0035434 | 0.00088807
16 | 0.0036144 | 0.00090585
17 | 0.0021167 | 0.0005305
18 | 0.0021179 | 0.00053078
19 | 0.0029097 | 0.00072924
20 | 0.0041739 | 0.0010461
21 | 0.0027 | 0.00067669
22 | 0.0044721 | 0.0011208
23 | 0.0056889 | 0.0014258
24 | 0.0023503 | 0.00058904
25 | 0.0023504 | 0.00058906
26 | 0.0026051 | 0.00065291
27 | 0.0023246 | 0.0005826
28 | 0.002388 | 0.00059849
29 | 0.0027026 | 0.00067734
30 | 0.0023518 | 0.00058942
31 | 0.0021167 | 0.0005305
32 | 0.0025842 | 0.00064766
33 | 0.0022516 | 0.00056431
34 | 0.0025825 | 0.00064722
35 | 0.0025844 | 0.00064771
36 | 0.0025826 | 0.00064725
37 | 0.0025842 | 0.00064767
38 | 0.0025842 | 0.00064767
39 | 0.0025826 | 0.00064725
40 | 0.0017618 | 0.00044154
41 | 0.0025826 | 0.00064725
42 | 0.0017619 | 0.00044157
43 | 0.0016026 | 0.00040165
44 | 0.0014533 | 0.00036423
45 | 0.001636 | 0.00041003
46 | 0.001454 | 0.00036441
47 | 0.0024124 | 0.00060461
48 | 0.0014534 | 0.00036425
49 | 0.0037126 | 0.00093046
50 | 0.0025826 | 0.00064725
51 | 0.0050316 | 0.001261
52 | 0.0035022 | 0.00087773
53 | 0.003808 | 0.00095436
54 | 0.0043656 | 0.0010941
55 | 0.0024021 | 0.00060203
56 | 0.0020373 | 0.0005106
57 | 0.0020362 | 0.00051033
58 | 0.0018313 | 0.00045898
59 | 0.0021016 | 0.0005267
60 | 0.0022621 | 0.00056693
61 | 0.0021016 | 0.0005267
62 | 0.0026055 | 0.000653
63 | 0.0026055 | 0.000653
64 | 0.0026051 | 0.00065291
65 | 0.0047673 | 0.0011948
66 | 0.0049445 | 0.0012392
67 | 0.0023803 | 0.00059656
68 | 0.0022633 | 0.00056723
69 | 0.0026431 | 0.00066242
70 | 0.0046854 | 0.0011743
71 | 0.001763 | 0.00044185
72 | 0.0017612 | 0.00044139
73 | 0.0017619 | 0.00044156
74 | 0.001763 | 0.00044185
75 | 0.0025841 | 0.00064764
76 | 0.001763 | 0.00044185
77 | 0.0025825 | 0.00064723
78 | 0.0017612 | 0.0004414
79 | 0.0025844 | 0.00064771
80 | 0.0023503 | 0.00058904
81 | 0.0027878 | 0.00069868
82 | 0.0025824 | 0.00064722
83 | 0.0025842 | 0.00064766
84 | 0.0025826 | 0.00064725
85 | 0.0025826 | 0.00064725
86 | 0.0025842 | 0.00064767
87 | 0.0025826 | 0.00064725
88 | 0.0025826 | 0.00064725
89 | 0.0023325 | 0.00058458
90 | 0.0023336 | 0.00058485
91 | 0.0023334 | 0.0005848
92 | 0.00099222 | 0.00024867
93 | 0.0042928 | 0.0010759
94 | 0.0057983 | 0.0014532
95 | 0.0025825 | 0.00064725
96 | 0.0037384 | 0.00093693
97 | 0.001218 | 0.00030525
98 | 0.0035274 | 0.00088404
99 | 0.0014532 | 0.00036421
100 | 0.003525 | 0.00088346
101 | 0.0043379 | 0.0010872
102 | 0.0017117 | 0.00042899
103 | 0.003166 | 0.00079349
104 | 0.0028949 | 0.00072553
105 | 0.0034901 | 0.0008747
106 | 0.0044871 | 0.0011246
107 | 0.0018142 | 0.00045467
108 | 0.0025842 | 0.00064766
109 | 0.0048964 | 0.0012271
110 | 0.0025842 | 0.00064767
111 | 0.0037066 | 0.00092896
112 | 0.003499 | 0.00087693
113 | 0.0033365 | 0.00083621
114 | 0.0035744 | 0.00089582
115 | 0.001763 | 0.00044185

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1