## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-212_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-212_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-212_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-212_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-212_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-212_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1061-212_0_4_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_1061-212_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1061-212_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1061-212_0_4_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_1061-212_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1061-212_0_4_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1061-212_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1061-212_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1061-212_0_4_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1061-212_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_1061-212_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1061-212_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1061-212_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1061-212_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1061-212_0_4_node_5 | 0.4 | n |  | TRUE
21 | bus_LV_1061-212_0_4_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_1061-212_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1061-212_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1061-212_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1061-212_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_1061-212_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1061-212_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1061-212_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1061-212_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1061-212_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_MV_218_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-212_0_4_load_0 | 0 | 0.010679 | 0.0026763 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-212_0_4_load_1 | 1 | 0.029484 | 0.0073895 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-212_0_4_load_2 | 2 | 0.0058161 | 0.0014577 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-212_0_4_load_3 | 3 | 0.0036101 | 0.00090477 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-212_0_4_load_8 | 5 | 0.08451 | 0.02118 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-212_0_4_load_31 | 9 | 0.005834 | 0.0014621 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-212_0_4_load_19 | 11 | 0.022369 | 0.0056063 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-212_0_4_load_28 | 12 | 0.0042089 | 0.0010549 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-212_0_4_load_23 | 15 | 0.09785 | 0.024524 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-212_0_4_load_20 | 17 | 0.061062 | 0.015304 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-212_0_4_load_22 | 19 | 0.031898 | 0.0079943 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-212_0_4_load_5 | 20 | 0.053869 | 0.013501 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-212_0_4_load_7 | 21 | 0.0055086 | 0.0013806 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-212_0_4_load_30 | 22 | 0.0073799 | 0.0018496 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-212_0_4_load_17 | 23 | 0.0040801 | 0.0010226 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-212_0_4_load_29 | 25 | 0.02294 | 0.0057492 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-212_0_4_load_14 | 26 | 0.013717 | 0.0034378 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-212_0_4_load_26 | 29 | 0.0036223 | 0.00090784 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-212_0_4_load_27 | 30 | 0.029112 | 0.0072963 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-212_0_4_line_0 |  | 0 | 1 | 0.068229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-212_0_4_line_1 |  | 0 | 2 | 0.024797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-212_0_4_line_2 |  | 1 | 3 | 0.038407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-212_0_4_line_3 |  | 2 | 4 | 0.016245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-212_0_4_line_4 |  | 3 | 5 | 0.040314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-212_0_4_line_5 |  | 3 | 6 | 0.084449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-212_0_4_line_6 |  | 4 | 7 | 0.10186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-212_0_4_line_7 |  | 5 | 8 | 0.015429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1061-212_0_4_line_8 |  | 6 | 9 | 0.038173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-212_0_4_line_9 |  | 7 | 12 | 0.10876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-212_0_4_line_10 |  | 8 | 20 | 0.036785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-212_0_4_line_11 |  | 8 | 10 | 0.042271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-212_0_4_line_12 |  | 10 | 11 | 0.016742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1061-212_0_4_line_13 |  | 11 | 16 | 0.049469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1061-212_0_4_line_14 |  | 13 | 14 | 0.003686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-212_0_4_line_15 |  | 13 | 15 | 0.041868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-212_0_4_line_16 |  | 14 | 22 | 0.018534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-212_0_4_line_17 |  | 14 | 16 | 0.029488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1061-212_0_4_line_18 |  | 14 | 18 | 0.023528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-212_0_4_line_19 |  | 16 | 17 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-212_0_4_line_20 |  | 18 | 19 | 0.020629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-212_0_4_line_21 |  | 19 | 23 | 0.083443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-212_0_4_line_22 |  | 20 | 21 | 0.0006932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-212_0_4_line_23 |  | 22 | 24 | 0.034715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-212_0_4_line_24 |  | 23 | 27 | 0.018267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-212_0_4_line_25 |  | 24 | 25 | 0.024728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-212_0_4_line_26 |  | 26 | 27 | 0.021974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-212_0_4_line_27 |  | 27 | 28 | 0.046696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-212_0_4_line_28 |  | 28 | 29 | 0.041938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-212_0_4_line_29 |  | 29 | 30 | 0.046415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-212_0_4_trafo_19 | 0.63 MVA 20/0.4 kV | 31 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2663720.6412 | 1212988.38 | 2663689.2156 | 1212974.0465 | 2663698.8332 | 1212951.3018 | 2663696.2945 | 1212945.738 | 2663697.4871 | 1212943.1177
1 | 2663720.6412 | 1212988.38 | 2663743.2019 | 1212998.6701
2 | 2663716.6232 | 1212911.6896 | 2663716.6232 | 1212911.6896 | 2663710.8735 | 1212913.7073 | 2663697.4871 | 1212943.1177
3 | 2663757.9818 | 1213005.4114 | 2663743.2019 | 1212998.6701
4 | 2663716.6232 | 1212911.6896 | 2663724.7665 | 1212913.1664 | 2663751.039 | 1212931.502
5 | 2663716.6232 | 1212911.6896 | 2663664.5951 | 1212845.1711
6 | 2663751.6768 | 1213093.476 | 2663753.0303 | 1213084.118 | 2663755.3027 | 1213069.1109 | 2663758.5021 | 1213056.2149 | 2663763.3037 | 1213039.8339 | 2663769.098 | 1213024.4085 | 2663773.2264 | 1213014.1575 | 2663773.9443 | 1213012.3752 | 2663757.9818 | 1213005.4114
7 | 2663763.6917 | 1212940.3323 | 2663751.039 | 1212931.502
8 | 2663664.5951 | 1212845.1711 | 2663636.2319 | 1212844.0567 | 2663626.4741 | 1212843.2839
9 | 2663751.6768 | 1213093.476 | 2663709.1883 | 1213087.763 | 2663707.8493 | 1213079.4214 | 2663711.2295 | 1213049.5947 | 2663712.408 | 1213034.5758 | 2663707.7994 | 1213027.2109 | 2663704.6223 | 1213025.38
10 | 2663763.6917 | 1212940.3323 | 2663764.0981 | 1212927.9068 | 2663763.3316 | 1212920.016 | 2663761.2208 | 1212914.2232 | 2663760.2751 | 1212908.176 | 2663760.547 | 1212904.046
11 | 2663763.6917 | 1212940.3323 | 2663776.0585 | 1212948.9587 | 2663782.3914 | 1212952.7843 | 2663789.5169 | 1212957.0854 | 2663795.5101 | 1212960.7073 | 2663797.2537 | 1212957.5017 | 2663797.6488 | 1212956.7833
12 | 2663797.6488 | 1212956.7833 | 2663800.9365 | 1212958.375 | 2663812.8461 | 1212963.8064
13 | 2663857.8558 | 1212984.3332 | 2663812.8461 | 1212963.8064
14 | 2663884.8321 | 1212996.4184 | 2663883.2467 | 1212999.7479
15 | 2663883.2467 | 1212999.7479 | 2663882.1709 | 1213002.3046 | 2663881.9059 | 1213002.9355 | 2663916.4419 | 1213018.4705 | 2663916.9311 | 1213018.6995
16 | 2663884.8321 | 1212996.4184 | 2663901.7585 | 1213003.9678
17 | 2663857.8558 | 1212984.3332 | 2663862.4144 | 1212986.4167 | 2663884.8321 | 1212996.4184
18 | 2663884.8321 | 1212996.4184 | 2663894.9283 | 1212975.1578
19 | 2663857.8558 | 1212984.3332 | 2663864.838 | 1212968.6307
20 | 2663894.9283 | 1212975.1578 | 2663898.406 | 1212971.7708 | 2663911.9739 | 1212963.7234
21 | 2663932.3639 | 1212898.8384 | 2663931.8728 | 1212899.2847 | 2663929.1118 | 1212903.1353 | 2663928.3494 | 1212904.0943 | 2663927.4816 | 1212908.51 | 2663927.3201 | 1212910.1092 | 2663927.7211 | 1212913.0932 | 2663939.2346 | 1212940.3444 | 2663939.0203 | 1212944.7448 | 2663937.8399 | 1212947.8452 | 2663936.0221 | 1212949.4601 | 2663911.9739 | 1212963.7234
22 | 2663760.5925 | 1212903.3543 | 2663760.547 | 1212904.046
23 | 2663933.4628 | 1213018.1082 | 2663901.7585 | 1213003.9678
24 | 2663947.115 | 1212888.4191 | 2663946.0854 | 1212888.7972 | 2663941.8803 | 1212890.5755 | 2663934.9799 | 1212896.4607 | 2663932.3639 | 1212898.8384
25 | 2663933.4628 | 1213018.1082 | 2663943.1343 | 1212995.35
26 | 2663947.115 | 1212888.4191 | 2663954.1756 | 1212909.2277
27 | 2663921.9066 | 1212849.5806 | 2663927.2279 | 1212855.6414 | 2663938.2349 | 1212869.9237 | 2663941.1257 | 1212874.513 | 2663942.4161 | 1212876.7394 | 2663945.3837 | 1212883.3864 | 2663947.115 | 1212888.4191
28 | 2663921.9066 | 1212849.5806 | 2663903.5129 | 1212866.7053 | 2663893.7053 | 1212875.8948 | 2663890.6398 | 1212877.287
29 | 2663849.3171 | 1212882.1567 | 2663849.6833 | 1212879.8815 | 2663854.6967 | 1212880.6578 | 2663855.0702 | 1212877.7045 | 2663869.6138 | 1212879.5613 | 2663880.5599 | 1212879.6785 | 2663887.5827 | 1212878.6753 | 2663890.6398 | 1212877.287

## bus_geodata
| x | y | coords
0 | 2663720.6412 | 1212988.38
1 | 2663697.4871 | 1212943.1177
2 | 2663743.2019 | 1212998.6701
3 | 2663716.6232 | 1212911.6896
4 | 2663757.9818 | 1213005.4114
5 | 2663751.039 | 1212931.502
6 | 2663664.5951 | 1212845.1711
7 | 2663751.6768 | 1213093.476
8 | 2663763.6917 | 1212940.3323
9 | 2663626.4741 | 1212843.2839
10 | 2663797.6488 | 1212956.7833
11 | 2663812.8461 | 1212963.8064
12 | 2663704.6223 | 1213025.38
13 | 2663883.2467 | 1212999.7479
14 | 2663884.8321 | 1212996.4184
15 | 2663916.9311 | 1213018.6995
16 | 2663857.8558 | 1212984.3332
17 | 2663864.838 | 1212968.6307
18 | 2663894.9283 | 1212975.1578
19 | 2663911.9739 | 1212963.7234
20 | 2663760.547 | 1212904.046
21 | 2663760.5925 | 1212903.3543
22 | 2663901.7585 | 1213003.9678
23 | 2663932.3639 | 1212898.8384
24 | 2663933.4628 | 1213018.1082
25 | 2663943.1343 | 1212995.35
26 | 2663954.1756 | 1212909.2277
27 | 2663947.115 | 1212888.4191
28 | 2663921.9066 | 1212849.5806
29 | 2663890.6398 | 1212877.287
30 | 2663849.3171 | 1212882.1567
31 | 2663797.6488 | 1212956.7833

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98822 | -0.22688 | 0.010679 | 0.0026763
1 | 0.98952 | -0.20169 | 0.029484 | 0.0073895
2 | 0.988 | -0.23132 | 0.0058161 | 0.0014577
3 | 0.99129 | -0.16743 | 0.0036101 | 0.00090477
4 | 0.98793 | -0.23254 | 0 | 0
5 | 0.99349 | -0.12488 | 0.08451 | 0.02118
6 | 0.99084 | -0.17618 | 0 | 0
7 | 0.98754 | -0.24021 | 0 | 0
8 | 0.99451 | -0.10526 | 0 | 0
9 | 0.99063 | -0.18013 | 0.005834 | 0.0014621
10 | 0.99844 | -0.029744 | 0 | 0
11 | 1 | 0 | -0.48152 | -0.12208
12 | 0.98712 | -0.2484 | 0.0042089 | 0.0010549
13 | 0.99064 | -0.17921 | 0 | 0
14 | 0.99097 | -0.17281 | 0 | 0
15 | 0.98687 | -0.25225 | 0.09785 | 0.024524
16 | 0.99382 | -0.11785 | 0 | 0
17 | 0.99287 | -0.13639 | 0.061062 | 0.015304
18 | 0.98918 | -0.2073 | 0 | 0
19 | 0.98761 | -0.23764 | 0.031898 | 0.0079943
20 | 0.99251 | -0.14383 | 0.053869 | 0.013501
21 | 0.99251 | -0.14389 | 0.0055086 | 0.0013806
22 | 0.99045 | -0.18279 | 0.0073799 | 0.0018496
23 | 0.98371 | -0.3133 | 0.0040801 | 0.0010226
24 | 0.98972 | -0.19695 | 0 | 0
25 | 0.9892 | -0.20705 | 0.02294 | 0.0057492
26 | 0.98264 | -0.33403 | 0.013717 | 0.0034378
27 | 0.98292 | -0.32859 | 0 | 0
28 | 0.98151 | -0.35621 | 0 | 0
29 | 0.98023 | -0.38108 | 0.0036223 | 0.00090784
30 | 0.97898 | -0.40563 | 0.029112 | 0.0072963
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.020709 | -0.0051891 | 0.020734 | 0.0052042 | 2.4878e-05 | 1.5047e-05 | 0.031182 | 0.031182 | 0.031182 | 0.98822 | -0.22688 | 0.98952 | -0.20169 | 8.5666
1 | 0.010031 | 0.0025128 | -0.010028 | -0.0025118 | 2.1211e-06 | 1.0399e-06 | 0.015103 | 0.015103 | 0.015103 | 0.98822 | -0.22688 | 0.988 | -0.23132 | 4.1492
2 | -0.050218 | -0.012594 | 0.0503 | 0.012646 | 8.2141e-05 | 5.2076e-05 | 0.07552 | 0.07552 | 0.07552 | 0.98952 | -0.20169 | 0.99129 | -0.16743 | 20.7472
3 | 0.0042124 | 0.0010541 | -0.0042121 | -0.0010542 | 2.4515e-07 | -5.1126e-08 | 0.0063436 | 0.0063437 | 0.0063437 | 0.988 | -0.23132 | 0.98793 | -0.23254 | 1.7428
4 | -0.059748 | -0.015013 | 0.05987 | 0.015091 | 0.00012164 | 7.733e-05 | 0.089701 | 0.089701 | 0.089701 | 0.99129 | -0.16743 | 0.99349 | -0.12488 | 24.6432
5 | 0.0058375 | 0.0014628 | -0.0058351 | -0.0014623 | 2.4317e-06 | 4.6808e-07 | 0.0087625 | 0.0087629 | 0.0087629 | 0.99129 | -0.16743 | 0.99084 | -0.17618 | 2.4074
6 | 0.0042121 | 0.0010542 | -0.0042106 | -0.0010545 | 1.5372e-06 | -3.1988e-07 | 0.0063437 | 0.0063442 | 0.0063442 | 0.98793 | -0.23254 | 0.98754 | -0.24021 | 1.7429
7 | -0.14438 | -0.036271 | 0.14451 | 0.036357 | 0.00013532 | 8.6206e-05 | 0.21628 | 0.21628 | 0.21628 | 0.99349 | -0.12488 | 0.99451 | -0.10526 | 29.7083
8 | 0.0058351 | 0.0014623 | -0.005834 | -0.0014621 | 1.0993e-06 | 2.1195e-07 | 0.0087629 | 0.0087631 | 0.0087631 | 0.99084 | -0.17618 | 0.99063 | -0.18013 | 2.4074
9 | 0.0042106 | 0.0010545 | -0.0042089 | -0.0010549 | 1.6416e-06 | -3.4025e-07 | 0.0063442 | 0.0063447 | 0.0063447 | 0.98754 | -0.24021 | 0.98712 | -0.2484 | 1.743
10 | 0.059487 | 0.014951 | -0.059378 | -0.014881 | 0.00010932 | 6.9488e-05 | 0.089021 | 0.089022 | 0.089022 | 0.99451 | -0.10526 | 0.99251 | -0.14383 | 24.4565
11 | -0.204 | -0.051308 | 0.20474 | 0.05178 | 0.00073875 | 0.0004717 | 0.3053 | 0.3053 | 0.3053 | 0.99451 | -0.10526 | 0.99844 | -0.029744 | 41.9365
12 | -0.20474 | -0.05178 | 0.20503 | 0.051966 | 0.00029259 | 0.00018682 | 0.3053 | 0.3053 | 0.3053 | 0.99844 | -0.029744 | 1 | 0 | 41.9364
13 | 0.27484 | 0.07011 | -0.27328 | -0.069116 | 0.0015546 | 0.00099368 | 0.4094 | 0.4094 | 0.4094 | 1 | 0 | 0.99382 | -0.11785 | 56.236
14 | -0.098192 | -0.024742 | 0.098222 | 0.024761 | 3.0089e-05 | 1.9209e-05 | 0.14754 | 0.14754 | 0.14754 | 0.99064 | -0.17921 | 0.99097 | -0.17281 | 40.5329
15 | 0.098192 | 0.024742 | -0.09785 | -0.024524 | 0.00034176 | 0.00021819 | 0.14754 | 0.14754 | 0.14754 | 0.99064 | -0.17921 | 0.98687 | -0.25225 | 40.5329
16 | 0.030361 | 0.0076241 | -0.030346 | -0.007615 | 1.4448e-05 | 9.0082e-06 | 0.045594 | 0.045594 | 0.045594 | 0.99097 | -0.17281 | 0.99045 | -0.18279 | 12.5259
17 | -0.21161 | -0.053421 | 0.21217 | 0.053778 | 0.00055871 | 0.00035681 | 0.31788 | 0.31788 | 0.31788 | 0.99097 | -0.17281 | 0.99382 | -0.11785 | 43.6654
18 | 0.083025 | 0.021036 | -0.082888 | -0.020949 | 0.00013731 | 8.7575e-05 | 0.12475 | 0.12475 | 0.12475 | 0.99097 | -0.17281 | 0.98918 | -0.2073 | 34.2721
19 | 0.061116 | 0.015338 | -0.061062 | -0.015304 | 5.3971e-05 | 3.4319e-05 | 0.091515 | 0.091515 | 0.091515 | 0.99382 | -0.11785 | 0.99287 | -0.13639 | 25.1414
20 | 0.082888 | 0.020949 | -0.082768 | -0.020872 | 0.00012039 | 7.6788e-05 | 0.12475 | 0.12475 | 0.12475 | 0.98918 | -0.2073 | 0.98761 | -0.23764 | 34.2721
21 | 0.05087 | 0.012878 | -0.050686 | -0.012761 | 0.00018404 | 0.00011672 | 0.076691 | 0.076691 | 0.076691 | 0.98761 | -0.23764 | 0.98371 | -0.3133 | 21.069
22 | 0.0055086 | 0.0013806 | -0.0055086 | -0.0013806 | 1.7731e-08 | 2.3891e-09 | 0.0082588 | 0.0082588 | 0.0082588 | 0.99251 | -0.14383 | 0.99251 | -0.14389 | 2.2689
23 | 0.022966 | 0.0057655 | -0.022951 | -0.005756 | 1.5501e-05 | 9.4742e-06 | 0.034507 | 0.034507 | 0.034507 | 0.99045 | -0.18279 | 0.98972 | -0.19695 | 9.48
24 | 0.046606 | 0.011738 | -0.046572 | -0.011717 | 3.4065e-05 | 2.157e-05 | 0.070519 | 0.070519 | 0.070519 | 0.98371 | -0.3133 | 0.98292 | -0.32859 | 19.3735
25 | 0.022951 | 0.005756 | -0.02294 | -0.0057492 | 1.1042e-05 | 6.7492e-06 | 0.034507 | 0.034507 | 0.034507 | 0.98972 | -0.19695 | 0.9892 | -0.20705 | 9.48
26 | -0.013717 | -0.0034378 | 0.013721 | 0.0034398 | 3.5553e-06 | 1.997e-06 | 0.020772 | 0.020772 | 0.020772 | 0.98264 | -0.33403 | 0.98292 | -0.32859 | 5.7065
27 | 0.032851 | 0.0082769 | -0.032808 | -0.0082497 | 4.3337e-05 | 2.7145e-05 | 0.049748 | 0.049748 | 0.049748 | 0.98292 | -0.32859 | 0.98151 | -0.35621 | 13.6671
28 | 0.032808 | 0.0082497 | -0.032769 | -0.0082253 | 3.8922e-05 | 2.4381e-05 | 0.049748 | 0.049748 | 0.049748 | 0.98151 | -0.35621 | 0.98023 | -0.38108 | 13.6671
29 | 0.029147 | 0.0073175 | -0.029112 | -0.0072963 | 3.4081e-05 | 2.1227e-05 | 0.04425 | 0.04425 | 0.04425 | 0.98023 | -0.38108 | 0.97898 | -0.40563 | 12.1565

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50389 | 0.12768

## res_load
| p_mw | q_mvar
0 | 0.010679 | 0.0026763
1 | 0.029484 | 0.0073895
2 | 0.0058161 | 0.0014577
3 | 0.0036101 | 0.00090477
4 | 0.08451 | 0.02118
5 | 0.005834 | 0.0014621
6 | 0.022369 | 0.0056063
7 | 0.0042089 | 0.0010549
8 | 0.09785 | 0.024524
9 | 0.061062 | 0.015304
10 | 0.031898 | 0.0079943
11 | 0.053869 | 0.013501
12 | 0.0055086 | 0.0013806
13 | 0.0073799 | 0.0018496
14 | 0.0040801 | 0.0010226
15 | 0.02294 | 0.0057492
16 | 0.013717 | 0.0034378
17 | 0.0036223 | 0.00090784
18 | 0.029112 | 0.0072963

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1