## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-234_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-234_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-234_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-234_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-234_0_4_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1061-234_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1061-234_0_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1061-234_0_4_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1061-234_0_4_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1061-234_0_4_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_1061-234_0_4_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_1061-234_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1061-234_0_4_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1061-234_0_4_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_1061-234_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1061-234_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1061-234_0_4_node_51 | 0.4 | n |  | TRUE
17 | bus_LV_1061-234_0_4_node_53 | 0.4 | n |  | TRUE
18 | bus_LV_1061-234_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1061-234_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1061-234_0_4_node_7 | 0.4 | n |  | TRUE
21 | bus_LV_1061-234_0_4_node_4 | 0.4 | n |  | TRUE
22 | bus_LV_1061-234_0_4_node_5 | 0.4 | n |  | TRUE
23 | bus_LV_1061-234_0_4_node_6 | 0.4 | n |  | TRUE
24 | bus_LV_1061-234_0_4_node_8 | 0.4 | n |  | TRUE
25 | bus_LV_1061-234_0_4_node_9 | 0.4 | n |  | TRUE
26 | bus_LV_1061-234_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_1061-234_0_4_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_1061-234_0_4_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_1061-234_0_4_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_1061-234_0_4_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_1061-234_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1061-234_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1061-234_0_4_node_52 | 0.4 | n |  | TRUE
34 | bus_LV_1061-234_0_4_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_1061-234_0_4_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1061-234_0_4_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1061-234_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1061-234_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1061-234_0_4_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_1061-234_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1061-234_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_1061-234_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1061-234_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1061-234_0_4_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_1061-234_0_4_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_1061-234_0_4_node_50 | 0.4 | n |  | TRUE
47 | bus_LV_1061-234_0_4_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_1061-234_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_1061-234_0_4_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1061-234_0_4_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_1061-234_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_MV_211_1_node_78 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-234_0_4_load_0 | 0 | 0.0082879 | 0.0020771 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-234_0_4_load_1 | 1 | 0.0078979 | 0.0019794 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-234_0_4_load_10 | 4 | 0.011792 | 0.0029553 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-234_0_4_load_21 | 6 | 0.0059222 | 0.0014843 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-234_0_4_load_20 | 7 | 0.013785 | 0.0034548 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-234_0_4_load_45 | 9 | 0.012107 | 0.0030342 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-234_0_4_load_39 | 13 | 0.0053006 | 0.0013285 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-234_0_4_load_53 | 17 | 0.0051524 | 0.0012913 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-234_0_4_load_26 | 18 | 0.0048158 | 0.001207 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-234_0_4_load_7 | 20 | 0.033423 | 0.0083766 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-234_0_4_load_4 | 21 | 0.019163 | 0.0048028 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-234_0_4_load_5 | 22 | 0.0079716 | 0.0019979 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-234_0_4_load_8 | 24 | 0.012245 | 0.003069 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-234_0_4_load_32 | 26 | 0.026221 | 0.0065717 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-234_0_4_load_40 | 27 | 0.013687 | 0.0034302 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-234_0_4_load_31 | 29 | 0.031042 | 0.0077798 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-234_0_4_load_43 | 30 | 0.0092699 | 0.0023233 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-234_0_4_load_30 | 31 | 0.033296 | 0.0083449 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-234_0_4_load_29 | 32 | 0.029015 | 0.0072718 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-234_0_4_load_52 | 33 | 0.01323 | 0.0033157 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-234_0_4_load_44 | 35 | 0.011797 | 0.0029566 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-234_0_4_load_35 | 36 | 0.0059202 | 0.0014837 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-234_0_4_load_23 | 37 | 0.024267 | 0.0060819 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-234_0_4_load_22 | 38 | 0.018133 | 0.0045445 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-234_0_4_load_33 | 39 | 0.0059202 | 0.0014837 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-234_0_4_load_25 | 41 | 0.019908 | 0.0049895 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-234_0_4_load_49 | 44 | 0.016764 | 0.0042014 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-234_0_4_load_50 | 46 | 0.011673 | 0.0029256 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-234_0_4_load_46 | 47 | 0.0091102 | 0.0022832 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-234_0_4_load_34 | 48 | 0.0059187 | 0.0014834 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-234_0_4_load_36 | 49 | 0.0059233 | 0.0014845 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-234_0_4_load_37 | 50 | 0.0059187 | 0.0014834 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-234_0_4_load_38 | 51 | 0.0059202 | 0.0014837 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-234_0_4_line_0 |  | 0 | 1 | 0.0049895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-234_0_4_line_1 |  | 0 | 2 | 0.0089961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-234_0_4_line_2 |  | 2 | 3 | 0.010454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-234_0_4_line_3 |  | 3 | 4 | 0.08521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-234_0_4_line_4 |  | 4 | 19 | 0.068802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-234_0_4_line_5 |  | 5 | 6 | 0.091381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-234_0_4_line_6 |  | 5 | 7 | 0.13845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-234_0_4_line_7 |  | 6 | 36 | 0.010667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-234_0_4_line_8 |  | 7 | 14 | 0.05085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-234_0_4_line_9 |  | 8 | 9 | 0.007695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-234_0_4_line_10 |  | 8 | 10 | 0.007098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1061-234_0_4_line_11 |  | 8 | 11 | 0.056897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-234_0_4_line_12 |  | 10 | 35 | 0.008285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-234_0_4_line_13 |  | 10 | 28 | 0.022154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1061-234_0_4_line_14 |  | 11 | 16 | 0.032746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-234_0_4_line_15 |  | 11 | 17 | 0.013728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-234_0_4_line_16 |  | 11 | 12 | 0.055961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-234_0_4_line_17 |  | 12 | 13 | 0.030475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-234_0_4_line_18 |  | 12 | 14 | 0.020088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-234_0_4_line_19 |  | 12 | 15 | 0.059027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-234_0_4_line_20 |  | 15 | 18 | 0.014875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-234_0_4_line_21 |  | 16 | 33 | 0.016532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-234_0_4_line_22 |  | 16 | 34 | 0.032324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-234_0_4_line_23 |  | 19 | 20 | 0.092581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-234_0_4_line_24 |  | 20 | 22 | 0.022444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-234_0_4_line_25 |  | 21 | 22 | 0.073387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-234_0_4_line_26 |  | 21 | 23 | 0.017084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1061-234_0_4_line_27 |  | 23 | 24 | 0.070359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-234_0_4_line_28 |  | 23 | 25 | 0.021289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1061-234_0_4_line_29 |  | 24 | 26 | 0.052887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-234_0_4_line_30 |  | 25 | 27 | 0.007792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-234_0_4_line_31 |  | 25 | 28 | 0.005421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1061-234_0_4_line_32 |  | 26 | 29 | 0.0329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-234_0_4_line_33 |  | 28 | 30 | 0.005735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1061-234_0_4_line_34 |  | 29 | 32 | 0.025795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1061-234_0_4_line_35 |  | 31 | 32 | 0.013853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1061-234_0_4_line_36 |  | 34 | 46 | 0.017985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1061-234_0_4_line_37 |  | 34 | 43 | 0.040336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1061-234_0_4_line_38 |  | 36 | 39 | 0.010665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1061-234_0_4_line_39 |  | 37 | 38 | 0.033858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1061-234_0_4_line_40 |  | 38 | 40 | 0.045587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1061-234_0_4_line_41 |  | 39 | 48 | 0.010664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1061-234_0_4_line_42 |  | 40 | 41 | 0.020921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1061-234_0_4_line_43 |  | 41 | 42 | 0.053047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1061-234_0_4_line_44 |  | 42 | 43 | 0.015788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1061-234_0_4_line_45 |  | 43 | 44 | 0.002938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1061-234_0_4_line_46 |  | 43 | 45 | 0.036821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1061-234_0_4_line_47 |  | 45 | 47 | 0.019046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1061-234_0_4_line_48 |  | 48 | 49 | 0.010665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1061-234_0_4_line_49 |  | 49 | 50 | 0.010665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1061-234_0_4_line_50 |  | 50 | 51 | 0.010664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-234_0_4_trafo_4 | 0.63 MVA 20/0.4 kV | 52 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2668936.5087 | 1212129.7454 | 2668941.4897 | 1212130.0364
1 | 2668942.611 | 1212121.1105 | 2668941.4897 | 1212130.0364
2 | 2668942.611 | 1212121.1105 | 2668946.0407 | 1212117.5701 | 2668949.235 | 1212114.683 | 2668950.1337 | 1212113.8373
3 | 2668950.1337 | 1212113.8373 | 2668982.87 | 1212129.3032 | 2669025.688 | 1212153.1375
4 | 2669084.4275 | 1212188.9265 | 2669068.6976 | 1212178.5935 | 2669033.1497 | 1212157.291 | 2669025.688 | 1212153.1375
5 | 2668631.8404 | 1212112.4222 | 2668635.1553 | 1212119.4981 | 2668638.6249 | 1212123.6962 | 2668645.6094 | 1212126.8452 | 2668712.0791 | 1212150.2184
6 | 2668631.8404 | 1212112.4222 | 2668659.0619 | 1212109.3557 | 2668673.0538 | 1212106.3927 | 2668716.6606 | 1212093.7869 | 2668731.8891 | 1212089.682 | 2668732.0338 | 1212089.6503 | 2668749.5729 | 1212086.1391 | 2668762.7645 | 1212084.7235 | 2668767.0459 | 1212084.904
7 | 2668712.0791 | 1212150.2184 | 2668722.1423 | 1212153.757
8 | 2668813.1275 | 1212072.0296 | 2668808.7039 | 1212074.7914 | 2668802.0102 | 1212081.3405 | 2668796.6606 | 1212084.6809 | 2668791.4809 | 1212086.4556 | 2668778.0143 | 1212085.3664 | 2668767.0459 | 1212084.904
9 | 2668877.1563 | 1212102.3984 | 2668884.8116 | 1212103.3763
10 | 2668877.1563 | 1212102.3984 | 2668878.352 | 1212109.3944
11 | 2668864.2749 | 1212065.1154 | 2668862.4199 | 1212063.8932 | 2668860.0633 | 1212069.9142 | 2668867.1736 | 1212073.9988 | 2668881.9398 | 1212079.6728 | 2668879.9953 | 1212083.5639 | 2668879.45 | 1212084.725 | 2668876.5341 | 1212089.8279 | 2668876.0606 | 1212095.9595 | 2668877.1563 | 1212102.3984
12 | 2668878.352 | 1212109.3944 | 2668870.0699 | 1212110.0658
13 | 2668887.2206 | 1212126.3629 | 2668886.8719 | 1212121.6893 | 2668879.7652 | 1212119.2724 | 2668878.352 | 1212109.3944
14 | 2668894.8566 | 1212077.0537 | 2668864.2749 | 1212065.1154
15 | 2668877.6009 | 1212063.2569 | 2668870.3194 | 1212062.8059 | 2668864.2749 | 1212065.1154
16 | 2668822.004 | 1212071.8763 | 2668823.0977 | 1212068.6202 | 2668824.6602 | 1212065.5697 | 2668825.6795 | 1212063.4913 | 2668827.8118 | 1212059.1243 | 2668829.7653 | 1212055.111 | 2668830.5201 | 1212053.5743 | 2668858.1353 | 1212062.5096 | 2668862.4199 | 1212063.8932 | 2668864.2749 | 1212065.1154
17 | 2668822.004 | 1212071.8763 | 2668824.929 | 1212079.8039 | 2668826.4075 | 1212084.6795 | 2668826.6783 | 1212088.2071 | 2668827.4917 | 1212089.495 | 2668828.3222 | 1212089.9493 | 2668831.0341 | 1212091.3259 | 2668838.7087 | 1212093.2601
18 | 2668822.004 | 1212071.8763 | 2668823.0977 | 1212068.6202 | 2668824.6602 | 1212065.5697 | 2668816.9923 | 1212069.6282 | 2668813.1275 | 1212072.0296
19 | 2668822.004 | 1212071.8763 | 2668823.0977 | 1212068.6202 | 2668824.6602 | 1212065.5697 | 2668825.6795 | 1212063.4913 | 2668827.8118 | 1212059.1243 | 2668829.7653 | 1212055.111 | 2668830.5201 | 1212053.5743 | 2668832.1099 | 1212046.8328 | 2668832.0791 | 1212044.8979 | 2668832.0399 | 1212042.3737 | 2668832.016 | 1212041.1504 | 2668833.0121 | 1212041.0841 | 2668832.9951 | 1212039.9276 | 2668832.9442 | 1212037.092 | 2668832.8747 | 1212033.2443 | 2668840.4947 | 1212032.6763 | 2668848.2219 | 1212026.7729
20 | 2668848.2219 | 1212026.7729 | 2668858.5116 | 1212027.292 | 2668862.3279 | 1212029.8107
21 | 2668908.9038 | 1212075.904 | 2668906.9227 | 1212076.3815 | 2668895.4895 | 1212074.2259 | 2668894.8566 | 1212077.0537
22 | 2668924.3107 | 1212090.5578 | 2668894.8566 | 1212077.0537
23 | 2669084.4275 | 1212188.9265 | 2669082.1825 | 1212191.8579 | 2669079.1814 | 1212194.4692 | 2669075.2121 | 1212197.3584 | 2669073.2626 | 1212198.392 | 2669066.466 | 1212200.7037 | 2669064.5464 | 1212201.1262 | 2669055.9386 | 1212201.7158 | 2669051.6661 | 1212201.2661 | 2669043.8291 | 1212199.5854 | 2669034.9398 | 1212196.9254 | 2669011.3848 | 1212183.8892 | 2669000.9523 | 1212179.0252
24 | 2668980.6103 | 1212169.5409 | 2669000.9523 | 1212179.0252
25 | 2668980.6103 | 1212169.5409 | 2668979.3266 | 1212168.9425 | 2668937.6954 | 1212156.5647 | 2668909.4035 | 1212152.8232
26 | 2668892.4448 | 1212152.2949 | 2668899.6491 | 1212151.5332 | 2668909.4035 | 1212152.8232
27 | 2668892.4448 | 1212152.2949 | 2668887.1805 | 1212152.8567 | 2668876.8179 | 1212157.351 | 2668868.3535 | 1212163.2792 | 2668860.0962 | 1212172.9899 | 2668855.1154 | 1212184.5285 | 2668853.5495 | 1212195.773 | 2668854.3929 | 1212202.4884
28 | 2668888.3827 | 1212131.6574 | 2668888.6044 | 1212138.7755 | 2668891.8737 | 1212147.1407 | 2668892.4448 | 1212152.2949
29 | 2668854.3929 | 1212202.4884 | 2668855.0177 | 1212207.4639 | 2668858.6274 | 1212216.6224 | 2668864.4104 | 1212224.4385 | 2668869.8624 | 1212230.6497 | 2668879.0641 | 1212237.8382 | 2668886.6961 | 1212241.2596
30 | 2668888.3827 | 1212131.6574 | 2668880.5698 | 1212131.834
31 | 2668888.3827 | 1212131.6574 | 2668887.2206 | 1212126.3629
32 | 2668918.3164 | 1212249.843 | 2668906.4594 | 1212247.972 | 2668890.6216 | 1212243.0193 | 2668886.6961 | 1212241.2596
33 | 2668892.9705 | 1212126.5294 | 2668887.2206 | 1212126.3629
34 | 2668943.6463 | 1212254.6133 | 2668934.5132 | 1212252.3988 | 2668918.3164 | 1212249.843
35 | 2668943.6463 | 1212254.6133 | 2668957.1094 | 1212257.8778
36 | 2668938.0394 | 1212087.3811 | 2668937.7066 | 1212089.2228 | 2668925.1087 | 1212087.2538 | 2668924.3107 | 1212090.5578
37 | 2668962.3529 | 1212101.8933 | 2668954.4517 | 1212102.4802 | 2668924.3107 | 1212090.5578
38 | 2668732.2038 | 1212157.295 | 2668722.1423 | 1212153.757
39 | 2668982.9921 | 1212039.96 | 2668960.8215 | 1212029.3304 | 2668952.3962 | 1212025.4608
40 | 2669023.8963 | 1212060.0456 | 2669019.7534 | 1212057.585 | 2668982.9921 | 1212039.96
41 | 2668732.2038 | 1212157.295 | 2668742.2638 | 1212160.8325
42 | 2669023.8963 | 1212060.0456 | 2669014.9293 | 1212078.9471
43 | 2668977.9591 | 1212104.5643 | 2668989.9141 | 1212095.7637 | 2669005.3214 | 1212099.1996 | 2669014.9293 | 1212078.9471
44 | 2668962.3529 | 1212101.8933 | 2668977.9591 | 1212104.5643
45 | 2668962.3529 | 1212101.8933 | 2668964.9821 | 1212100.5673
46 | 2668962.3529 | 1212101.8933 | 2668954.4517 | 1212102.4802 | 2668979.9768 | 1212116.0281
47 | 2668996.9692 | 1212114.4569 | 2668996.0577 | 1212117.0591 | 2668981.2989 | 1212115.3652 | 2668979.9768 | 1212116.0281
48 | 2668742.2638 | 1212160.8325 | 2668752.3252 | 1212164.3705
49 | 2668752.3252 | 1212164.3705 | 2668762.3865 | 1212167.9084
50 | 2668772.4465 | 1212171.4459 | 2668762.3865 | 1212167.9084

## bus_geodata
| x | y | coords
0 | 2668941.4897 | 1212130.0364
1 | 2668936.5087 | 1212129.7454
2 | 2668942.611 | 1212121.1105
3 | 2668950.1337 | 1212113.8373
4 | 2669025.688 | 1212153.1375
5 | 2668631.8404 | 1212112.4222
6 | 2668712.0791 | 1212150.2184
7 | 2668767.0459 | 1212084.904
8 | 2668877.1563 | 1212102.3984
9 | 2668884.8116 | 1212103.3763
10 | 2668878.352 | 1212109.3944
11 | 2668864.2749 | 1212065.1154
12 | 2668822.004 | 1212071.8763
13 | 2668838.7087 | 1212093.2601
14 | 2668813.1275 | 1212072.0296
15 | 2668848.2219 | 1212026.7729
16 | 2668894.8566 | 1212077.0537
17 | 2668877.6009 | 1212063.2569
18 | 2668862.3279 | 1212029.8107
19 | 2669084.4275 | 1212188.9265
20 | 2669000.9523 | 1212179.0252
21 | 2668909.4035 | 1212152.8232
22 | 2668980.6103 | 1212169.5409
23 | 2668892.4448 | 1212152.2949
24 | 2668854.3929 | 1212202.4884
25 | 2668888.3827 | 1212131.6574
26 | 2668886.6961 | 1212241.2596
27 | 2668880.5698 | 1212131.834
28 | 2668887.2206 | 1212126.3629
29 | 2668918.3164 | 1212249.843
30 | 2668892.9705 | 1212126.5294
31 | 2668957.1094 | 1212257.8778
32 | 2668943.6463 | 1212254.6133
33 | 2668908.9038 | 1212075.904
34 | 2668924.3107 | 1212090.5578
35 | 2668870.0699 | 1212110.0658
36 | 2668722.1423 | 1212153.757
37 | 2668952.3962 | 1212025.4608
38 | 2668982.9921 | 1212039.96
39 | 2668732.2038 | 1212157.295
40 | 2669023.8963 | 1212060.0456
41 | 2669014.9293 | 1212078.9471
42 | 2668977.9591 | 1212104.5643
43 | 2668962.3529 | 1212101.8933
44 | 2668964.9821 | 1212100.5673
45 | 2668979.9768 | 1212116.0281
46 | 2668938.0394 | 1212087.3811
47 | 2668996.9692 | 1212114.4569
48 | 2668742.2638 | 1212160.8325
49 | 2668752.3252 | 1212164.3705
50 | 2668762.3865 | 1212167.9084
51 | 2668772.4465 | 1212171.4459
52 | 2668892.4448 | 1212152.2949

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98839 | -0.22361 | 0.0082879 | 0.0020771
1 | 0.98836 | -0.22431 | 0.0078979 | 0.0019794
2 | 0.98853 | -0.22101 | 0 | 0
3 | 0.98868 | -0.21799 | 0 | 0
4 | 0.98995 | -0.19343 | 0.011792 | 0.0029553
5 | 0.97712 | -0.43923 | 0 | 0
6 | 0.97359 | -0.50862 | 0.0059222 | 0.0014843
7 | 0.98247 | -0.33504 | 0.013785 | 0.0034548
8 | 0.99436 | -0.10668 | 0 | 0
9 | 0.99428 | -0.10832 | 0.012107 | 0.0030342
10 | 0.99479 | -0.098518 | 0 | 0
11 | 0.98951 | -0.19921 | 0 | 0
12 | 0.98611 | -0.26454 | 0 | 0
13 | 0.98597 | -0.26744 | 0.0053006 | 0.0013285
14 | 0.98508 | -0.28445 | 0 | 0
15 | 0.98585 | -0.26964 | 0 | 0
16 | 0.98607 | -0.26536 | 0 | 0
17 | 0.98945 | -0.20047 | 0.0051524 | 0.0012913
18 | 0.98579 | -0.27092 | 0.0048158 | 0.001207
19 | 0.99171 | -0.15925 | 0 | 0
20 | 0.99409 | -0.11344 | 0.033423 | 0.0083766
21 | 1 | 0 | -0.44013 | -0.11254
22 | 0.99535 | -0.089162 | 0.0079716 | 0.0019979
23 | 0.99809 | -0.036029 | 0 | 0
24 | 0.98951 | -0.19971 | 0.012245 | 0.003069
25 | 0.99658 | -0.064689 | 0 | 0
26 | 0.98366 | -0.31296 | 0.026221 | 0.0065717
27 | 0.99648 | -0.066561 | 0.013687 | 0.0034302
28 | 0.99621 | -0.071566 | 0 | 0
29 | 0.98082 | -0.36844 | 0.031042 | 0.0077798
30 | 0.99617 | -0.0725 | 0.0092699 | 0.0023233
31 | 0.9789 | -0.406 | 0.033296 | 0.0083449
32 | 0.97933 | -0.39761 | 0.029015 | 0.0072718
33 | 0.98587 | -0.26928 | 0.01323 | 0.0033157
34 | 0.98307 | -0.3234 | 0 | 0
35 | 0.9947 | -0.10024 | 0.011797 | 0.0029566
36 | 0.97323 | -0.51559 | 0.0059202 | 0.0014837
37 | 0.97238 | -0.53287 | 0.024267 | 0.0060819
38 | 0.97314 | -0.51773 | 0.018133 | 0.0045445
39 | 0.97294 | -0.5214 | 0.0059202 | 0.0014837
40 | 0.97494 | -0.48222 | 0 | 0
41 | 0.97577 | -0.46597 | 0.019908 | 0.0049895
42 | 0.97885 | -0.40565 | 0 | 0
43 | 0.97977 | -0.38777 | 0 | 0
44 | 0.97972 | -0.38867 | 0.016764 | 0.0042014
45 | 0.97945 | -0.39387 | 0 | 0
46 | 0.98288 | -0.32719 | 0.011673 | 0.0029256
47 | 0.97929 | -0.39702 | 0.0091102 | 0.0022832
48 | 0.9727 | -0.52606 | 0.0059187 | 0.0014834
49 | 0.97253 | -0.52955 | 0.0059233 | 0.0014845
50 | 0.97241 | -0.53187 | 0.0059187 | 0.0014834
51 | 0.97235 | -0.53304 | 0.0059202 | 0.0014837
52 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0078982 | 0.0019795 | -0.0078979 | -0.0019794 | 2.6455e-07 | 1.0536e-07 | 0.011891 | 0.011891 | 0.011891 | 0.98839 | -0.22361 | 0.98836 | -0.22431 | 3.2667
1 | -0.016186 | -0.0040566 | 0.016188 | 0.0040578 | 2.0032e-06 | 1.1667e-06 | 0.024368 | 0.024368 | 0.024368 | 0.98839 | -0.22361 | 0.98853 | -0.22101 | 6.6945
2 | -0.016188 | -0.0040578 | 0.01619 | 0.0040592 | 2.3278e-06 | 1.3558e-06 | 0.024368 | 0.024368 | 0.024368 | 0.98853 | -0.22101 | 0.98868 | -0.21799 | 6.6945
3 | -0.01619 | -0.0040592 | 0.016209 | 0.0040702 | 1.8974e-05 | 1.1049e-05 | 0.024368 | 0.024367 | 0.024368 | 0.98868 | -0.21799 | 0.98995 | -0.19343 | 6.6945
4 | -0.028001 | -0.0070255 | 0.028047 | 0.0070539 | 4.5712e-05 | 2.837e-05 | 0.042092 | 0.042092 | 0.042092 | 0.98995 | -0.19343 | 0.99171 | -0.15925 | 11.5638
5 | 0.041611 | 0.010492 | -0.041473 | -0.010405 | 0.0001377 | 8.699e-05 | 0.063391 | 0.063391 | 0.063391 | 0.97712 | -0.43923 | 0.97359 | -0.50862 | 17.4152
6 | -0.041611 | -0.010492 | 0.04182 | 0.010624 | 0.00020863 | 0.00013178 | 0.063391 | 0.06339 | 0.063391 | 0.97712 | -0.43923 | 0.98247 | -0.33504 | 17.4151
7 | 0.035551 | 0.0089208 | -0.035539 | -0.0089134 | 1.1812e-05 | 7.427e-06 | 0.05434 | 0.05434 | 0.05434 | 0.97359 | -0.50862 | 0.97323 | -0.51559 | 14.9285
8 | -0.055605 | -0.014079 | 0.05574 | 0.014165 | 0.00013541 | 8.6017e-05 | 0.084268 | 0.084268 | 0.084268 | 0.98247 | -0.33504 | 0.98508 | -0.28445 | 23.1506
9 | 0.012108 | 0.0030347 | -0.012107 | -0.0030342 | 9.4729e-07 | 5.0645e-07 | 0.018118 | 0.018118 | 0.018118 | 0.99436 | -0.10668 | 0.99428 | -0.10832 | 4.9776
10 | -0.19858 | -0.050883 | 0.19866 | 0.050933 | 7.8563e-05 | 5.0004e-05 | 0.29757 | 0.29757 | 0.29757 | 0.99436 | -0.10668 | 0.99479 | -0.098518 | 27.2497
11 | 0.18648 | 0.047849 | -0.18564 | -0.047317 | 0.0008331 | 0.00053172 | 0.27945 | 0.27945 | 0.27945 | 0.99436 | -0.10668 | 0.98951 | -0.19921 | 38.3859
12 | 0.011798 | 0.0029571 | -0.011797 | -0.0029566 | 9.6759e-07 | 5.117e-07 | 0.017647 | 0.017648 | 0.017648 | 0.99479 | -0.098518 | 0.9947 | -0.10024 | 4.8482
13 | -0.21046 | -0.053891 | 0.21073 | 0.054066 | 0.00027515 | 0.00017523 | 0.31521 | 0.31521 | 0.31521 | 0.99479 | -0.098518 | 0.99621 | -0.071566 | 28.8658
14 | 0.11437 | 0.029159 | -0.11401 | -0.028927 | 0.00036398 | 0.00023253 | 0.17216 | 0.17217 | 0.17217 | 0.98951 | -0.19921 | 0.98607 | -0.26536 | 47.2981
15 | 0.0051527 | 0.0012913 | -0.0051524 | -0.0012913 | 3.0908e-07 | 2.1481e-08 | 0.0077485 | 0.0077485 | 0.0077485 | 0.98951 | -0.19921 | 0.98945 | -0.20047 | 2.1287
16 | 0.06612 | 0.016866 | -0.065912 | -0.016734 | 0.00020791 | 0.00013235 | 0.099536 | 0.099536 | 0.099536 | 0.98951 | -0.19921 | 0.98611 | -0.26454 | 27.3452
17 | 0.0053013 | 0.0013285 | -0.0053006 | -0.0013285 | 7.3132e-07 | 7.9322e-08 | 0.0079995 | 0.0079997 | 0.0079997 | 0.98611 | -0.26454 | 0.98597 | -0.26744 | 2.1977
18 | 0.055794 | 0.014199 | -0.05574 | -0.014165 | 5.3493e-05 | 3.3979e-05 | 0.084268 | 0.084268 | 0.084268 | 0.98611 | -0.26454 | 0.98508 | -0.28445 | 23.1506
19 | 0.0048173 | 0.001207 | -0.0048161 | -0.001207 | 1.1696e-06 | -4.2703e-09 | 0.007269 | 0.0072693 | 0.0072693 | 0.98611 | -0.26454 | 0.98585 | -0.26964 | 1.9971
20 | 0.0048161 | 0.001207 | -0.0048158 | -0.001207 | 2.9477e-07 | -1.0045e-09 | 0.0072693 | 0.0072694 | 0.0072694 | 0.98585 | -0.26964 | 0.98579 | -0.27092 | 1.9971
21 | 0.013232 | 0.0033171 | -0.01323 | -0.0033157 | 2.4719e-06 | 1.3712e-06 | 0.019968 | 0.019968 | 0.019968 | 0.98607 | -0.26536 | 0.98587 | -0.26928 | 5.4858
22 | 0.10077 | 0.02561 | -0.10049 | -0.02543 | 0.00028078 | 0.00017929 | 0.1522 | 0.1522 | 0.1522 | 0.98607 | -0.26536 | 0.98307 | -0.3234 | 41.8124
23 | -0.028047 | -0.0070539 | 0.028108 | 0.0070921 | 6.151e-05 | 3.8169e-05 | 0.042092 | 0.042091 | 0.042092 | 0.99171 | -0.15925 | 0.99409 | -0.11344 | 11.5637
24 | -0.061531 | -0.015469 | 0.061603 | 0.015514 | 7.1426e-05 | 4.5422e-05 | 0.092121 | 0.092121 | 0.092121 | 0.99409 | -0.11344 | 0.99535 | -0.089162 | 25.3081
25 | 0.069872 | 0.017702 | -0.069574 | -0.017512 | 0.00029788 | 0.00018968 | 0.10404 | 0.10404 | 0.10404 | 1 | 0 | 0.99535 | -0.089162 | 28.582
26 | 0.36861 | 0.094836 | -0.36797 | -0.094424 | 0.0006445 | 0.00041181 | 0.54937 | 0.54937 | 0.54937 | 1 | 0 | 0.99809 | -0.036029 | 50.3087
27 | 0.13388 | 0.03435 | -0.13282 | -0.033676 | 0.001054 | 0.00067368 | 0.19987 | 0.19987 | 0.19987 | 0.99809 | -0.036029 | 0.98951 | -0.19971 | 54.9102
28 | 0.23409 | 0.060074 | -0.23377 | -0.059867 | 0.00032505 | 0.0002072 | 0.3495 | 0.3495 | 0.3495 | 0.99809 | -0.036029 | 0.99658 | -0.064689 | 32.0053
29 | 0.12058 | 0.030607 | -0.11992 | -0.03019 | 0.00065303 | 0.00041727 | 0.18146 | 0.18146 | 0.18146 | 0.98951 | -0.19971 | 0.98366 | -0.31296 | 49.8514
30 | 0.013688 | 0.0034309 | -0.013687 | -0.0034302 | 1.2205e-06 | 6.7963e-07 | 0.020438 | 0.020438 | 0.020438 | 0.99658 | -0.064689 | 0.99648 | -0.066561 | 5.6148
31 | 0.22008 | 0.056436 | -0.22001 | -0.056389 | 7.3374e-05 | 4.6747e-05 | 0.32906 | 0.32906 | 0.32906 | 0.99658 | -0.064689 | 0.99621 | -0.071566 | 30.1338
32 | 0.093701 | 0.023618 | -0.093453 | -0.02346 | 0.00024805 | 0.00015833 | 0.14179 | 0.14179 | 0.14179 | 0.98366 | -0.31296 | 0.98082 | -0.36844 | 38.9542
33 | 0.0092703 | 0.0023234 | -0.0092699 | -0.0023233 | 4.1235e-07 | 1.8924e-07 | 0.013847 | 0.013847 | 0.013847 | 0.99621 | -0.071566 | 0.99617 | -0.0725 | 3.8041
34 | 0.062411 | 0.01568 | -0.062325 | -0.015625 | 8.6748e-05 | 5.5194e-05 | 0.094699 | 0.094699 | 0.094699 | 0.98082 | -0.36844 | 0.97933 | -0.39761 | 26.0163
35 | -0.033296 | -0.0083449 | 0.03331 | 0.0083532 | 1.3308e-05 | 8.3429e-06 | 0.050613 | 0.050613 | 0.050613 | 0.9789 | -0.406 | 0.97933 | -0.39761 | 13.9048
36 | 0.011675 | 0.0029267 | -0.011673 | -0.0029256 | 2.1064e-06 | 1.1201e-06 | 0.017673 | 0.017673 | 0.017673 | 0.98307 | -0.3234 | 0.98288 | -0.32719 | 4.8551
37 | 0.088817 | 0.022504 | -0.088544 | -0.022329 | 0.00027374 | 0.00017468 | 0.13452 | 0.13452 | 0.13452 | 0.98307 | -0.3234 | 0.97977 | -0.38777 | 36.9574
38 | 0.029619 | 0.0074296 | -0.029611 | -0.0074245 | 8.2032e-06 | 5.1175e-06 | 0.045288 | 0.045288 | 0.045288 | 0.97323 | -0.51559 | 0.97294 | -0.5214 | 12.4418
39 | -0.024267 | -0.0060819 | 0.024284 | 0.0060927 | 1.751e-05 | 1.0786e-05 | 0.037135 | 0.037135 | 0.037135 | 0.97238 | -0.53287 | 0.97314 | -0.51773 | 10.202
40 | -0.042417 | -0.010637 | 0.042489 | 0.010683 | 7.192e-05 | 4.5461e-05 | 0.064862 | 0.064862 | 0.064862 | 0.97314 | -0.51773 | 0.97494 | -0.48222 | 17.8192
41 | 0.023691 | 0.0059408 | -0.023686 | -0.0059375 | 5.2502e-06 | 3.2277e-06 | 0.036234 | 0.036234 | 0.036234 | 0.97294 | -0.5214 | 0.9727 | -0.52606 | 9.9544
42 | -0.042489 | -0.010683 | 0.042522 | 0.010704 | 3.3005e-05 | 2.0862e-05 | 0.064862 | 0.064862 | 0.064862 | 0.97494 | -0.48222 | 0.97577 | -0.46597 | 17.8192
43 | -0.062431 | -0.015693 | 0.062611 | 0.015808 | 0.00018037 | 0.00011477 | 0.095221 | 0.095221 | 0.095221 | 0.97577 | -0.46597 | 0.97885 | -0.40565 | 26.1597
44 | -0.062611 | -0.015808 | 0.062665 | 0.015842 | 5.3682e-05 | 3.4158e-05 | 0.095221 | 0.095221 | 0.095221 | 0.97885 | -0.40565 | 0.97977 | -0.38777 | 26.1597
45 | 0.016765 | 0.0042019 | -0.016764 | -0.0042014 | 7.1424e-07 | 4.2012e-07 | 0.025461 | 0.025461 | 0.025461 | 0.97977 | -0.38777 | 0.97972 | -0.38867 | 6.9949
46 | 0.0091142 | 0.0022851 | -0.0091116 | -0.0022839 | 2.6458e-06 | 1.2298e-06 | 0.013843 | 0.013843 | 0.013843 | 0.97977 | -0.38777 | 0.97945 | -0.39387 | 3.8029
47 | 0.0091116 | 0.0022839 | -0.0091102 | -0.0022832 | 1.3686e-06 | 6.3624e-07 | 0.013843 | 0.013843 | 0.013843 | 0.97945 | -0.39387 | 0.97929 | -0.39702 | 3.803
48 | 0.017767 | 0.0044542 | -0.017764 | -0.0044524 | 2.9545e-06 | 1.7585e-06 | 0.02718 | 0.02718 | 0.02718 | 0.9727 | -0.52606 | 0.97253 | -0.52955 | 7.4669
49 | 0.011841 | 0.0029679 | -0.011839 | -0.0029672 | 1.3127e-06 | 7.0781e-07 | 0.018117 | 0.018117 | 0.018117 | 0.97253 | -0.52955 | 0.97241 | -0.53187 | 4.9772
50 | 0.0059205 | 0.0014838 | -0.0059202 | -0.0014837 | 3.2823e-07 | 7.7788e-08 | 0.0090598 | 0.0090598 | 0.0090598 | 0.97241 | -0.53187 | 0.97235 | -0.53304 | 2.489

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4593 | 0.11734

## res_load
| p_mw | q_mvar
0 | 0.0082879 | 0.0020771
1 | 0.0078979 | 0.0019794
2 | 0.011792 | 0.0029553
3 | 0.0059222 | 0.0014843
4 | 0.013785 | 0.0034548
5 | 0.012107 | 0.0030342
6 | 0.0053006 | 0.0013285
7 | 0.0051524 | 0.0012913
8 | 0.0048158 | 0.001207
9 | 0.033423 | 0.0083766
10 | 0.019163 | 0.0048028
11 | 0.0079716 | 0.0019979
12 | 0.012245 | 0.003069
13 | 0.026221 | 0.0065717
14 | 0.013687 | 0.0034302
15 | 0.031042 | 0.0077798
16 | 0.0092699 | 0.0023233
17 | 0.033296 | 0.0083449
18 | 0.029015 | 0.0072718
19 | 0.01323 | 0.0033157
20 | 0.011797 | 0.0029566
21 | 0.0059202 | 0.0014837
22 | 0.024267 | 0.0060819
23 | 0.018133 | 0.0045445
24 | 0.0059202 | 0.0014837
25 | 0.019908 | 0.0049895
26 | 0.016764 | 0.0042014
27 | 0.011673 | 0.0029256
28 | 0.0091102 | 0.0022832
29 | 0.0059187 | 0.0014834
30 | 0.0059233 | 0.0014845
31 | 0.0059187 | 0.0014834
32 | 0.0059202 | 0.0014837

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1