## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-236_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-236_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-236_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-236_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-236_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-236_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1061-236_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1061-236_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1061-236_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1061-236_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1061-236_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1061-236_0_3_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1061-236_0_3_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1061-236_0_3_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1061-236_0_3_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1061-236_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1061-236_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1061-236_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1061-236_0_3_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_1061-236_0_3_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1061-236_0_3_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1061-236_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1061-236_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1061-236_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1061-236_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1061-236_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1061-236_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1061-236_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1061-236_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_MV_211_1_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-236_0_3_load_0 | 0 | 0.010211 | 0.0025591 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-236_0_3_load_1 | 1 | 0.016334 | 0.0040937 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-236_0_3_load_2 | 2 | 0.019578 | 0.0049068 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-236_0_3_load_3 | 3 | 0.010314 | 0.0025848 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-236_0_3_load_4 | 4 | 0.011767 | 0.0029491 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-236_0_3_load_9 | 5 | 0.01356 | 0.0033984 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-236_0_3_load_5 | 6 | 0.019268 | 0.0048291 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-236_0_3_load_7 | 7 | 0.010755 | 0.0026955 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-236_0_3_load_8 | 10 | 0.015145 | 0.0037957 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-236_0_3_load_26 | 12 | 0.0054243 | 0.0013595 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-236_0_3_load_25 | 14 | 0.021228 | 0.0053202 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-236_0_3_load_27 | 18 | 0.025833 | 0.0064744 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-236_0_3_load_28 | 20 | 0.02296 | 0.0057542 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-236_0_3_load_11 | 22 | 0.012073 | 0.0030259 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-236_0_3_load_22 | 25 | 0.0088453 | 0.0022169 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-236_0_3_load_29 | 26 | 0.026762 | 0.0067072 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-236_0_3_load_24 | 27 | 0.012673 | 0.0031762 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-236_0_3_load_23 | 28 | 0.012091 | 0.0030304 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-236_0_3_line_0 |  | 0 | 1 | 0.033609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-236_0_3_line_1 |  | 0 | 2 | 0.0022574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-236_0_3_line_2 |  | 1 | 3 | 0.0055304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-236_0_3_line_3 |  | 2 | 4 | 0.029712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-236_0_3_line_4 |  | 3 | 5 | 0.028515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-236_0_3_line_5 |  | 4 | 6 | 0.013253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-236_0_3_line_6 |  | 5 | 7 | 0.0066789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1061-236_0_3_line_7 |  | 7 | 10 | 0.011763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1061-236_0_3_line_8 |  | 8 | 9 | 0.11709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1061-236_0_3_line_9 |  | 8 | 10 | 0.041841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1061-236_0_3_line_10 |  | 9 | 21 | 0.012801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1061-236_0_3_line_11 |  | 9 | 22 | 0.014276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-236_0_3_line_12 |  | 11 | 12 | 0.003179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-236_0_3_line_13 |  | 11 | 13 | 0.075611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-236_0_3_line_14 |  | 13 | 14 | 0.023667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-236_0_3_line_15 |  | 13 | 15 | 0.069941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-236_0_3_line_16 |  | 13 | 16 | 0.038793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-236_0_3_line_17 |  | 15 | 20 | 0.027846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-236_0_3_line_18 |  | 15 | 17 | 0.070731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-236_0_3_line_19 |  | 16 | 23 | 0.019124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1061-236_0_3_line_20 |  | 17 | 18 | 0.005239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-236_0_3_line_21 |  | 17 | 19 | 0.054587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-236_0_3_line_22 |  | 19 | 26 | 0.006463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-236_0_3_line_23 |  | 21 | 24 | 0.015916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1061-236_0_3_line_24 |  | 21 | 25 | 0.006326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-236_0_3_line_25 |  | 23 | 27 | 0.006756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-236_0_3_line_26 |  | 23 | 24 | 0.018014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1061-236_0_3_line_27 |  | 24 | 28 | 0.005552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-236_0_3_trafo_9 | 0.63 MVA 20/0.4 kV | 29 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2669010.8439 | 1211949.4699 | 2668985.2496 | 1211930.8403 | 2668983.5522 | 1211929.8752
1 | 2669010.8439 | 1211949.4699 | 2669012.6691 | 1211950.7984
2 | 2668983.5522 | 1211929.8752 | 2668978.7446 | 1211927.1418
3 | 2669036.7618 | 1211968.1788 | 2669035.2437 | 1211967.2301 | 2669012.6691 | 1211950.7984
4 | 2668953.7521 | 1211913.4627 | 2668957.3645 | 1211914.9859 | 2668978.7446 | 1211927.1418
5 | 2669036.7618 | 1211968.1788 | 2669048.0002 | 1211975.2025
6 | 2668953.7521 | 1211913.4627 | 2668947.5978 | 1211910.8678
7 | 2668936.7593 | 1211906.2979 | 2668947.5978 | 1211910.8678
8 | 2668888.8632 | 1211850.6656 | 2668876.8321 | 1211852.2166 | 2668867.0907 | 1211853.5383 | 2668859.2607 | 1211855.8271 | 2668856.4996 | 1211856.7292 | 2668853.6527 | 1211855.8513 | 2668859.4477 | 1211874.5076 | 2668860.162 | 1211883.0545 | 2668866.381 | 1211901.838 | 2668868.2313 | 1211907.4184 | 2668873.6194 | 1211906.6912 | 2668878.2998 | 1211906.056 | 2668895.3428 | 1211904.1071
9 | 2668895.3428 | 1211904.1071 | 2668900.0905 | 1211903.5615 | 2668913.0578 | 1211902.5218 | 2668923.9583 | 1211903.4594 | 2668936.7593 | 1211906.2979
10 | 2668888.8632 | 1211850.6656 | 2668894.6183 | 1211839.225
11 | 2668888.8632 | 1211850.6656 | 2668902.8256 | 1211847.6917
12 | 2668887.606 | 1211787.8231 | 2668890.7783 | 1211787.504
13 | 2668890.7783 | 1211787.504 | 2668893.9949 | 1211787.9525 | 2668897.5564 | 1211788.8053 | 2668902.2844 | 1211789.9717 | 2668911.3253 | 1211792.0663 | 2668914.0212 | 1211792.2086 | 2668915.4819 | 1211792.0476 | 2668916.4926 | 1211790.7251 | 2668917.3463 | 1211787.8665 | 2668917.6352 | 1211786.5357 | 2668922.7729 | 1211787.7625 | 2668931.1743 | 1211789.9609 | 2668945.5325 | 1211793.5179 | 2668955.6833 | 1211796.2258 | 2668956.7884 | 1211791.9915 | 2668957.4928 | 1211792.1886
14 | 2668971.1734 | 1211777.4598 | 2668972.1297 | 1211778.2158 | 2668969.0455 | 1211780.7706 | 2668968.6737 | 1211782.0449 | 2668968.1412 | 1211784.0622 | 2668967.9196 | 1211785.4827 | 2668965.7618 | 1211786.7808 | 2668963.5726 | 1211786.8556 | 2668962.0934 | 1211786.6383 | 2668958.6491 | 1211789.4447 | 2668957.4928 | 1211792.1886
15 | 2668957.4928 | 1211792.1886 | 2668970.8381 | 1211795.9452 | 2668987.7434 | 1211800.0098 | 2668994.948 | 1211802.5392 | 2668996.0556 | 1211806.6323 | 2668995.8544 | 1211807.6084 | 2668995.4203 | 1211809.6602 | 2668993.6512 | 1211814.1425 | 2668995.3137 | 1211820.1877 | 2668996.3639 | 1211825.3031 | 2668996.3392 | 1211829.4053 | 2668995.3907 | 1211832.5741
16 | 2668946.7594 | 1211828.6984 | 2668947.3037 | 1211826.9703 | 2668949.2993 | 1211820.645 | 2668953.771 | 1211803.8862 | 2668955.3889 | 1211797.3675 | 2668955.6833 | 1211796.2258 | 2668956.7884 | 1211791.9915 | 2668957.4928 | 1211792.1886
17 | 2668980.7123 | 1211817.962 | 2668985.1896 | 1211813.8667 | 2668988.2328 | 1211818.7939 | 2668992.4897 | 1211830.4615 | 2668995.3907 | 1211832.5741
18 | 2668995.3907 | 1211832.5741 | 2668996.3392 | 1211829.4053 | 2668996.3639 | 1211825.3031 | 2668995.3137 | 1211820.1877 | 2668993.6512 | 1211814.1425 | 2668995.4203 | 1211809.6602 | 2668995.8544 | 1211807.6084 | 2668998.6096 | 1211809.1856 | 2669008.1482 | 1211814.8884 | 2669013.8888 | 1211819.1575 | 2669020.7957 | 1211824.4295 | 2669027.6376 | 1211830.0566 | 2669032.2448 | 1211833.7789
19 | 2668946.7594 | 1211828.6984 | 2668943.647 | 1211829.0961 | 2668930.2119 | 1211831.8092 | 2668927.9268 | 1211832.2831
20 | 2669028.9987 | 1211837.855 | 2669029.7979 | 1211836.4189 | 2669031.4287 | 1211834.7034 | 2669032.2448 | 1211833.7789
21 | 2669032.2448 | 1211833.7789 | 2669033.7204 | 1211834.9634 | 2669035.9236 | 1211835.656 | 2669037.2882 | 1211841.1752 | 2669039.8721 | 1211845.7302 | 2669042.9248 | 1211848.5228 | 2669058.6887 | 1211863.2144 | 2669067.3702 | 1211867.4619 | 2669069.0032 | 1211866.8582 | 2669069.5921 | 1211869.1554
22 | 2669074.5918 | 1211873.1046 | 2669071.8968 | 1211870.2605 | 2669069.5921 | 1211869.1554
23 | 2668894.6183 | 1211839.225 | 2668910.2478 | 1211835.9923
24 | 2668889.6101 | 1211835.3425 | 2668894.6183 | 1211839.225
25 | 2668924.4154 | 1211827.106 | 2668927.5043 | 1211829.3986 | 2668927.9268 | 1211832.2831
26 | 2668910.2478 | 1211835.9923 | 2668927.9268 | 1211832.2831
27 | 2668910.2478 | 1211835.9923 | 2668907.3085 | 1211831.2777

## bus_geodata
| x | y | coords
0 | 2669010.8439 | 1211949.4699
1 | 2668983.5522 | 1211929.8752
2 | 2669012.6691 | 1211950.7984
3 | 2668978.7446 | 1211927.1418
4 | 2669036.7618 | 1211968.1788
5 | 2668953.7521 | 1211913.4627
6 | 2669048.0002 | 1211975.2025
7 | 2668947.5978 | 1211910.8678
8 | 2668895.3428 | 1211904.1071
9 | 2668888.8632 | 1211850.6656
10 | 2668936.7593 | 1211906.2979
11 | 2668890.7783 | 1211787.504
12 | 2668887.606 | 1211787.8231
13 | 2668957.4928 | 1211792.1886
14 | 2668971.1734 | 1211777.4598
15 | 2668995.3907 | 1211832.5741
16 | 2668946.7594 | 1211828.6984
17 | 2669032.2448 | 1211833.7789
18 | 2669028.9987 | 1211837.855
19 | 2669069.5921 | 1211869.1554
20 | 2668980.7123 | 1211817.962
21 | 2668894.6183 | 1211839.225
22 | 2668902.8256 | 1211847.6917
23 | 2668927.9268 | 1211832.2831
24 | 2668910.2478 | 1211835.9923
25 | 2668889.6101 | 1211835.3425
26 | 2669074.5918 | 1211873.1046
27 | 2668924.4154 | 1211827.106
28 | 2668907.3085 | 1211831.2777
29 | 2668895.3428 | 1211904.1071

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99548 | -0.086937 | 0.010211 | 0.0025591
1 | 0.99734 | -0.051048 | 0.016334 | 0.0040937
2 | 0.99537 | -0.088947 | 0.019578 | 0.0049068
3 | 0.99773 | -0.043574 | 0.010314 | 0.0025848
4 | 0.99453 | -0.10518 | 0.011767 | 0.0029491
5 | 1 | 0 | -0.26634 | -0.067662
6 | 0.9943 | -0.10968 | 0.019268 | 0.0048291
7 | 0.99946 | -0.010123 | 0.010755 | 0.0026955
8 | 0.9957 | -0.081116 | 0 | 0
9 | 0.98766 | -0.2346 | 0 | 0
10 | 0.99857 | -0.026871 | 0.015145 | 0.0037957
11 | 0.97997 | -0.38348 | 0 | 0
12 | 0.97995 | -0.3838 | 0.0054243 | 0.0013595
13 | 0.98035 | -0.37604 | 0 | 0
14 | 0.97988 | -0.38516 | 0.021228 | 0.0053202
15 | 0.97542 | -0.47237 | 0 | 0
16 | 0.98404 | -0.3044 | 0 | 0
17 | 0.97194 | -0.54076 | 0 | 0
18 | 0.97182 | -0.54326 | 0.025833 | 0.0064744
19 | 0.97058 | -0.56776 | 0 | 0
20 | 0.97482 | -0.48409 | 0.02296 | 0.0057542
21 | 0.98685 | -0.25014 | 0 | 0
22 | 0.9875 | -0.23768 | 0.012073 | 0.0030259
23 | 0.98495 | -0.28682 | 0 | 0
24 | 0.98591 | -0.26825 | 0 | 0
25 | 0.9868 | -0.25115 | 0.0088453 | 0.0022169
26 | 0.97042 | -0.57096 | 0.026762 | 0.0067072
27 | 0.98487 | -0.28836 | 0.012673 | 0.0031762
28 | 0.98585 | -0.26945 | 0.012091 | 0.0030304
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.060858 | -0.015265 | 0.060962 | 0.015331 | 0.00010431 | 6.6319e-05 | 0.090973 | 0.090973 | 0.090973 | 0.99548 | -0.086937 | 0.99734 | -0.051048 | 24.9926
1 | 0.050647 | 0.012706 | -0.050642 | -0.012702 | 4.8523e-06 | 3.0761e-06 | 0.07571 | 0.07571 | 0.07571 | 0.99548 | -0.086937 | 0.99537 | -0.088947 | 20.7995
2 | -0.077296 | -0.019425 | 0.077324 | 0.019442 | 2.7591e-05 | 1.7586e-05 | 0.11534 | 0.11534 | 0.11534 | 0.99734 | -0.051048 | 0.99773 | -0.043574 | 31.6877
3 | 0.031064 | 0.0077957 | -0.03104 | -0.0077807 | 2.4031e-05 | 1.4994e-05 | 0.046442 | 0.046442 | 0.046442 | 0.99537 | -0.088947 | 0.99453 | -0.10518 | 12.7588
4 | -0.087637 | -0.022027 | 0.08782 | 0.022144 | 0.00018273 | 0.00011658 | 0.13073 | 0.13072 | 0.13073 | 0.99773 | -0.043574 | 1 | 0 | 35.9135
5 | 0.019272 | 0.0048316 | -0.019268 | -0.0048291 | 4.1324e-06 | 2.4728e-06 | 0.028836 | 0.028836 | 0.028836 | 0.99453 | -0.10518 | 0.9943 | -0.10968 | 7.922
6 | 0.17687 | 0.045518 | -0.17679 | -0.045463 | 8.7026e-05 | 5.5521e-05 | 0.26361 | 0.26361 | 0.26361 | 1 | 0 | 0.99946 | -0.010123 | 36.2108
7 | 0.16603 | 0.042767 | -0.1659 | -0.042681 | 0.00013521 | 8.6228e-05 | 0.2476 | 0.2476 | 0.2476 | 0.99946 | -0.010123 | 0.99857 | -0.026871 | 34.0114
8 | 0.15035 | 0.038632 | -0.14924 | -0.037924 | 0.0011118 | 0.00070856 | 0.22504 | 0.22504 | 0.22504 | 0.9957 | -0.081116 | 0.98766 | -0.2346 | 30.9116
9 | -0.15035 | -0.038632 | 0.15075 | 0.038885 | 0.00039728 | 0.00025317 | 0.22504 | 0.22504 | 0.22504 | 0.9957 | -0.081116 | 0.99857 | -0.026871 | 30.9115
10 | 0.13717 | 0.034897 | -0.13707 | -0.034831 | 0.00010269 | 6.5395e-05 | 0.20684 | 0.20684 | 0.20684 | 0.98766 | -0.2346 | 0.98685 | -0.25014 | 28.4126
11 | 0.012075 | 0.0030268 | -0.012073 | -0.0030259 | 1.7718e-06 | 9.5131e-07 | 0.018193 | 0.018193 | 0.018193 | 0.98766 | -0.2346 | 0.9875 | -0.23768 | 4.998
12 | 0.0054244 | 0.0013595 | -0.0054243 | -0.0013595 | 8.0876e-08 | 1.1709e-08 | 0.0082366 | 0.0082366 | 0.0082366 | 0.97997 | -0.38348 | 0.97995 | -0.3838 | 2.2628
13 | -0.0054244 | -0.0013595 | 0.0054263 | 0.0013598 | 1.9235e-06 | 2.7806e-07 | 0.0082366 | 0.0082363 | 0.0082366 | 0.97997 | -0.38348 | 0.98035 | -0.37604 | 2.2628
14 | 0.021237 | 0.0053258 | -0.021228 | -0.0053202 | 9.2225e-06 | 5.6042e-06 | 0.032236 | 0.032236 | 0.032236 | 0.98035 | -0.37604 | 0.97988 | -0.38516 | 8.856
15 | 0.076132 | 0.019302 | -0.075782 | -0.019079 | 0.00035072 | 0.00022358 | 0.11564 | 0.11564 | 0.11564 | 0.98035 | -0.37604 | 0.97542 | -0.47237 | 31.7685
16 | -0.1028 | -0.025988 | 0.10315 | 0.026214 | 0.00035452 | 0.0002264 | 0.15611 | 0.15611 | 0.15611 | 0.98035 | -0.37604 | 0.98404 | -0.3044 | 42.8871
17 | 0.022972 | 0.0057621 | -0.02296 | -0.0057542 | 1.2826e-05 | 7.8611e-06 | 0.035046 | 0.035047 | 0.035047 | 0.97542 | -0.47237 | 0.97482 | -0.48409 | 9.6282
18 | 0.052809 | 0.013317 | -0.052637 | -0.013207 | 0.00017227 | 0.00010937 | 0.080591 | 0.080591 | 0.080591 | 0.97542 | -0.47237 | 0.97194 | -0.54076 | 22.1405
19 | -0.10315 | -0.026214 | 0.10324 | 0.02627 | 8.7384e-05 | 5.544e-05 | 0.15611 | 0.15611 | 0.15611 | 0.98404 | -0.3044 | 0.98495 | -0.28682 | 21.4435
20 | 0.025836 | 0.0064763 | -0.025833 | -0.0064744 | 3.0739e-06 | 1.9024e-06 | 0.039555 | 0.039555 | 0.039555 | 0.97194 | -0.54076 | 0.97182 | -0.54326 | 10.8668
21 | 0.026801 | 0.0067311 | -0.026766 | -0.0067098 | 3.4471e-05 | 2.1386e-05 | 0.041036 | 0.041036 | 0.041036 | 0.97194 | -0.54076 | 0.97058 | -0.56776 | 11.2737
22 | 0.026766 | 0.0067098 | -0.026762 | -0.0067072 | 4.0814e-06 | 2.5322e-06 | 0.041036 | 0.041036 | 0.041036 | 0.97058 | -0.56776 | 0.97042 | -0.57096 | 11.2738
23 | 0.12822 | 0.032614 | -0.12811 | -0.032543 | 0.00011174 | 7.111e-05 | 0.19351 | 0.19351 | 0.19351 | 0.98685 | -0.25014 | 0.98591 | -0.26825 | 26.5805
24 | 0.0088458 | 0.002217 | -0.0088453 | -0.0022169 | 4.2203e-07 | 1.8928e-07 | 0.013338 | 0.013338 | 0.013338 | 0.98685 | -0.25014 | 0.9868 | -0.25115 | 3.6643
25 | 0.012674 | 0.0031767 | -0.012673 | -0.0031762 | 9.2885e-07 | 5.0849e-07 | 0.019148 | 0.019148 | 0.019148 | 0.98495 | -0.28682 | 0.98487 | -0.28836 | 5.2603
26 | -0.11591 | -0.029447 | 0.11602 | 0.029513 | 0.00010374 | 6.5936e-05 | 0.17526 | 0.17526 | 0.17526 | 0.98495 | -0.28682 | 0.98591 | -0.26825 | 24.0736
27 | 0.012092 | 0.0030308 | -0.012091 | -0.0030304 | 6.9348e-07 | 3.7303e-07 | 0.018251 | 0.018251 | 0.018251 | 0.98591 | -0.26825 | 0.98585 | -0.26945 | 5.0139

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2799 | 0.071061

## res_load
| p_mw | q_mvar
0 | 0.010211 | 0.0025591
1 | 0.016334 | 0.0040937
2 | 0.019578 | 0.0049068
3 | 0.010314 | 0.0025848
4 | 0.011767 | 0.0029491
5 | 0.01356 | 0.0033984
6 | 0.019268 | 0.0048291
7 | 0.010755 | 0.0026955
8 | 0.015145 | 0.0037957
9 | 0.0054243 | 0.0013595
10 | 0.021228 | 0.0053202
11 | 0.025833 | 0.0064744
12 | 0.02296 | 0.0057542
13 | 0.012073 | 0.0030259
14 | 0.0088453 | 0.0022169
15 | 0.026762 | 0.0067072
16 | 0.012673 | 0.0031762
17 | 0.012091 | 0.0030304

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1