## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-239_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-239_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-239_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-239_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-239_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-239_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1061-239_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1061-239_0_4_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_1061-239_0_4_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_1061-239_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1061-239_0_4_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1061-239_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1061-239_0_4_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1061-239_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1061-239_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1061-239_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1061-239_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1061-239_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1061-239_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1061-239_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1061-239_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1061-239_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1061-239_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1061-239_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1061-239_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1061-239_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1061-239_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1061-239_0_4_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1061-239_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1061-239_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1061-239_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_MV_211_1_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-239_0_4_load_0 | 0 | 0.013373 | 0.0033516 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-239_0_4_load_4 | 4 | 0.013271 | 0.0033259 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-239_0_4_load_8 | 6 | 0.010966 | 0.0027484 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-239_0_4_load_29 | 7 | 0.013975 | 0.0035024 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-239_0_4_load_31 | 8 | 0.016893 | 0.0042339 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-239_0_4_load_6 | 9 | 0.013794 | 0.0034571 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-239_0_4_load_30 | 10 | 0.013045 | 0.0032694 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-239_0_4_load_14 | 11 | 0.024527 | 0.0061471 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-239_0_4_load_10 | 15 | 0.0066466 | 0.0016658 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-239_0_4_load_11 | 16 | 0.015285 | 0.0038309 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-239_0_4_load_18 | 18 | 0.039707 | 0.0099516 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-239_0_4_load_15 | 19 | 0.0066084 | 0.0016562 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-239_0_4_load_20 | 23 | 0.025983 | 0.0065121 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-239_0_4_load_21 | 24 | 0.020388 | 0.0051097 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-239_0_4_load_26 | 27 | 0.01039 | 0.002604 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-239_0_4_load_24 | 29 | 0.050186 | 0.012578 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-239_0_4_load_27 | 30 | 0.023275 | 0.0058332 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-239_0_4_line_0 |  | 0 | 1 | 0.019084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-239_0_4_line_1 |  | 0 | 2 | 0.018821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-239_0_4_line_2 |  | 1 | 3 | 0.035187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-239_0_4_line_3 |  | 1 | 4 | 0.003635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-239_0_4_line_4 |  | 2 | 5 | 0.016539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-239_0_4_line_5 |  | 3 | 8 | 0.003005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-239_0_4_line_6 |  | 5 | 10 | 0.005657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-239_0_4_line_7 |  | 6 | 7 | 0.083705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-239_0_4_line_8 |  | 6 | 8 | 0.034826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-239_0_4_line_9 |  | 6 | 9 | 0.0094887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-239_0_4_line_10 |  | 9 | 13 | 0.0069115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-239_0_4_line_11 |  | 11 | 12 | 0.022488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-239_0_4_line_12 |  | 12 | 17 | 0.025452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1061-239_0_4_line_13 |  | 12 | 16 | 0.022263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-239_0_4_line_14 |  | 13 | 14 | 0.016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-239_0_4_line_15 |  | 13 | 15 | 0.001663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-239_0_4_line_16 |  | 14 | 16 | 0.0029237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-239_0_4_line_17 |  | 17 | 18 | 0.028799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-239_0_4_line_18 |  | 17 | 19 | 0.0071674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-239_0_4_line_19 |  | 19 | 20 | 0.0077329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-239_0_4_line_20 |  | 20 | 21 | 0.039166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-239_0_4_line_21 |  | 21 | 22 | 0.00434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-239_0_4_line_22 |  | 21 | 23 | 0.00928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-239_0_4_line_23 |  | 22 | 24 | 0.010476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-239_0_4_line_24 |  | 22 | 25 | 0.069701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-239_0_4_line_25 |  | 25 | 26 | 0.01527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-239_0_4_line_26 |  | 25 | 27 | 0.004445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-239_0_4_line_27 |  | 25 | 28 | 0.062011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-239_0_4_line_28 |  | 26 | 30 | 0.007392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-239_0_4_line_29 |  | 28 | 29 | 0.011677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-239_0_4_trafo_12 | 0.63 MVA 20/0.4 kV | 31 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2669257.8194 | 1212244.8494 | 2669251.3354 | 1212241.8278 | 2669240.1469 | 1212237.6865
1 | 2669222.4957 | 1212231.1531 | 2669240.1469 | 1212237.6865
2 | 2669257.8194 | 1212244.8494 | 2669259.7843 | 1212245.7617 | 2669270.6289 | 1212252.1026 | 2669281.4676 | 1212259.611 | 2669287.312 | 1212264.0594
3 | 2669257.8194 | 1212244.8494 | 2669258.9839 | 1212241.4052
4 | 2669206.8623 | 1212225.635 | 2669213.3112 | 1212227.7556 | 2669222.4957 | 1212231.1531
5 | 2669287.312 | 1212264.0594 | 2669289.0425 | 1212261.6002
6 | 2669206.8623 | 1212225.635 | 2669208.7401 | 1212220.2979
7 | 2669296.9435 | 1212227.6819 | 2669224.183 | 1212269.0631
8 | 2669296.9435 | 1212227.6819 | 2669289.0425 | 1212261.6002
9 | 2669296.9435 | 1212227.6819 | 2669297.8606 | 1212228.5264 | 2669303.7668 | 1212222.7777
10 | 2669308.7195 | 1212217.957 | 2669303.7668 | 1212222.7777
11 | 2669286.351 | 1212198.9854 | 2669291.811 | 1212199.8938 | 2669295.3088 | 1212196.3989 | 2669300.2323 | 1212192.4759 | 2669304.0886 | 1212188.2069
12 | 2669286.8846 | 1212169.4064 | 2669304.0886 | 1212188.2069
13 | 2669304.0886 | 1212188.2069 | 2669319.123 | 1212204.6264
14 | 2669308.7195 | 1212217.957 | 2669313.5678 | 1212213.3216 | 2669321.0975 | 1212206.7827
15 | 2669308.7195 | 1212217.957 | 2669307.4248 | 1212216.908
16 | 2669321.0975 | 1212206.7827 | 2669319.123 | 1212204.6264
17 | 2669314.1212 | 1212168.9781 | 2669312.6746 | 1212167.2713 | 2669296.3087 | 1212167.2368 | 2669292.2917 | 1212167.0344 | 2669290.3638 | 1212166.8564 | 2669289.2752 | 1212167.6887 | 2669286.8846 | 1212169.4064
18 | 2669286.8846 | 1212169.4064 | 2669282.0449 | 1212164.1198
19 | 2669276.8233 | 1212158.4161 | 2669282.0449 | 1212164.1198
20 | 2669276.8233 | 1212158.4161 | 2669290.1053 | 1212149.2201 | 2669303.7809 | 1212140.1511 | 2669310.3522 | 1212138.9378
21 | 2669310.3522 | 1212138.9378 | 2669314.6316 | 1212138.1425
22 | 2669305.3365 | 1212131.8306 | 2669308.9792 | 1212134.1744 | 2669310.3522 | 1212138.9378
23 | 2669314.6316 | 1212138.1425 | 2669314.7639 | 1212132.6518 | 2669317.4266 | 1212128.4356
24 | 2669314.6316 | 1212138.1425 | 2669316.9159 | 1212137.7244 | 2669327.5199 | 1212138.637 | 2669331.3098 | 1212140.082 | 2669339.4794 | 1212143.2122 | 2669351.9205 | 1212154.0636 | 2669378.7118 | 1212159.912
25 | 2669393.6725 | 1212163.177 | 2669378.7118 | 1212159.912
26 | 2669381.6456 | 1212156.5663 | 2669378.7118 | 1212159.912
27 | 2669359.1325 | 1212187.257 | 2669359.2507 | 1212182.978 | 2669357.167 | 1212164.1864 | 2669351.9205 | 1212154.0636 | 2669378.7118 | 1212159.912
28 | 2669393.6725 | 1212163.177 | 2669391.1602 | 1212170.1299
29 | 2669368.5805 | 1212194.1378 | 2669362.4666 | 1212189.9975 | 2669359.1325 | 1212187.257

## bus_geodata
| x | y | coords
0 | 2669240.1469 | 1212237.6865
1 | 2669257.8194 | 1212244.8494
2 | 2669222.4957 | 1212231.1531
3 | 2669287.312 | 1212264.0594
4 | 2669258.9839 | 1212241.4052
5 | 2669206.8623 | 1212225.635
6 | 2669296.9435 | 1212227.6819
7 | 2669224.183 | 1212269.0631
8 | 2669289.0425 | 1212261.6002
9 | 2669303.7668 | 1212222.7777
10 | 2669208.7401 | 1212220.2979
11 | 2669286.351 | 1212198.9854
12 | 2669304.0886 | 1212188.2069
13 | 2669308.7195 | 1212217.957
14 | 2669321.0975 | 1212206.7827
15 | 2669307.4248 | 1212216.908
16 | 2669319.123 | 1212204.6264
17 | 2669286.8846 | 1212169.4064
18 | 2669314.1212 | 1212168.9781
19 | 2669282.0449 | 1212164.1198
20 | 2669276.8233 | 1212158.4161
21 | 2669310.3522 | 1212138.9378
22 | 2669314.6316 | 1212138.1425
23 | 2669305.3365 | 1212131.8306
24 | 2669317.4266 | 1212128.4356
25 | 2669378.7118 | 1212159.912
26 | 2669393.6725 | 1212163.177
27 | 2669381.6456 | 1212156.5663
28 | 2669359.1325 | 1212187.257
29 | 2669368.5805 | 1212194.1378
30 | 2669391.1602 | 1212170.1299
31 | 2669286.351 | 1212198.9854

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99083 | -0.17644 | 0.013373 | 0.0033516
1 | 0.99129 | -0.16749 | 0 | 0
2 | 0.99061 | -0.1808 | 0 | 0
3 | 0.99257 | -0.14275 | 0 | 0
4 | 0.99125 | -0.16835 | 0.013271 | 0.0033259
5 | 0.99041 | -0.18463 | 0 | 0
6 | 0.99448 | -0.10585 | 0.010966 | 0.0027484
7 | 0.99342 | -0.12649 | 0.013975 | 0.0035024
8 | 0.99268 | -0.14064 | 0.016893 | 0.0042339
9 | 0.99519 | -0.092223 | 0.013794 | 0.0034571
10 | 0.99034 | -0.18594 | 0.013045 | 0.0032694
11 | 0.9995 | -0.0096184 | 0.024527 | 0.0061471
12 | 1 | 0 | -0.3225 | -0.08139
13 | 0.99579 | -0.080636 | 0 | 0
14 | 0.99734 | -0.050831 | 0 | 0
15 | 0.99578 | -0.08083 | 0.0066466 | 0.0016658
16 | 0.99762 | -0.045608 | 0.015285 | 0.0038309
17 | 0.99794 | -0.03924 | 0 | 0
18 | 0.9969 | -0.059275 | 0.039707 | 0.0099516
19 | 0.99704 | -0.056421 | 0.0066084 | 0.0016562
20 | 0.99611 | -0.074094 | 0 | 0
21 | 0.99142 | -0.16411 | 0 | 0
22 | 0.991 | -0.17214 | 0 | 0
23 | 0.9912 | -0.16839 | 0.025983 | 0.0065121
24 | 0.9908 | -0.17593 | 0.020388 | 0.0051097
25 | 0.98561 | -0.27644 | 0 | 0
26 | 0.98528 | -0.28282 | 0 | 0
27 | 0.98557 | -0.27727 | 0.01039 | 0.002604
28 | 0.98274 | -0.33244 | 0 | 0
29 | 0.98219 | -0.34302 | 0.050186 | 0.012578
30 | 0.98512 | -0.28591 | 0.023275 | 0.0058332
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026424 | -0.0066242 | 0.026435 | 0.0066312 | 1.127e-05 | 6.9668e-06 | 0.039684 | 0.039684 | 0.039684 | 0.99083 | -0.17644 | 0.99129 | -0.16749 | 10.9021
1 | 0.013051 | 0.0032727 | -0.013048 | -0.0032712 | 2.7115e-06 | 1.493e-06 | 0.0196 | 0.0196 | 0.0196 | 0.99083 | -0.17644 | 0.99061 | -0.1808 | 5.3847
2 | -0.039706 | -0.0099574 | 0.039753 | 0.009987 | 4.6879e-05 | 2.9548e-05 | 0.059605 | 0.059605 | 0.059605 | 0.99129 | -0.16749 | 0.99257 | -0.14275 | 16.3749
3 | 0.013271 | 0.0033262 | -0.013271 | -0.0033259 | 5.4096e-07 | 2.9936e-07 | 0.019921 | 0.019921 | 0.019921 | 0.99129 | -0.16749 | 0.99125 | -0.16835 | 5.4729
4 | 0.013048 | 0.0032712 | -0.013046 | -0.0032698 | 2.3827e-06 | 1.3121e-06 | 0.0196 | 0.019601 | 0.019601 | 0.99061 | -0.1808 | 0.99041 | -0.18463 | 5.3848
5 | -0.039753 | -0.009987 | 0.039757 | 0.0099895 | 4.0035e-06 | 2.5234e-06 | 0.059605 | 0.059605 | 0.059605 | 0.99257 | -0.14275 | 0.99268 | -0.14064 | 16.3749
6 | 0.013046 | 0.0032698 | -0.013045 | -0.0032694 | 8.1499e-07 | 4.488e-07 | 0.019601 | 0.019601 | 0.019601 | 0.99041 | -0.18463 | 0.99034 | -0.18594 | 5.3848
7 | 0.013988 | 0.0035101 | -0.013975 | -0.0035024 | 1.3753e-05 | 7.7171e-06 | 0.020932 | 0.020932 | 0.020932 | 0.99448 | -0.10585 | 0.99342 | -0.12649 | 5.7506
8 | 0.056745 | 0.014283 | -0.056651 | -0.014223 | 9.4197e-05 | 5.9835e-05 | 0.084927 | 0.084928 | 0.084928 | 0.99448 | -0.10585 | 0.99268 | -0.14064 | 23.3318
9 | -0.081699 | -0.020542 | 0.081753 | 0.020576 | 5.3194e-05 | 3.3921e-05 | 0.12227 | 0.12227 | 0.12227 | 0.99448 | -0.10585 | 0.99519 | -0.092223 | 33.59
10 | -0.095547 | -0.024033 | 0.0956 | 0.024067 | 5.292e-05 | 3.3779e-05 | 0.14289 | 0.14289 | 0.14289 | 0.99519 | -0.092223 | 0.99579 | -0.080636 | 39.2562
11 | -0.024527 | -0.0061471 | 0.024538 | 0.006154 | 1.1244e-05 | 6.9014e-06 | 0.036515 | 0.036515 | 0.036515 | 0.9995 | -0.0096184 | 1 | 0 | 10.0316
12 | 0.17835 | 0.045398 | -0.17801 | -0.045183 | 0.00033673 | 0.00021484 | 0.26563 | 0.26563 | 0.26563 | 1 | 0 | 0.99794 | -0.03924 | 36.4878
13 | 0.11796 | 0.029837 | -0.1177 | -0.029673 | 0.0002575 | 0.00016451 | 0.17562 | 0.17562 | 0.17562 | 1 | 0 | 0.99762 | -0.045608 | 48.2483
14 | -0.10225 | -0.025732 | 0.10239 | 0.025825 | 0.00014587 | 9.3139e-05 | 0.15282 | 0.15282 | 0.15282 | 0.99579 | -0.080636 | 0.99734 | -0.050831 | 41.9848
15 | 0.0066467 | 0.0016658 | -0.0066466 | -0.0016658 | 6.1519e-08 | 1.7738e-08 | 0.0099321 | 0.0099321 | 0.0099321 | 0.99579 | -0.080636 | 0.99578 | -0.08083 | 2.7286
16 | -0.10239 | -0.025825 | 0.10242 | 0.025842 | 2.5607e-05 | 1.635e-05 | 0.15282 | 0.15282 | 0.15282 | 0.99734 | -0.050831 | 0.99762 | -0.045608 | 41.9848
17 | 0.039745 | 0.0099755 | -0.039707 | -0.0099516 | 3.7937e-05 | 2.3904e-05 | 0.059269 | 0.059269 | 0.059269 | 0.99794 | -0.03924 | 0.9969 | -0.059275 | 16.2827
18 | 0.13827 | 0.035208 | -0.13815 | -0.035135 | 0.00011446 | 7.3161e-05 | 0.20636 | 0.20636 | 0.20636 | 0.99794 | -0.03924 | 0.99704 | -0.056421 | 56.693
19 | 0.13154 | 0.033478 | -0.13143 | -0.033407 | 0.00011197 | 7.156e-05 | 0.1965 | 0.1965 | 0.1965 | 0.99704 | -0.056421 | 0.99611 | -0.074094 | 53.9836
20 | 0.13143 | 0.033407 | -0.13086 | -0.033044 | 0.00056711 | 0.00036244 | 0.1965 | 0.1965 | 0.1965 | 0.99611 | -0.074094 | 0.99142 | -0.16411 | 53.9836
21 | 0.10487 | 0.026529 | -0.10483 | -0.026503 | 4.0369e-05 | 2.578e-05 | 0.15749 | 0.15749 | 0.15749 | 0.99142 | -0.16411 | 0.991 | -0.17214 | 43.2674
22 | 0.025989 | 0.0065153 | -0.025983 | -0.0065121 | 5.295e-06 | 3.2692e-06 | 0.039007 | 0.039007 | 0.039007 | 0.99142 | -0.16411 | 0.9912 | -0.16839 | 10.7163
23 | 0.020392 | 0.005112 | -0.020388 | -0.0051097 | 3.6831e-06 | 2.2223e-06 | 0.030619 | 0.030619 | 0.030619 | 0.991 | -0.17214 | 0.9908 | -0.17593 | 8.4119
24 | 0.084442 | 0.021391 | -0.084022 | -0.021123 | 0.00042074 | 0.00026838 | 0.12687 | 0.12687 | 0.12687 | 0.991 | -0.17214 | 0.98561 | -0.27644 | 34.8556
25 | 0.023285 | 0.0058397 | -0.023278 | -0.0058353 | 7.0774e-06 | 4.335e-06 | 0.035156 | 0.035156 | 0.035156 | 0.98561 | -0.27644 | 0.98528 | -0.28282 | 9.6583
26 | 0.01039 | 0.0026042 | -0.01039 | -0.002604 | 4.1017e-07 | 2.0587e-07 | 0.015687 | 0.015687 | 0.015687 | 0.98561 | -0.27644 | 0.98557 | -0.27727 | 4.3095
27 | 0.050346 | 0.012679 | -0.050212 | -0.012594 | 0.00013443 | 8.5246e-05 | 0.076031 | 0.076032 | 0.076032 | 0.98561 | -0.27644 | 0.98274 | -0.33244 | 20.8878
28 | 0.023278 | 0.0058353 | -0.023275 | -0.0058332 | 3.4261e-06 | 2.0986e-06 | 0.035156 | 0.035156 | 0.035156 | 0.98528 | -0.28282 | 0.98512 | -0.28591 | 9.6583
29 | 0.050212 | 0.012594 | -0.050186 | -0.012578 | 2.5314e-05 | 1.6053e-05 | 0.076032 | 0.076032 | 0.076032 | 0.98274 | -0.33244 | 0.98219 | -0.34302 | 20.8878

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3225 | 0.08139

## res_load
| p_mw | q_mvar
0 | 0.013373 | 0.0033516
1 | 0.013271 | 0.0033259
2 | 0.010966 | 0.0027484
3 | 0.013975 | 0.0035024
4 | 0.016893 | 0.0042339
5 | 0.013794 | 0.0034571
6 | 0.013045 | 0.0032694
7 | 0.024527 | 0.0061471
8 | 0.0066466 | 0.0016658
9 | 0.015285 | 0.0038309
10 | 0.039707 | 0.0099516
11 | 0.0066084 | 0.0016562
12 | 0.025983 | 0.0065121
13 | 0.020388 | 0.0051097
14 | 0.01039 | 0.002604
15 | 0.050186 | 0.012578
16 | 0.023275 | 0.0058332

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1