## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-240_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-240_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-240_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-240_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1061-240_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1061-240_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1061-240_0_3_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1061-240_0_3_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1061-240_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1061-240_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1061-240_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1061-240_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1061-240_0_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1061-240_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1061-240_0_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1061-240_0_3_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1061-240_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1061-240_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1061-240_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1061-240_0_3_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1061-240_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1061-240_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1061-240_0_3_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_1061-240_0_3_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1061-240_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1061-240_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1061-240_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_MV_3_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-240_0_3_load_0 | 0 | 0.008234 | 0.0020636 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-240_0_3_load_1 | 1 | 0.0083325 | 0.0020883 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-240_0_3_load_18 | 6 | 0.009173 | 0.002299 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-240_0_3_load_20 | 7 | 0.0043401 | 0.0010877 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-240_0_3_load_21 | 11 | 0.060641 | 0.015198 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-240_0_3_load_31 | 12 | 0.0086455 | 0.0021668 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-240_0_3_load_30 | 14 | 0.014572 | 0.0036521 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-240_0_3_load_29 | 15 | 0.043516 | 0.010906 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-240_0_3_load_24 | 17 | 0.058357 | 0.014626 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-240_0_3_load_28 | 19 | 0.0018674 | 0.000468 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-240_0_3_load_27 | 22 | 0.042019 | 0.010531 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-240_0_3_load_32 | 23 | 0.015965 | 0.0040013 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-240_0_3_load_19 | 24 | 0.012097 | 0.0030318 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-240_0_3_load_22 | 25 | 0.072049 | 0.018057 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-240_0_3_load_23 | 26 | 0.043904 | 0.011003 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-240_0_3_line_0 |  | 0 | 1 | 0.016364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-240_0_3_line_1 |  | 0 | 2 | 0.00046115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-240_0_3_line_2 |  | 2 | 3 | 0.047017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-240_0_3_line_3 |  | 2 | 4 | 0.028193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-240_0_3_line_4 |  | 3 | 5 | 0.050672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-240_0_3_line_5 |  | 3 | 6 | 0.019516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-240_0_3_line_6 |  | 4 | 12 | 0.006273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-240_0_3_line_7 |  | 4 | 13 | 0.023866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-240_0_3_line_8 |  | 4 | 10 | 0.043542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-240_0_3_line_9 |  | 5 | 7 | 0.023411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-240_0_3_line_10 |  | 8 | 9 | 0.026117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1061-240_0_3_line_11 |  | 8 | 10 | 0.06423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-240_0_3_line_12 |  | 8 | 11 | 0.023946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1061-240_0_3_line_13 |  | 9 | 16 | 0.049754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-240_0_3_line_14 |  | 9 | 17 | 0.028805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-240_0_3_line_15 |  | 10 | 15 | 0.0069852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-240_0_3_line_16 |  | 11 | 25 | 0.0023134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-240_0_3_line_17 |  | 13 | 14 | 0.006733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-240_0_3_line_18 |  | 16 | 18 | 0.10751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-240_0_3_line_19 |  | 16 | 19 | 0.031742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-240_0_3_line_20 |  | 17 | 26 | 0.045331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-240_0_3_line_21 |  | 18 | 23 | 0.015129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-240_0_3_line_22 |  | 18 | 21 | 0.034308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-240_0_3_line_23 |  | 20 | 21 | 0.089563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-240_0_3_line_24 |  | 20 | 22 | 0.059003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-240_0_3_line_25 |  | 21 | 24 | 0.02802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-240_0_3_trafo_21 | 0.63 MVA 20/0.4 kV | 27 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2662822.2188 | 1211331.0502 | 2662817.9875 | 1211346.8578
1 | 2662822.2188 | 1211331.0502 | 2662822.3381 | 1211330.6047
2 | 2662803.7484 | 1211306.3165 | 2662816.8543 | 1211309.423 | 2662821.2816 | 1211311.1484 | 2662823.9649 | 1211313.2335 | 2662826.6286 | 1211316.4524 | 2662827.8242 | 1211319.8226 | 2662828.2131 | 1211324.0181 | 2662828.1013 | 1211328.8644 | 2662827.7122 | 1211331.8954 | 2662822.3381 | 1211330.6047
3 | 2662822.3381 | 1211330.6047 | 2662827.7122 | 1211331.8954 | 2662828.1013 | 1211328.8644 | 2662828.808 | 1211328.8607 | 2662832.3718 | 1211328.876 | 2662833.4052 | 1211328.8758 | 2662831.1272 | 1211338.0907 | 2662835.8197 | 1211339.163
4 | 2662767.4132 | 1211286.4999 | 2662766.0628 | 1211291.3442 | 2662774.5216 | 1211293.4122 | 2662797.712 | 1211299.3598 | 2662796.253 | 1211304.4142 | 2662803.7484 | 1211306.3165
5 | 2662803.7484 | 1211306.3165 | 2662802.4976 | 1211311.7955 | 2662801.8392 | 1211320.9164 | 2662800.2419 | 1211325.3912
6 | 2662835.8197 | 1211339.163 | 2662841.9525 | 1211340.5618
7 | 2662835.8197 | 1211339.163 | 2662834.9175 | 1211341.8552 | 2662829.8847 | 1211362.2702
8 | 2662835.8197 | 1211339.163 | 2662837.7735 | 1211333.3134 | 2662838.9383 | 1211330.9464 | 2662841.4075 | 1211325.936 | 2662843.665 | 1211323.0024 | 2662846.1305 | 1211321.2273 | 2662848.9016 | 1211320.0335 | 2662852.6735 | 1211319.762 | 2662856.2636 | 1211320.1667 | 2662856.5096 | 1211319.1798 | 2662857.4211 | 1211315.6095 | 2662857.6748 | 1211314.6115 | 2662857.992 | 1211313.3474 | 2662859.0308 | 1211309.2447 | 2662859.213 | 1211308.5351
9 | 2662767.4132 | 1211286.4999 | 2662767.7922 | 1211285.1475 | 2662767.7362 | 1211283.9684 | 2662766.8603 | 1211282.714 | 2662761.9568 | 1211280.7501 | 2662761.7387 | 1211277.6459 | 2662764.4184 | 1211267.0787
10 | 2662832.1929 | 1211258.5756 | 2662835.568 | 1211246.2036 | 2662836.3183 | 1211246.4005 | 2662839.4254 | 1211247.2115 | 2662840.7632 | 1211242.1225 | 2662843.8778 | 1211242.9447 | 2662844.6735 | 1211243.1532
11 | 2662832.1929 | 1211258.5756 | 2662836.7103 | 1211259.6794 | 2662836.3252 | 1211261.6099 | 2662836.5803 | 1211266.2487 | 2662838.3792 | 1211270.7704 | 2662842.7059 | 1211281.3224 | 2662843.4477 | 1211287.3673 | 2662843.2577 | 1211290.2559 | 2662843.986 | 1211290.3748 | 2662848.0594 | 1211291.0625 | 2662848.7269 | 1211291.1807 | 2662848.5569 | 1211297.216 | 2662849.2233 | 1211299.6022 | 2662851.0021 | 1211302.4227 | 2662853.3639 | 1211304.7267 | 2662856.5295 | 1211307.1949 | 2662859.213 | 1211308.5351
12 | 2662832.1929 | 1211258.5756 | 2662808.924 | 1211252.92
13 | 2662844.6735 | 1211243.1532 | 2662845.8176 | 1211238.429 | 2662841.9599 | 1211237.4545 | 2662838.8827 | 1211236.6883 | 2662838.14 | 1211236.5025 | 2662845.9176 | 1211205.132 | 2662846.9231 | 1211200.5842
14 | 2662844.6735 | 1211243.1532 | 2662872.5361 | 1211250.4618
15 | 2662859.213 | 1211308.5351 | 2662860.8609 | 1211309.3641 | 2662865.8315 | 1211310.6749
16 | 2662806.6761 | 1211252.3736 | 2662808.924 | 1211252.92
17 | 2662829.8847 | 1211362.2702 | 2662836.4566 | 1211363.8181
18 | 2662762.7594 | 1211174.8717 | 2662765.025 | 1211166.1124 | 2662804.7826 | 1211175.6253 | 2662840.3659 | 1211184.6276 | 2662845.1583 | 1211186.3236 | 2662847.3825 | 1211187.9925 | 2662848.4286 | 1211190.405 | 2662848.6704 | 1211192.6978 | 2662846.9231 | 1211200.5842
19 | 2662846.9231 | 1211200.5842 | 2662840.3758 | 1211198.8364 | 2662837.769 | 1211208.2369 | 2662823.0026 | 1211204.591
20 | 2662916.3835 | 1211261.9635 | 2662872.5361 | 1211250.4618
21 | 2662762.7594 | 1211174.8717 | 2662758.9729 | 1211189.5186
22 | 2662729.5228 | 1211165.9946 | 2662762.7594 | 1211174.8717
23 | 2662658.2887 | 1211134.8161 | 2662732.5289 | 1211153.2851 | 2662729.5228 | 1211165.9946
24 | 2662658.2887 | 1211134.8161 | 2662656.3891 | 1211142.7566 | 2662650.1098 | 1211163.9592 | 2662644.6581 | 1211188.1278 | 2662643.6624 | 1211191.9495
25 | 2662729.5228 | 1211165.9946 | 2662727.4914 | 1211167.6632 | 2662721.3729 | 1211192.3057

## bus_geodata
| x | y | coords
0 | 2662822.2188 | 1211331.0502
1 | 2662817.9875 | 1211346.8578
2 | 2662822.3381 | 1211330.6047
3 | 2662803.7484 | 1211306.3165
4 | 2662835.8197 | 1211339.163
5 | 2662767.4132 | 1211286.4999
6 | 2662800.2419 | 1211325.3912
7 | 2662764.4184 | 1211267.0787
8 | 2662832.1929 | 1211258.5756
9 | 2662844.6735 | 1211243.1532
10 | 2662859.213 | 1211308.5351
11 | 2662808.924 | 1211252.92
12 | 2662841.9525 | 1211340.5618
13 | 2662829.8847 | 1211362.2702
14 | 2662836.4566 | 1211363.8181
15 | 2662865.8315 | 1211310.6749
16 | 2662846.9231 | 1211200.5842
17 | 2662872.5361 | 1211250.4618
18 | 2662762.7594 | 1211174.8717
19 | 2662823.0026 | 1211204.591
20 | 2662658.2887 | 1211134.8161
21 | 2662729.5228 | 1211165.9946
22 | 2662643.6624 | 1211191.9495
23 | 2662758.9729 | 1211189.5186
24 | 2662721.3729 | 1211192.3057
25 | 2662806.6761 | 1211252.3736
26 | 2662916.3835 | 1211261.9635
27 | 2662792.3162 | 1211248.8833

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9884 | -0.22291 | 0.008234 | 0.0020636
1 | 0.98828 | -0.22535 | 0.0083325 | 0.0020883
2 | 0.98841 | -0.22278 | 0 | 0
3 | 0.98783 | -0.23412 | 0 | 0
4 | 0.98919 | -0.20766 | 0 | 0
5 | 0.98763 | -0.23805 | 0 | 0
6 | 0.98766 | -0.23732 | 0.009173 | 0.002299
7 | 0.98753 | -0.23987 | 0.0043401 | 0.0010877
8 | 0.99702 | -0.056734 | 0 | 0
9 | 0.99493 | -0.096709 | 0 | 0
10 | 0.99132 | -0.1664 | 0 | 0
11 | 1 | 0 | -0.34781 | -0.087949
12 | 0.98914 | -0.20862 | 0.0086455 | 0.0021668
13 | 0.98887 | -0.21385 | 0 | 0
14 | 0.98878 | -0.2156 | 0.014572 | 0.0036521
15 | 0.99104 | -0.1718 | 0.043516 | 0.010906
16 | 0.99161 | -0.15996 | 0 | 0
17 | 0.99223 | -0.14872 | 0.058357 | 0.014626
18 | 0.98463 | -0.29448 | 0 | 0
19 | 0.99156 | -0.16101 | 0.0018674 | 0.000468
20 | 0.97942 | -0.39606 | 0 | 0
21 | 0.98291 | -0.32792 | 0 | 0
22 | 0.97712 | -0.44121 | 0.042019 | 0.010531
23 | 0.98441 | -0.29882 | 0.015965 | 0.0040013
24 | 0.9826 | -0.33403 | 0.012097 | 0.0030318
25 | 0.99985 | -0.0029055 | 0.072049 | 0.018057
26 | 0.99041 | -0.18402 | 0.043904 | 0.011003
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0083335 | 0.0020887 | -0.0083325 | -0.0020883 | 9.659e-07 | 4.0846e-07 | 0.012546 | 0.012546 | 0.012546 | 0.9884 | -0.22291 | 0.98828 | -0.22535 | 3.4467
1 | -0.016568 | -0.0041524 | 0.016568 | 0.0041524 | 1.0758e-07 | 6.2942e-08 | 0.024942 | 0.024942 | 0.024942 | 0.9884 | -0.22291 | 0.98841 | -0.22278 | 6.8522
2 | 0.013523 | 0.0033912 | -0.013516 | -0.0033871 | 7.3081e-06 | 4.0749e-06 | 0.020359 | 0.020359 | 0.020359 | 0.98841 | -0.22278 | 0.98783 | -0.23412 | 5.5932
3 | -0.030091 | -0.0075437 | 0.030112 | 0.0075572 | 2.1696e-05 | 1.3524e-05 | 0.045301 | 0.045301 | 0.045301 | 0.98841 | -0.22278 | 0.98919 | -0.20766 | 12.4453
4 | 0.0043413 | 0.0010875 | -0.0043405 | -0.0010877 | 8.1259e-07 | -1.285e-07 | 0.0065393 | 0.0065395 | 0.0065395 | 0.98783 | -0.23412 | 0.98763 | -0.23805 | 1.7966
5 | 0.0091744 | 0.0022996 | -0.009173 | -0.002299 | 1.3978e-06 | 6.4477e-07 | 0.01382 | 0.01382 | 0.01382 | 0.98783 | -0.23412 | 0.98766 | -0.23732 | 3.7967
6 | 0.0086459 | 0.0021669 | -0.0086455 | -0.0021668 | 3.9791e-07 | 1.7414e-07 | 0.013006 | 0.013006 | 0.013006 | 0.98919 | -0.20766 | 0.98914 | -0.20862 | 3.573
7 | 0.014577 | 0.0036552 | -0.014573 | -0.0036528 | 4.3038e-06 | 2.4482e-06 | 0.021929 | 0.021929 | 0.021929 | 0.98919 | -0.20766 | 0.98887 | -0.21385 | 6.0245
8 | -0.053336 | -0.013379 | 0.053441 | 0.013446 | 0.00010512 | 6.6716e-05 | 0.080236 | 0.080236 | 0.080236 | 0.98919 | -0.20766 | 0.99132 | -0.1664 | 22.0428
9 | 0.0043405 | 0.0010877 | -0.0043401 | -0.0010877 | 3.7544e-07 | -5.9265e-08 | 0.0065395 | 0.0065396 | 0.0065396 | 0.98763 | -0.23805 | 0.98753 | -0.23987 | 1.7966
10 | 0.17588 | 0.044722 | -0.17554 | -0.044506 | 0.00033799 | 0.00021563 | 0.26272 | 0.26272 | 0.26272 | 0.99702 | -0.056734 | 0.99493 | -0.096709 | 36.0878
11 | 0.097478 | 0.024685 | -0.096968 | -0.024359 | 0.00051043 | 0.00032584 | 0.14557 | 0.14557 | 0.14557 | 0.99702 | -0.056734 | 0.99132 | -0.1664 | 39.9926
12 | -0.27336 | -0.069407 | 0.2741 | 0.069885 | 0.00074848 | 0.0004784 | 0.40829 | 0.40829 | 0.40829 | 0.99702 | -0.056734 | 1 | 0 | 56.084
13 | 0.07295 | 0.018668 | -0.072728 | -0.018526 | 0.00022266 | 0.00014186 | 0.10924 | 0.10924 | 0.10924 | 0.99493 | -0.096709 | 0.99161 | -0.15996 | 30.0115
14 | 0.10259 | 0.025838 | -0.10233 | -0.025676 | 0.00025445 | 0.00016247 | 0.15348 | 0.15348 | 0.15348 | 0.99493 | -0.096709 | 0.99223 | -0.14872 | 42.1643
15 | 0.043527 | 0.010913 | -0.043516 | -0.010906 | 1.1182e-05 | 7.0667e-06 | 0.065338 | 0.065338 | 0.065338 | 0.99132 | -0.1664 | 0.99104 | -0.1718 | 17.9499
16 | 0.072059 | 0.018064 | -0.072049 | -0.018057 | 9.9743e-06 | 6.3532e-06 | 0.10723 | 0.10723 | 0.10723 | 1 | 0 | 0.99985 | -0.0029055 | 29.458
17 | 0.014573 | 0.0036528 | -0.014572 | -0.0036521 | 1.2142e-06 | 6.9071e-07 | 0.021929 | 0.021929 | 0.021929 | 0.98887 | -0.21385 | 0.98878 | -0.2156 | 6.0245
18 | 0.07086 | 0.018058 | -0.070403 | -0.017767 | 0.00045676 | 0.00029095 | 0.10644 | 0.10644 | 0.10644 | 0.99161 | -0.15996 | 0.98463 | -0.29448 | 29.2418
19 | 0.0018675 | 0.00046766 | -0.0018674 | -0.000468 | 9.3471e-08 | -3.4962e-07 | 0.0028022 | 0.0028023 | 0.0028023 | 0.99161 | -0.15996 | 0.99156 | -0.16101 | 0.76987
20 | 0.043978 | 0.01105 | -0.043904 | -0.011003 | 7.3964e-05 | 4.6753e-05 | 0.065963 | 0.065963 | 0.065963 | 0.99223 | -0.14872 | 0.99041 | -0.18402 | 18.1216
21 | 0.015969 | 0.0040032 | -0.015965 | -0.0040013 | 3.3042e-06 | 1.9223e-06 | 0.024133 | 0.024133 | 0.024133 | 0.98463 | -0.29448 | 0.98441 | -0.29882 | 6.6299
22 | 0.054435 | 0.013764 | -0.054348 | -0.013709 | 8.7158e-05 | 5.5345e-05 | 0.082307 | 0.082308 | 0.082308 | 0.98463 | -0.29448 | 0.98291 | -0.32792 | 22.612
23 | -0.042109 | -0.010588 | 0.042247 | 0.010675 | 0.00013752 | 8.6881e-05 | 0.063989 | 0.063988 | 0.063989 | 0.97942 | -0.39606 | 0.98291 | -0.32792 | 17.5793
24 | 0.042109 | 0.010588 | -0.042019 | -0.010531 | 9.0596e-05 | 5.7241e-05 | 0.063989 | 0.063989 | 0.063989 | 0.97942 | -0.39606 | 0.97712 | -0.44121 | 17.5794
25 | 0.012101 | 0.0030337 | -0.012097 | -0.0030318 | 3.5263e-06 | 1.9018e-06 | 0.018319 | 0.01832 | 0.01832 | 0.98291 | -0.32792 | 0.9826 | -0.33403 | 5.0328

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40845 | 0.10315

## res_load
| p_mw | q_mvar
0 | 0.008234 | 0.0020636
1 | 0.0083325 | 0.0020883
2 | 0.009173 | 0.002299
3 | 0.0043401 | 0.0010877
4 | 0.060641 | 0.015198
5 | 0.0086455 | 0.0021668
6 | 0.014572 | 0.0036521
7 | 0.043516 | 0.010906
8 | 0.058357 | 0.014626
9 | 0.0018674 | 0.000468
10 | 0.042019 | 0.010531
11 | 0.015965 | 0.0040013
12 | 0.012097 | 0.0030318
13 | 0.072049 | 0.018057
14 | 0.043904 | 0.011003

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1