## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-241_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-241_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-241_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-241_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1061-241_0_5_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1061-241_0_5_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1061-241_0_5_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_1061-241_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1061-241_0_5_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1061-241_0_5_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_1061-241_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1061-241_0_5_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1061-241_0_5_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_1061-241_0_5_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1061-241_0_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_1061-241_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1061-241_0_5_node_5 | 0.4 | n |  | TRUE
17 | bus_LV_1061-241_0_5_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1061-241_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1061-241_0_5_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1061-241_0_5_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_1061-241_0_5_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1061-241_0_5_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1061-241_0_5_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1061-241_0_5_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_1061-241_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1061-241_0_5_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_1061-241_0_5_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_1061-241_0_5_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1061-241_0_5_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_1061-241_0_5_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_1061-241_0_5_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_1061-241_0_5_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_1061-241_0_5_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_1061-241_0_5_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1061-241_0_5_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_1061-241_0_5_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_1061-241_0_5_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_1061-241_0_5_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_1061-241_0_5_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1061-241_0_5_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1061-241_0_5_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1061-241_0_5_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1061-241_0_5_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1061-241_0_5_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_1061-241_0_5_node_48 | 0.4 | n |  | TRUE
46 | bus_MV_221_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-241_0_5_load_0 | 0 | 0.048596 | 0.012179 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-241_0_5_load_1 | 1 | 0.055032 | 0.013792 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-241_0_5_load_2 | 2 | 0.0071762 | 0.0017985 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-241_0_5_load_45 | 6 | 0.0027616 | 0.00069212 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-241_0_5_load_50 | 9 | 0.023815 | 0.0059687 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-241_0_5_load_23 | 12 | 0.011385 | 0.0028532 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-241_0_5_load_18 | 13 | 0.012677 | 0.0031772 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-241_0_5_load_5 | 16 | 0.046001 | 0.011529 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-241_0_5_load_17 | 17 | 0.00479 | 0.0012005 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-241_0_5_load_29 | 20 | 0.012243 | 0.0030684 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-241_0_5_load_30 | 21 | 0.011997 | 0.0030069 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-241_0_5_load_22 | 22 | 0.014048 | 0.0035208 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-241_0_5_load_52 | 24 | 0.011814 | 0.002961 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-241_0_5_load_33 | 26 | 0.015142 | 0.003795 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-241_0_5_load_26 | 28 | 0.012517 | 0.0031369 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-241_0_5_load_35 | 30 | 0.0096242 | 0.0024121 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-241_0_5_load_43 | 32 | 0.02162 | 0.0054186 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-241_0_5_load_44 | 33 | 0.012538 | 0.0031424 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-241_0_5_load_28 | 34 | 0.013619 | 0.0034132 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-241_0_5_load_51 | 36 | 0.011033 | 0.0027652 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-241_0_5_load_47 | 37 | 0.009621 | 0.0024113 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-241_0_5_load_46 | 38 | 0.013177 | 0.0033025 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-241_0_5_load_31 | 39 | 0.011907 | 0.0029843 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-241_0_5_load_32 | 40 | 0.012604 | 0.0031589 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-241_0_5_load_38 | 41 | 0.013177 | 0.0033025 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-241_0_5_load_39 | 42 | 0.0096233 | 0.0024118 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-241_0_5_load_41 | 43 | 0.0096243 | 0.0024121 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-241_0_5_load_49 | 44 | 0.01318 | 0.0033033 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-241_0_5_load_48 | 45 | 0.009622 | 0.0024115 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-241_0_5_line_0 |  | 0 | 1 | 0.024708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-241_0_5_line_1 |  | 0 | 2 | 0.043742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-241_0_5_line_2 |  | 2 | 3 | 0.018659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-241_0_5_line_3 |  | 3 | 4 | 0.035112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-241_0_5_line_4 |  | 4 | 21 | 0.036129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-241_0_5_line_5 |  | 5 | 6 | 0.0092981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-241_0_5_line_6 |  | 5 | 7 | 0.069087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-241_0_5_line_7 |  | 6 | 10 | 0.068687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-241_0_5_line_8 |  | 7 | 15 | 0.070514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-241_0_5_line_9 |  | 7 | 16 | 0.081861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-241_0_5_line_10 |  | 8 | 9 | 0.003881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-241_0_5_line_11 |  | 8 | 10 | 0.046702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-241_0_5_line_12 |  | 10 | 14 | 0.084258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-241_0_5_line_13 |  | 11 | 12 | 0.028881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1061-241_0_5_line_14 |  | 11 | 13 | 0.023223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1061-241_0_5_line_15 |  | 12 | 27 | 0.007652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1061-241_0_5_line_16 |  | 13 | 35 | 0.016648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1061-241_0_5_line_17 |  | 14 | 22 | 0.026357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1061-241_0_5_line_18 |  | 15 | 17 | 0.031781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-241_0_5_line_19 |  | 18 | 19 | 0.00725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-241_0_5_line_20 |  | 18 | 20 | 0.020338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-241_0_5_line_21 |  | 19 | 34 | 0.012089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1061-241_0_5_line_22 |  | 19 | 28 | 0.030198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-241_0_5_line_23 |  | 20 | 21 | 0.017926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-241_0_5_line_24 |  | 22 | 35 | 0.012974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1061-241_0_5_line_25 |  | 23 | 24 | 0.004791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-241_0_5_line_26 |  | 23 | 25 | 0.013733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-241_0_5_line_27 |  | 25 | 36 | 0.004742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-241_0_5_line_28 |  | 25 | 35 | 0.016101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-241_0_5_line_29 |  | 26 | 27 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-241_0_5_line_30 |  | 27 | 30 | 0.028742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1061-241_0_5_line_31 |  | 29 | 30 | 0.013691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1061-241_0_5_line_32 |  | 29 | 31 | 0.008272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1061-241_0_5_line_33 |  | 31 | 33 | 0.0015871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1061-241_0_5_line_34 |  | 31 | 42 | 0.02644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1061-241_0_5_line_35 |  | 32 | 33 | 0.019716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1061-241_0_5_line_36 |  | 34 | 39 | 0.0030388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1061-241_0_5_line_37 |  | 37 | 38 | 0.0075564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1061-241_0_5_line_38 |  | 38 | 45 | 0.013823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1061-241_0_5_line_39 |  | 39 | 40 | 0.040007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1061-241_0_5_line_40 |  | 40 | 41 | 0.00062638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1061-241_0_5_line_41 |  | 41 | 42 | 0.016593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1061-241_0_5_line_42 |  | 42 | 43 | 0.016403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1061-241_0_5_line_43 |  | 43 | 44 | 0.011157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1061-241_0_5_line_44 |  | 44 | 45 | 0.0051916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-241_0_5_trafo_47 | 0.63 MVA 20/0.4 kV | 46 | 37 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2663368.0737 | 1212543.3398 | 2663348.6868 | 1212543.3119 | 2663343.3659 | 1212543.3141
1 | 2663368.0737 | 1212543.3398 | 2663397.0743 | 1212543.3815 | 2663397.4278 | 1212558.1189
2 | 2663400.6763 | 1212576.1732 | 2663397.6902 | 1212569.0593 | 2663397.4278 | 1212558.1189
3 | 2663400.6763 | 1212576.1732 | 2663400.2771 | 1212605.8539 | 2663400.4018 | 1212611.2807
4 | 2663400.4018 | 1212611.2807 | 2663392.5515 | 1212611.4863 | 2663386.7125 | 1212613.3143 | 2663383.9195 | 1212616.62 | 2663383.4523 | 1212634.4438
5 | 2663248.686 | 1212543.6068 | 2663248.541 | 1212552.9037
6 | 2663248.686 | 1212543.6068 | 2663249.9124 | 1212474.544
7 | 2663197.7223 | 1212570.839 | 2663248.2581 | 1212571.0524 | 2663248.541 | 1212552.9037
8 | 2663186.6141 | 1212484.8797 | 2663187.4343 | 1212484.9106 | 2663191.657 | 1212485.0554 | 2663192.6215 | 1212485.0879 | 2663193.4873 | 1212485.1193 | 2663197.6567 | 1212485.2747 | 2663198.682 | 1212485.3078 | 2663198.6917 | 1212481.5278 | 2663199.9639 | 1212478.3393 | 2663202.4134 | 1212475.8971 | 2663203.6492 | 1212475.421 | 2663206.0981 | 1212474.4686 | 2663249.9124 | 1212474.544
9 | 2663249.9124 | 1212474.544 | 2663331.7729 | 1212474.5906
10 | 2663222.1929 | 1212588.8204 | 2663222.1809 | 1212584.9401
11 | 2663197.7223 | 1212570.839 | 2663197.745 | 1212576.5872 | 2663196.3768 | 1212578.0847 | 2663195.6732 | 1212580.6678 | 2663195.3445 | 1212589.4586 | 2663212.1911 | 1212584.8675 | 2663222.1809 | 1212584.9401
12 | 2663197.7223 | 1212570.839 | 2663197.745 | 1212576.5872 | 2663196.3768 | 1212578.0847 | 2663195.6732 | 1212580.6678 | 2663195.3445 | 1212589.4586 | 2663195.0225 | 1212642.0652 | 2663195.8487 | 1212654.4371
13 | 2663264.5865 | 1212665.4279 | 2663264.5443 | 1212694.3088
14 | 2663264.5865 | 1212665.4279 | 2663264.6061 | 1212654.9884 | 2663251.8248 | 1212654.7514
15 | 2663264.5332 | 1212701.9609 | 2663264.5443 | 1212694.3088
16 | 2663235.1799 | 1212654.4427 | 2663251.8248 | 1212654.7514
17 | 2663195.8487 | 1212654.4371 | 2663222.2061 | 1212654.4409
18 | 2663186.6141 | 1212484.8797 | 2663186.2595 | 1212500.4188 | 2663186.4221 | 1212516.6558
19 | 2663382.4497 | 1212672.6944 | 2663382.3423 | 1212679.9421
20 | 2663382.4497 | 1212672.6944 | 2663382.9826 | 1212652.3633
21 | 2663382.3423 | 1212679.9421 | 2663370.2553 | 1212679.7256
22 | 2663382.3423 | 1212679.9421 | 2663381.9248 | 1212708.4997 | 2663381.9235 | 1212710.1373
23 | 2663382.9826 | 1212652.3633 | 2663383.4523 | 1212634.4438
24 | 2663235.1799 | 1212654.4427 | 2663222.2061 | 1212654.4409
25 | 2663230.2849 | 1212684.0312 | 2663235.0839 | 1212684.2711
26 | 2663235.1231 | 1212670.5409 | 2663235.0839 | 1212684.2711
27 | 2663235.1231 | 1212670.5409 | 2663230.387 | 1212670.1127
28 | 2663235.1799 | 1212654.4427 | 2663235.1231 | 1212670.5409
29 | 2663264.5332 | 1212701.9609 | 2663264.5158 | 1212714.0187
30 | 2663264.5332 | 1212701.9609 | 2663293.2747 | 1212701.8517
31 | 2663306.9655 | 1212701.7997 | 2663293.2747 | 1212701.8517
32 | 2663306.9655 | 1212701.7997 | 2663315.2621 | 1212701.7655
33 | 2663315.2621 | 1212701.7655 | 2663315.1826 | 1212703.3506
34 | 2663310.8695 | 1212676.1365 | 2663315.8021 | 1212690.9757 | 2663315.2621 | 1212701.7655
35 | 2663312.917 | 1212722.9309 | 2663315.0693 | 1212705.6103 | 2663315.1826 | 1212703.3506
36 | 2663367.217 | 1212679.6712 | 2663370.2553 | 1212679.7256
37 | 2663313.6834 | 1212630.0714 | 2663309.6869 | 1212623.6584
38 | 2663313.6834 | 1212630.0714 | 2663313.6834 | 1212630.0714 | 2663310.8443 | 1212637.7238 | 2663310.848 | 1212643.3848
39 | 2663367.217 | 1212679.6712 | 2663342.6844 | 1212679.2317 | 2663337.6272 | 1212676.1316 | 2663328.0888 | 1212676.1334
40 | 2663327.4624 | 1212676.1335 | 2663328.0888 | 1212676.1334
41 | 2663310.8695 | 1212676.1365 | 2663327.4624 | 1212676.1335
42 | 2663310.8695 | 1212676.1365 | 2663310.8587 | 1212659.7333
43 | 2663310.8514 | 1212648.5764 | 2663310.8587 | 1212659.7333
44 | 2663310.8514 | 1212648.5764 | 2663310.848 | 1212643.3848

## bus_geodata
| x | y | coords
0 | 2663368.0737 | 1212543.3398
1 | 2663343.3659 | 1212543.3141
2 | 2663397.4278 | 1212558.1189
3 | 2663400.6763 | 1212576.1732
4 | 2663400.4018 | 1212611.2807
5 | 2663248.686 | 1212543.6068
6 | 2663248.541 | 1212552.9037
7 | 2663249.9124 | 1212474.544
8 | 2663222.1809 | 1212584.9401
9 | 2663222.1929 | 1212588.8204
10 | 2663197.7223 | 1212570.839
11 | 2663264.5865 | 1212665.4279
12 | 2663264.5443 | 1212694.3088
13 | 2663251.8248 | 1212654.7514
14 | 2663195.8487 | 1212654.4371
15 | 2663186.6141 | 1212484.8797
16 | 2663331.7729 | 1212474.5906
17 | 2663186.4221 | 1212516.6558
18 | 2663382.4497 | 1212672.6944
19 | 2663382.3423 | 1212679.9421
20 | 2663382.9826 | 1212652.3633
21 | 2663383.4523 | 1212634.4438
22 | 2663222.2061 | 1212654.4409
23 | 2663235.0839 | 1212684.2711
24 | 2663230.2849 | 1212684.0312
25 | 2663235.1231 | 1212670.5409
26 | 2663264.5158 | 1212714.0187
27 | 2663264.5332 | 1212701.9609
28 | 2663381.9235 | 1212710.1373
29 | 2663306.9655 | 1212701.7997
30 | 2663293.2747 | 1212701.8517
31 | 2663315.2621 | 1212701.7655
32 | 2663312.917 | 1212722.9309
33 | 2663315.1826 | 1212703.3506
34 | 2663370.2553 | 1212679.7256
35 | 2663235.1799 | 1212654.4427
36 | 2663230.387 | 1212670.1127
37 | 2663309.6869 | 1212623.6584
38 | 2663313.6834 | 1212630.0714
39 | 2663367.217 | 1212679.6712
40 | 2663328.0888 | 1212676.1334
41 | 2663327.4624 | 1212676.1335
42 | 2663310.8695 | 1212676.1365
43 | 2663310.8587 | 1212659.7333
44 | 2663310.8514 | 1212648.5764
45 | 2663310.848 | 1212643.3848
46 | 2663309.8709 | 1212605.6159

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9723 | -0.53359 | 0.048596 | 0.012179
1 | 0.97103 | -0.55869 | 0.055032 | 0.013792
2 | 0.97653 | -0.45038 | 0.0071762 | 0.0017985
3 | 0.97846 | -0.41266 | 0 | 0
4 | 0.98209 | -0.34209 | 0 | 0
5 | 0.97826 | -0.41744 | 0 | 0
6 | 0.9787 | -0.40884 | 0.0027616 | 0.00069212
7 | 0.97499 | -0.48157 | 0 | 0
8 | 0.98111 | -0.36225 | 0 | 0
9 | 0.98102 | -0.36393 | 0.023815 | 0.0059687
10 | 0.98214 | -0.34213 | 0 | 0
11 | 0.99055 | -0.18001 | 0 | 0
12 | 0.9914 | -0.16374 | 0.011385 | 0.0028532
13 | 0.98987 | -0.19311 | 0.012677 | 0.0031772
14 | 0.98821 | -0.22504 | 0 | 0
15 | 0.97467 | -0.48777 | 0 | 0
16 | 0.97147 | -0.55087 | 0.046001 | 0.011529
17 | 0.97453 | -0.49057 | 0.00479 | 0.0012005
18 | 0.99044 | -0.1817 | 0 | 0
19 | 0.99135 | -0.16432 | 0 | 0
20 | 0.98788 | -0.23062 | 0.012243 | 0.0030684
21 | 0.98583 | -0.27002 | 0.011997 | 0.0030069
22 | 0.98916 | -0.20686 | 0.014048 | 0.0035208
23 | 0.98895 | -0.21102 | 0 | 0
24 | 0.98889 | -0.21203 | 0.011814 | 0.002961
25 | 0.98909 | -0.20813 | 0 | 0
26 | 0.99148 | -0.16229 | 0.015142 | 0.003795
27 | 0.99165 | -0.15905 | 0 | 0
28 | 0.99101 | -0.17102 | 0.012517 | 0.0031369
29 | 0.99318 | -0.12965 | 0 | 0
30 | 0.99267 | -0.13952 | 0.0096242 | 0.0024121
31 | 0.99349 | -0.12369 | 0 | 0
32 | 0.99306 | -0.13218 | 0.02162 | 0.0054186
33 | 0.99344 | -0.12465 | 0.012538 | 0.0031424
34 | 0.99218 | -0.14851 | 0.013619 | 0.0034132
35 | 0.98943 | -0.20158 | 0 | 0
36 | 0.98905 | -0.20906 | 0.011033 | 0.0027652
37 | 1 | 0 | -0.4596 | -0.11732
38 | 0.99921 | -0.014875 | 0.013177 | 0.0033025
39 | 0.9923 | -0.14634 | 0.011907 | 0.0029843
40 | 0.9939 | -0.11575 | 0.012604 | 0.0031589
41 | 0.99393 | -0.11523 | 0.013177 | 0.0033025
42 | 0.9947 | -0.10069 | 0.0096233 | 0.0024118
43 | 0.99623 | -0.07142 | 0.0096243 | 0.0024121
44 | 0.9973 | -0.051092 | 0.01318 | 0.0033033
45 | 0.99782 | -0.041349 | 0.009622 | 0.0024115
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.055098 | 0.013834 | -0.055032 | -0.013792 | 6.5896e-05 | 4.1867e-05 | 0.084332 | 0.084332 | 0.084332 | 0.9723 | -0.53359 | 0.97103 | -0.55869 | 23.1683
1 | -0.10369 | -0.026014 | 0.10411 | 0.026277 | 0.00041315 | 0.00026387 | 0.1587 | 0.1587 | 0.1587 | 0.9723 | -0.53359 | 0.97653 | -0.45038 | 43.6
2 | -0.11128 | -0.028076 | 0.11148 | 0.028205 | 0.00020136 | 0.00012863 | 0.16964 | 0.16964 | 0.16964 | 0.97653 | -0.45038 | 0.97846 | -0.41266 | 46.6041
3 | -0.11148 | -0.028205 | 0.11186 | 0.028447 | 0.00037891 | 0.00024206 | 0.16964 | 0.16964 | 0.16964 | 0.97846 | -0.41266 | 0.98209 | -0.34209 | 46.6041
4 | -0.11186 | -0.028447 | 0.11225 | 0.028696 | 0.00038989 | 0.00024907 | 0.16964 | 0.16964 | 0.16964 | 0.98209 | -0.34209 | 0.98583 | -0.27002 | 46.604
5 | -0.051103 | -0.012926 | 0.051124 | 0.012939 | 2.1091e-05 | 1.3381e-05 | 0.077774 | 0.077774 | 0.077774 | 0.97826 | -0.41744 | 0.9787 | -0.40884 | 21.3664
6 | 0.051103 | 0.012926 | -0.050946 | -0.012826 | 0.00015671 | 9.9429e-05 | 0.077774 | 0.077774 | 0.077774 | 0.97826 | -0.41744 | 0.97499 | -0.48157 | 21.3665
7 | -0.053885 | -0.013631 | 0.054058 | 0.013741 | 0.00017308 | 0.0001099 | 0.081972 | 0.081972 | 0.081972 | 0.9787 | -0.40884 | 0.98214 | -0.34213 | 22.5199
8 | 0.004792 | 0.0012005 | -0.0047906 | -0.0012005 | 1.4144e-06 | 2.608e-08 | 0.0073134 | 0.0073137 | 0.0073137 | 0.97499 | -0.48157 | 0.97467 | -0.48777 | 2.0093
9 | 0.046154 | 0.011626 | -0.046001 | -0.011529 | 0.00015241 | 9.6522e-05 | 0.070461 | 0.070461 | 0.070461 | 0.97499 | -0.48157 | 0.97147 | -0.55087 | 19.3574
10 | 0.023817 | 0.0059699 | -0.023815 | -0.0059687 | 1.8991e-06 | 1.1664e-06 | 0.036123 | 0.036123 | 0.036123 | 0.98111 | -0.36225 | 0.98102 | -0.36393 | 9.924
11 | -0.023817 | -0.0059699 | 0.02384 | 0.0059839 | 2.2853e-05 | 1.4035e-05 | 0.036123 | 0.036123 | 0.036123 | 0.98111 | -0.36225 | 0.98214 | -0.34213 | 9.924
12 | -0.077899 | -0.019725 | 0.078339 | 0.020006 | 0.00044066 | 0.00028095 | 0.11809 | 0.11809 | 0.11809 | 0.98214 | -0.34213 | 0.98821 | -0.22504 | 32.4437
13 | -0.12814 | -0.032573 | 0.12824 | 0.032636 | 0.0001005 | 6.2831e-05 | 0.19266 | 0.19266 | 0.19266 | 0.99055 | -0.18001 | 0.9914 | -0.16374 | 13.2321
14 | 0.12814 | 0.032573 | -0.12806 | -0.032523 | 8.0812e-05 | 5.0524e-05 | 0.19266 | 0.19266 | 0.19266 | 0.99055 | -0.18001 | 0.98987 | -0.19311 | 13.2322
15 | -0.13963 | -0.03549 | 0.13966 | 0.035509 | 3.156e-05 | 1.9804e-05 | 0.20975 | 0.20975 | 0.20975 | 0.9914 | -0.16374 | 0.99165 | -0.15905 | 14.4057
16 | 0.11538 | 0.029346 | -0.11534 | -0.029316 | 4.7038e-05 | 2.9248e-05 | 0.1736 | 0.1736 | 0.1736 | 0.98987 | -0.19311 | 0.98943 | -0.20158 | 11.9233
17 | -0.078339 | -0.020006 | 0.078408 | 0.020049 | 6.8923e-05 | 4.3435e-05 | 0.11809 | 0.11809 | 0.11809 | 0.98821 | -0.22504 | 0.98916 | -0.20686 | 16.2218
18 | 0.0047906 | 0.0012005 | -0.00479 | -0.0012005 | 6.375e-07 | 1.1965e-08 | 0.0073137 | 0.0073138 | 0.0073138 | 0.97467 | -0.48777 | 0.97453 | -0.49057 | 2.0093
19 | -0.13706 | -0.03513 | 0.13717 | 0.035203 | 0.00011558 | 7.388e-05 | 0.20619 | 0.20619 | 0.20619 | 0.99044 | -0.1817 | 0.99135 | -0.16432 | 56.6451
20 | 0.13706 | 0.03513 | -0.13673 | -0.034922 | 0.00032424 | 0.00020725 | 0.20619 | 0.20619 | 0.20619 | 0.99044 | -0.1817 | 0.98788 | -0.23062 | 56.6451
21 | -0.14969 | -0.038343 | 0.14981 | 0.038416 | 0.00011473 | 7.3116e-05 | 0.22498 | 0.22498 | 0.22498 | 0.99135 | -0.16432 | 0.99218 | -0.14851 | 30.9041
22 | 0.012521 | 0.0031391 | -0.012517 | -0.0031369 | 3.9998e-06 | 2.1707e-06 | 0.018794 | 0.018794 | 0.018794 | 0.99135 | -0.16432 | 0.99101 | -0.17102 | 5.1631
23 | 0.12449 | 0.031854 | -0.12425 | -0.031703 | 0.00023695 | 0.00015142 | 0.18775 | 0.18775 | 0.18775 | 0.98788 | -0.23062 | 0.98583 | -0.27002 | 51.579
24 | -0.092457 | -0.02357 | 0.09248 | 0.023585 | 2.3577e-05 | 1.4423e-05 | 0.13923 | 0.13923 | 0.13923 | 0.98916 | -0.20686 | 0.98943 | -0.20158 | 9.5623
25 | 0.011815 | 0.0029613 | -0.011814 | -0.002961 | 5.6781e-07 | 3.0193e-07 | 0.017778 | 0.017778 | 0.017778 | 0.98895 | -0.21102 | 0.98889 | -0.21203 | 4.8839
26 | -0.011815 | -0.0029613 | 0.011817 | 0.0029622 | 1.6276e-06 | 8.6541e-07 | 0.017778 | 0.017777 | 0.017778 | 0.98895 | -0.21102 | 0.98909 | -0.20813 | 4.8839
27 | 0.011034 | 0.0027654 | -0.011033 | -0.0027652 | 4.8998e-07 | 2.5273e-07 | 0.016599 | 0.016599 | 0.016599 | 0.98909 | -0.20813 | 0.98905 | -0.20906 | 4.5603
28 | -0.02285 | -0.0057276 | 0.022858 | 0.005732 | 7.1354e-06 | 4.3599e-06 | 0.034377 | 0.034377 | 0.034377 | 0.98909 | -0.20813 | 0.98943 | -0.20158 | 9.4442
29 | -0.015142 | -0.003795 | 0.015145 | 0.0037964 | 2.3353e-06 | 1.339e-06 | 0.022726 | 0.022726 | 0.022726 | 0.99148 | -0.16229 | 0.99165 | -0.15905 | 6.2433
30 | -0.1548 | -0.039306 | 0.15495 | 0.039397 | 0.00014562 | 9.1713e-05 | 0.23247 | 0.23247 | 0.23247 | 0.99165 | -0.15905 | 0.99267 | -0.13952 | 15.9665
31 | 0.16465 | 0.041859 | -0.16457 | -0.04181 | 7.8242e-05 | 4.9367e-05 | 0.2469 | 0.2469 | 0.2469 | 0.99318 | -0.12965 | 0.99267 | -0.13952 | 16.9573
32 | -0.16465 | -0.041859 | 0.1647 | 0.041889 | 4.7273e-05 | 2.9827e-05 | 0.2469 | 0.2469 | 0.2469 | 0.99318 | -0.12965 | 0.99349 | -0.12369 | 16.9573
33 | 0.034168 | 0.0085667 | -0.034167 | -0.0085657 | 1.5588e-06 | 9.7707e-07 | 0.051177 | 0.051177 | 0.051177 | 0.99349 | -0.12369 | 0.99344 | -0.12465 | 14.0596
34 | -0.19887 | -0.050455 | 0.19909 | 0.050595 | 0.00022023 | 0.00013958 | 0.29807 | 0.29807 | 0.29807 | 0.99349 | -0.12369 | 0.9947 | -0.10069 | 20.4722
35 | -0.02162 | -0.0054186 | 0.021628 | 0.0054233 | 7.7598e-06 | 4.7111e-06 | 0.032397 | 0.032396 | 0.032397 | 0.99306 | -0.13218 | 0.99344 | -0.12465 | 8.9001
36 | -0.16342 | -0.041829 | 0.16344 | 0.04184 | 1.7157e-05 | 1.0823e-05 | 0.24541 | 0.24541 | 0.24541 | 0.99218 | -0.14851 | 0.9923 | -0.14634 | 16.8548
37 | 0.45795 | 0.11732 | -0.45762 | -0.11711 | 0.00032983 | 0.00021069 | 0.68234 | 0.68234 | 0.68234 | 1 | 0 | 0.99921 | -0.014875 | 46.8639
38 | 0.44444 | 0.1138 | -0.44387 | -0.11344 | 0.00056916 | 0.00036354 | 0.66272 | 0.66272 | 0.66272 | 0.99921 | -0.014875 | 0.99782 | -0.041349 | 45.5162
39 | -0.17535 | -0.044824 | 0.17561 | 0.044988 | 0.00025994 | 0.00016429 | 0.26326 | 0.26326 | 0.26326 | 0.9923 | -0.14634 | 0.9939 | -0.11575 | 18.0811
40 | -0.18821 | -0.048147 | 0.18822 | 0.04815 | 4.6742e-06 | 2.959e-06 | 0.28213 | 0.28213 | 0.28213 | 0.9939 | -0.11575 | 0.99393 | -0.11523 | 19.3771
41 | -0.2014 | -0.051453 | 0.20154 | 0.051543 | 0.00014174 | 8.9854e-05 | 0.30186 | 0.30186 | 0.30186 | 0.99393 | -0.11523 | 0.9947 | -0.10069 | 20.732
42 | -0.41025 | -0.10455 | 0.41083 | 0.10492 | 0.00058036 | 0.00037058 | 0.61433 | 0.61433 | 0.61433 | 0.9947 | -0.10069 | 0.99623 | -0.07142 | 42.1928
43 | -0.42045 | -0.10733 | 0.42087 | 0.1076 | 0.00041343 | 0.00026402 | 0.6287 | 0.6287 | 0.6287 | 0.99623 | -0.07142 | 0.9973 | -0.051092 | 43.1801
44 | -0.43405 | -0.1109 | 0.43425 | 0.11103 | 0.0002046 | 0.00013068 | 0.64837 | 0.64837 | 0.64837 | 0.9973 | -0.051092 | 0.99782 | -0.041349 | 44.5307

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46922 | 0.11973

## res_load
| p_mw | q_mvar
0 | 0.048596 | 0.012179
1 | 0.055032 | 0.013792
2 | 0.0071762 | 0.0017985
3 | 0.0027616 | 0.00069212
4 | 0.023815 | 0.0059687
5 | 0.011385 | 0.0028532
6 | 0.012677 | 0.0031772
7 | 0.046001 | 0.011529
8 | 0.00479 | 0.0012005
9 | 0.012243 | 0.0030684
10 | 0.011997 | 0.0030069
11 | 0.014048 | 0.0035208
12 | 0.011814 | 0.002961
13 | 0.015142 | 0.003795
14 | 0.012517 | 0.0031369
15 | 0.0096242 | 0.0024121
16 | 0.02162 | 0.0054186
17 | 0.012538 | 0.0031424
18 | 0.013619 | 0.0034132
19 | 0.011033 | 0.0027652
20 | 0.009621 | 0.0024113
21 | 0.013177 | 0.0033025
22 | 0.011907 | 0.0029843
23 | 0.012604 | 0.0031589
24 | 0.013177 | 0.0033025
25 | 0.0096233 | 0.0024118
26 | 0.0096243 | 0.0024121
27 | 0.01318 | 0.0033033
28 | 0.009622 | 0.0024115

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1