## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-248_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-248_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-248_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-248_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-248_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-248_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1061-248_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1061-248_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_1061-248_0_4_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1061-248_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1061-248_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1061-248_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1061-248_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1061-248_0_4_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_1061-248_0_4_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_1061-248_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1061-248_0_4_node_54 | 0.4 | n |  | TRUE
17 | bus_LV_1061-248_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1061-248_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1061-248_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1061-248_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1061-248_0_4_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_1061-248_0_4_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_1061-248_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1061-248_0_4_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_1061-248_0_4_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_1061-248_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_1061-248_0_4_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_1061-248_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1061-248_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1061-248_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1061-248_0_4_node_56 | 0.4 | n |  | TRUE
32 | bus_LV_1061-248_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1061-248_0_4_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_1061-248_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1061-248_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1061-248_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_1061-248_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1061-248_0_4_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_1061-248_0_4_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_1061-248_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_1061-248_0_4_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_1061-248_0_4_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_1061-248_0_4_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_1061-248_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_1061-248_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1061-248_0_4_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1061-248_0_4_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_1061-248_0_4_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_1061-248_0_4_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_1061-248_0_4_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_1061-248_0_4_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_1061-248_0_4_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_1061-248_0_4_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1061-248_0_4_node_52 | 0.4 | n |  | TRUE
55 | bus_MV_211_1_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-248_0_4_load_0 | 0 | 0.018751 | 0.0046995 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-248_0_4_load_1 | 1 | 0.01392 | 0.0034886 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-248_0_4_load_2 | 2 | 0.017413 | 0.0043641 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-248_0_4_load_5 | 5 | 0.018657 | 0.0046758 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-248_0_4_load_23 | 7 | 0.013203 | 0.0033091 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-248_0_4_load_45 | 13 | 0.0012732 | 0.0003191 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-248_0_4_load_53 | 14 | 0.0011527 | 0.00028891 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-248_0_4_load_54 | 16 | 0.0063812 | 0.0015993 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-248_0_4_load_26 | 19 | 0.023965 | 0.0060061 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-248_0_4_load_38 | 22 | 0.030597 | 0.0076683 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-248_0_4_load_33 | 24 | 0.0012958 | 0.00032475 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-248_0_4_load_34 | 25 | 0.0041369 | 0.0010368 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-248_0_4_load_32 | 26 | 0.018531 | 0.0046444 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-248_0_4_load_58 | 27 | 0.036566 | 0.0091643 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-248_0_4_load_35 | 29 | 0.0069398 | 0.0017393 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-248_0_4_load_56 | 31 | 0.04072 | 0.010205 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-248_0_4_load_57 | 33 | 0.03273 | 0.0082029 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-248_0_4_load_24 | 37 | 0.025546 | 0.0064025 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-248_0_4_load_43 | 39 | 0.0024001 | 0.00060151 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-248_0_4_load_41 | 40 | 0.022472 | 0.005632 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-248_0_4_load_55 | 42 | 0.0047374 | 0.0011873 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-248_0_4_load_59 | 43 | 0.033347 | 0.0083577 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-248_0_4_load_31 | 44 | 0.046779 | 0.011724 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-248_0_4_load_28 | 45 | 0.030939 | 0.007754 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-248_0_4_load_37 | 46 | 0.0080238 | 0.0020109 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1061-248_0_4_load_27 | 47 | 0.026666 | 0.0066832 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1061-248_0_4_load_46 | 48 | 0.0010647 | 0.00026683 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1061-248_0_4_load_47 | 49 | 0.0013165 | 0.00032994 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1061-248_0_4_load_48 | 50 | 0.0014411 | 0.00036117 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1061-248_0_4_load_49 | 51 | 0.0055455 | 0.0013898 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1061-248_0_4_load_50 | 52 | 0.0024538 | 0.00061498 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1061-248_0_4_load_51 | 53 | 0.0050049 | 0.0012543 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1061-248_0_4_load_52 | 54 | 0.0057468 | 0.0014403 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-248_0_4_line_0 |  | 0 | 1 | 0.022645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-248_0_4_line_1 |  | 0 | 2 | 0.0384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-248_0_4_line_2 |  | 1 | 3 | 0.040362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-248_0_4_line_3 |  | 2 | 4 | 0.021479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-248_0_4_line_4 |  | 3 | 5 | 0.019383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1061-248_0_4_line_5 |  | 3 | 6 | 0.011978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-248_0_4_line_6 |  | 4 | 7 | 0.057407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-248_0_4_line_7 |  | 4 | 8 | 0.0088496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-248_0_4_line_8 |  | 5 | 9 | 0.020037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1061-248_0_4_line_9 |  | 6 | 10 | 0.006692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-248_0_4_line_10 |  | 8 | 26 | 0.0043154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-248_0_4_line_11 |  | 9 | 34 | 0.02078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-248_0_4_line_12 |  | 9 | 17 | 0.070884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1061-248_0_4_line_13 |  | 10 | 29 | 0.12284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-248_0_4_line_14 |  | 10 | 12 | 0.016032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-248_0_4_line_15 |  | 11 | 12 | 0.015245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-248_0_4_line_16 |  | 11 | 13 | 0.017512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-248_0_4_line_17 |  | 12 | 14 | 0.016548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-248_0_4_line_18 |  | 13 | 41 | 0.0083051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-248_0_4_line_19 |  | 14 | 15 | 0.045303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-248_0_4_line_20 |  | 15 | 16 | 0.019561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-248_0_4_line_21 |  | 16 | 42 | 0.002808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-248_0_4_line_22 |  | 17 | 18 | 0.10372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1061-248_0_4_line_23 |  | 17 | 19 | 0.034371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1061-248_0_4_line_24 |  | 18 | 27 | 0.013575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-248_0_4_line_25 |  | 18 | 28 | 0.044194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1061-248_0_4_line_26 |  | 20 | 21 | 0.038703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-248_0_4_line_27 |  | 20 | 22 | 0.021399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-248_0_4_line_28 |  | 21 | 40 | 0.02986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-248_0_4_line_29 |  | 23 | 24 | 0.010308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-248_0_4_line_30 |  | 23 | 25 | 0.038433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-248_0_4_line_31 |  | 23 | 26 | 0.03915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-248_0_4_line_32 |  | 28 | 33 | 0.017025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-248_0_4_line_33 |  | 28 | 30 | 0.31921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1061-248_0_4_line_34 |  | 30 | 31 | 0.017205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1061-248_0_4_line_35 |  | 30 | 32 | 0.059495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1061-248_0_4_line_36 |  | 32 | 44 | 0.016411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1061-248_0_4_line_37 |  | 32 | 45 | 0.060026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1061-248_0_4_line_38 |  | 34 | 46 | 0.008282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1061-248_0_4_line_39 |  | 34 | 36 | 0.038001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1061-248_0_4_line_40 |  | 35 | 36 | 0.059973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1061-248_0_4_line_41 |  | 35 | 37 | 0.002561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1061-248_0_4_line_42 |  | 36 | 43 | 0.006163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1061-248_0_4_line_43 |  | 38 | 39 | 0.0038133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1061-248_0_4_line_44 |  | 38 | 40 | 0.042492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1061-248_0_4_line_45 |  | 39 | 41 | 0.018929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1061-248_0_4_line_46 |  | 41 | 48 | 0.0026252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1061-248_0_4_line_47 |  | 42 | 54 | 0.00667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1061-248_0_4_line_48 |  | 45 | 47 | 0.049225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_1061-248_0_4_line_49 |  | 49 | 50 | 0.0022576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1061-248_0_4_line_50 |  | 49 | 51 | 0.01643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1061-248_0_4_line_51 |  | 50 | 52 | 0.00090259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1061-248_0_4_line_52 |  | 51 | 53 | 0.0057382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1061-248_0_4_line_53 |  | 53 | 54 | 0.021887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-248_0_4_trafo_26 | 0.63 MVA 20/0.4 kV | 55 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41
0 | 2669313.051 | 1211606.0758 | 2669305.0854 | 1211608.846 | 2669291.7827 | 1211613.8474
1 | 2669313.051 | 1211606.0758 | 2669331.1636 | 1211599.7766 | 2669349.4781 | 1211593.9371
2 | 2669254.0624 | 1211628.2101 | 2669272.7082 | 1211621.1555 | 2669277.6315 | 1211619.2559 | 2669287.2719 | 1211615.5433 | 2669291.7827 | 1211613.8474
3 | 2669369.8812 | 1211587.2299 | 2669363.9983 | 1211589.3073 | 2669349.4781 | 1211593.9371
4 | 2669254.0624 | 1211628.2101 | 2669252.9303 | 1211626.2402 | 2669250.3184 | 1211622.1295 | 2669246.5514 | 1211616.7269 | 2669244.4668 | 1211613.6675 | 2669243.3701 | 1211612.0526
5 | 2669254.0624 | 1211628.2101 | 2669254.4849 | 1211629.1267 | 2669256.4115 | 1211633.3517 | 2669258.3257 | 1211637.3431 | 2669258.7422 | 1211638.115 | 2669259.2333 | 1211639.0102
6 | 2669369.8812 | 1211587.2299 | 2669367.2844 | 1211582.4857 | 2669348.1719 | 1211559.7382 | 2669333.4585 | 1211542.9123
7 | 2669369.8812 | 1211587.2299 | 2669371.7763 | 1211591.5435 | 2669375.6975 | 1211590.2216
8 | 2669231.8483 | 1211596.3881 | 2669234.1509 | 1211597.6822 | 2669234.7622 | 1211598.0451 | 2669236.3193 | 1211600.0644 | 2669236.752 | 1211602.7156 | 2669238.0843 | 1211604.4654 | 2669239.1923 | 1211605.9014 | 2669243.3701 | 1211612.0526
9 | 2669259.2333 | 1211639.0102 | 2669258.0526 | 1211640.5752 | 2669257.6132 | 1211642.4157 | 2669257.3545 | 1211644.414 | 2669257.497 | 1211645.2272
10 | 2669375.6975 | 1211590.2216 | 2669376.884 | 1211593.393 | 2669377.2083 | 1211594.2639
11 | 2669218.2612 | 1211612.1291 | 2669220.2268 | 1211609.7282 | 2669223.0402 | 1211606.292 | 2669227.1904 | 1211601.6039 | 2669230.5566 | 1211597.685 | 2669231.8483 | 1211596.3881
12 | 2669231.8483 | 1211596.3881 | 2669227.4956 | 1211591.6791 | 2669216.0747 | 1211581.1956 | 2669211.2621 | 1211576.8259 | 2669199.5346 | 1211565.9054 | 2669194.6808 | 1211561.1572 | 2669191.6689 | 1211558.1204 | 2669188.0922 | 1211556.6113 | 2669185.626 | 1211556.3159 | 2669182.8473 | 1211556.0946 | 2669181.1441 | 1211556.1861 | 2669180.5103 | 1211554.4888 | 2669179.4297 | 1211552.008
13 | 2669257.497 | 1211645.2272 | 2669259.1988 | 1211647.8709 | 2669260.1118 | 1211649.0822 | 2669264.4745 | 1211652.2682 | 2669272.9821 | 1211657.1033 | 2669281.0897 | 1211661.0554 | 2669365.5411 | 1211702.2808
14 | 2669243.0916 | 1211652.2644 | 2669243.8406 | 1211651.8951 | 2669249.0755 | 1211649.3321 | 2669249.9543 | 1211648.9087 | 2669250.5351 | 1211648.6263 | 2669256.8092 | 1211645.5639 | 2669257.497 | 1211645.2272
15 | 2669243.0916 | 1211652.2644 | 2669246.4131 | 1211653.5038 | 2669251.8604 | 1211656.202 | 2669256.9223 | 1211658.729
16 | 2669256.9223 | 1211658.729 | 2669248.6303 | 1211674.1529
17 | 2669243.0916 | 1211652.2644 | 2669240.398 | 1211651.2659 | 2669235.3059 | 1211650.6953 | 2669226.8252 | 1211651.7889
18 | 2669244.6978 | 1211681.4679 | 2669248.6303 | 1211674.1529
19 | 2669181.9926 | 1211654.0013 | 2669192.6083 | 1211655.9478 | 2669199.1752 | 1211655.8127 | 2669212.6938 | 1211653.8127 | 2669223.6776 | 1211652.1947 | 2669226.8252 | 1211651.7889
20 | 2669181.9926 | 1211654.0013 | 2669181.7759 | 1211655.6553 | 2669166.4169 | 1211655.8218 | 2669166.1673 | 1211658.3427
21 | 2669168.9752 | 1211658.3217 | 2669166.1673 | 1211658.3427
22 | 2669179.4297 | 1211552.008 | 2669176.7293 | 1211552.8995 | 2669147.044 | 1211574.2242 | 2669145.0667 | 1211575.0129 | 2669140.7686 | 1211576.7309 | 2669130.753 | 1211577.4153 | 2669128.8409 | 1211577.1707 | 2669129.1346 | 1211574.1278 | 2669129.5321 | 1211569.9854 | 2669130.9419 | 1211570.9579 | 2669135.5097 | 1211571.5334 | 2669138.6185 | 1211571.4582 | 2669141.1729 | 1211570.6985 | 2669146.1392 | 1211568.3657 | 2669148.2468 | 1211566.8225 | 2669150.1824 | 1211565.0438 | 2669153.8463 | 1211559.0381 | 2669155.4286 | 1211556.2658 | 2669159.3611 | 1211552.6536
23 | 2669179.4297 | 1211552.008 | 2669181.7867 | 1211551.2349 | 2669187.3056 | 1211551.0543 | 2669193.6528 | 1211553.485 | 2669208.3547 | 1211566.4047
24 | 2669150.015 | 1211542.7835 | 2669159.3611 | 1211552.6536
25 | 2669159.3611 | 1211552.6536 | 2669164.803 | 1211549.2812 | 2669170.318 | 1211545.5095 | 2669173.5198 | 1211543.3119 | 2669175.6506 | 1211542.3915 | 2669177.3883 | 1211537.3641 | 2669179.8169 | 1211530.4213 | 2669182.5028 | 1211523.5704 | 2669183.6979 | 1211518.8035
26 | 2669315.7953 | 1211740.6192 | 2669313.2171 | 1211743.4355 | 2669308.9206 | 1211745.0199 | 2669304.2259 | 1211745.5657 | 2669295.0933 | 1211742.2131 | 2669279.1489 | 1211741.7721
27 | 2669315.7953 | 1211740.6192 | 2669316.5264 | 1211739.8272 | 2669324.4467 | 1211721.1128
28 | 2669279.1489 | 1211741.7721 | 2669276.1508 | 1211741.4816 | 2669260.6566 | 1211734.9865 | 2669251.5179 | 1211730.8109
29 | 2669340.0142 | 1211606.4837 | 2669330.2091 | 1211609.6648
30 | 2669340.0142 | 1211606.4837 | 2669343.1588 | 1211615.0922 | 2669340.3614 | 1211621.7194 | 2669336.4198 | 1211630.6792 | 2669326.6817 | 1211638.2152
31 | 2669340.0142 | 1211606.4837 | 2669346.9173 | 1211604.2403 | 2669377.2083 | 1211594.2639
32 | 2669170.6482 | 1211507.8676 | 2669182.1583 | 1211517.8962 | 2669183.6979 | 1211518.8035
33 | 2669207.2993 | 1211339.4655 | 2669203.595 | 1211339.1112 | 2669191.964 | 1211338.8317 | 2669167.7275 | 1211338.4172 | 2669157.3116 | 1211338.1963 | 2669146.5363 | 1211338.1714 | 2669139.0506 | 1211338.218 | 2669131.9958 | 1211337.1467 | 2669125.3961 | 1211336.8034 | 2669122.4234 | 1211336.9246 | 2669119.2887 | 1211336.5992 | 2669116.627 | 1211338.7364 | 2669114.5614 | 1211350.4197 | 2669114.723 | 1211358.7712 | 2669112.9288 | 1211367.3669 | 2669108.0835 | 1211378.262 | 2669105.0085 | 1211389.1776 | 2669106.0659 | 1211397.6062 | 2669109.2255 | 1211408.2383 | 2669112.2974 | 1211419.2252 | 2669116.1533 | 1211430.0989 | 2669117.4167 | 1211434.5162 | 2669117.739 | 1211438.8338 | 2669116.2628 | 1211444.2534 | 2669113.6229 | 1211449.1036 | 2669116.3685 | 1211448.9019 | 2669123.6068 | 1211456.4238 | 2669127.1862 | 1211459.0224 | 2669127.6696 | 1211459.2726 | 2669137.1636 | 1211464.2746 | 2669147.9464 | 1211470.837 | 2669159.5577 | 1211477.3868 | 2669166.16 | 1211481.4213 | 2669177.4846 | 1211487.7899 | 2669182.5274 | 1211491.3172 | 2669185.7262 | 1211494.6231 | 2669187.3416 | 1211496.8654 | 2669188.3179 | 1211499.1671 | 2669189.4205 | 1211503.0378 | 2669189.5262 | 1211507.0193 | 2669187.3171 | 1211512.7306 | 2669183.6979 | 1211518.8035
34 | 2669206.6446 | 1211350.6983 | 2669211.7199 | 1211350.7794 | 2669207.2993 | 1211339.4655
35 | 2669207.2993 | 1211339.4655 | 2669217.8646 | 1211340.5665 | 2669224.4768 | 1211345.0683 | 2669237.9542 | 1211346.0252 | 2669241.4347 | 1211347.322 | 2669245.4254 | 1211351.8044 | 2669255.829 | 1211360.9308 | 2669257.6061 | 1211364.298
36 | 2669257.6061 | 1211364.298 | 2669255.6359 | 1211374.2924 | 2669249.4357 | 1211373.5756
37 | 2669257.6061 | 1211364.298 | 2669274.0561 | 1211378.2198 | 2669284.3397 | 1211385.8995 | 2669306.356 | 1211399.0432
38 | 2669212.6098 | 1211606.0598 | 2669218.2612 | 1211612.1291
39 | 2669186.6028 | 1211631.9299 | 2669189.6829 | 1211629.086 | 2669191.7902 | 1211627.5651 | 2669194.9227 | 1211626.7564 | 2669199.9239 | 1211625.3469 | 2669204.04 | 1211623.5935 | 2669208.0043 | 1211621.1713 | 2669211.2355 | 1211619.0519 | 2669213.9233 | 1211616.6261 | 2669216.8525 | 1211613.6915 | 2669218.2612 | 1211612.1291
40 | 2669145.1306 | 1211620.6199 | 2669145.781 | 1211621.5391 | 2669146.484 | 1211622.5145 | 2669147.7895 | 1211623.9527 | 2669148.9466 | 1211625.7451 | 2669149.3156 | 1211628.6511 | 2669149.4364 | 1211631.3431 | 2669150.0159 | 1211634.4406 | 2669150.0521 | 1211635.2527 | 2669149.8807 | 1211636.9295 | 2669149.4136 | 1211638.5473 | 2669154.5828 | 1211639.0298 | 2669165.5763 | 1211639.8466 | 2669172.9917 | 1211639.9326 | 2669178.8688 | 1211639.6561 | 2669180.9626 | 1211638.6464 | 2669185.2303 | 1211633.6483 | 2669186.6028 | 1211631.9299
41 | 2669145.1306 | 1211620.6199 | 2669142.771 | 1211621.6154
42 | 2669182.8143 | 1211627.0607 | 2669186.6028 | 1211631.9299
43 | 2669238.9717 | 1211700.1576 | 2669235.7353 | 1211698.141
44 | 2669238.9717 | 1211700.1576 | 2669238.0236 | 1211701.9699 | 2669234.5656 | 1211707.9113 | 2669233.0664 | 1211712.0298 | 2669232.7286 | 1211713.638 | 2669233.6315 | 1211718.3403 | 2669235.0861 | 1211721.9817 | 2669236.6079 | 1211723.7671 | 2669244.9272 | 1211727.7995 | 2669251.5179 | 1211730.8109
45 | 2669244.6978 | 1211681.4679 | 2669235.7353 | 1211698.141
46 | 2669244.6978 | 1211681.4679 | 2669242.3715 | 1211680.2513
47 | 2669175.645 | 1211658.2716 | 2669168.9752 | 1211658.3217
48 | 2669348.6223 | 1211424.276 | 2669306.356 | 1211399.0432
49 | 2669208.6703 | 1211679.0874 | 2669210.6882 | 1211680.0996
50 | 2669208.6703 | 1211679.0874 | 2669204.5521 | 1211677.0217 | 2669193.9237 | 1211672.251 | 2669193.8144 | 1211672.1169
51 | 2669210.6882 | 1211680.0996 | 2669211.495 | 1211680.5044
52 | 2669193.8144 | 1211672.1169 | 2669190.1897 | 1211667.6686
53 | 2669190.1897 | 1211667.6686 | 2669187.6678 | 1211664.5737 | 2669187.2196 | 1211661.2886 | 2669187.1188 | 1211658.1855 | 2669175.645 | 1211658.2716

## bus_geodata
| x | y | coords
0 | 2669313.051 | 1211606.0758
1 | 2669291.7827 | 1211613.8474
2 | 2669349.4781 | 1211593.937
3 | 2669254.0624 | 1211628.2101
4 | 2669369.8812 | 1211587.2299
5 | 2669243.3701 | 1211612.0526
6 | 2669259.2333 | 1211639.0102
7 | 2669333.4585 | 1211542.9123
8 | 2669375.6975 | 1211590.2216
9 | 2669231.8483 | 1211596.3881
10 | 2669257.497 | 1211645.2272
11 | 2669256.9223 | 1211658.729
12 | 2669243.0916 | 1211652.2644
13 | 2669248.6303 | 1211674.1529
14 | 2669226.8252 | 1211651.7889
15 | 2669181.9926 | 1211654.0013
16 | 2669166.1673 | 1211658.3427
17 | 2669179.4297 | 1211552.008
18 | 2669159.3611 | 1211552.6536
19 | 2669208.3547 | 1211566.4047
20 | 2669315.7953 | 1211740.6192
21 | 2669279.1489 | 1211741.7721
22 | 2669324.4467 | 1211721.1128
23 | 2669340.0142 | 1211606.4837
24 | 2669330.2091 | 1211609.6648
25 | 2669326.6817 | 1211638.2152
26 | 2669377.2083 | 1211594.2639
27 | 2669150.015 | 1211542.7835
28 | 2669183.6979 | 1211518.8035
29 | 2669365.5411 | 1211702.2808
30 | 2669207.2993 | 1211339.4655
31 | 2669206.6446 | 1211350.6983
32 | 2669257.6061 | 1211364.298
33 | 2669170.6482 | 1211507.8676
34 | 2669218.2612 | 1211612.1291
35 | 2669145.1306 | 1211620.6199
36 | 2669186.6028 | 1211631.9299
37 | 2669142.771 | 1211621.6154
38 | 2669238.9717 | 1211700.1576
39 | 2669235.7353 | 1211698.141
40 | 2669251.5179 | 1211730.8109
41 | 2669244.6978 | 1211681.4679
42 | 2669168.9752 | 1211658.3217
43 | 2669182.8143 | 1211627.0607
44 | 2669249.4357 | 1211373.5756
45 | 2669306.356 | 1211399.0432
46 | 2669212.6098 | 1211606.0598
47 | 2669348.6223 | 1211424.276
48 | 2669242.3715 | 1211680.2513
49 | 2669208.6703 | 1211679.0874
50 | 2669210.6882 | 1211680.0997
51 | 2669193.8144 | 1211672.1169
52 | 2669211.4949 | 1211680.5044
53 | 2669190.1897 | 1211667.6686
54 | 2669175.645 | 1211658.2716
55 | 2669208.3547 | 1211566.4047

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98432 | -0.30088 | 0.018751 | 0.0046995
1 | 0.98585 | -0.27105 | 0.01392 | 0.0034886
2 | 0.98238 | -0.33866 | 0.017413 | 0.0043641
3 | 0.9891 | -0.2081 | 0 | 0
4 | 0.98164 | -0.3531 | 0 | 0
5 | 0.99076 | -0.17607 | 0.018657 | 0.0046758
6 | 0.98801 | -0.22915 | 0 | 0
7 | 0.98094 | -0.36682 | 0.013203 | 0.0033091
8 | 0.98145 | -0.35693 | 0 | 0
9 | 0.99171 | -0.1579 | 0 | 0
10 | 0.9874 | -0.24093 | 0 | 0
11 | 0.98522 | -0.28303 | 0 | 0
12 | 0.98604 | -0.26722 | 0 | 0
13 | 0.98429 | -0.30123 | 0.0012732 | 0.0003191
14 | 0.98552 | -0.27725 | 0.0011527 | 0.00028891
15 | 0.98416 | -0.30381 | 0 | 0
16 | 0.98357 | -0.3153 | 0.0063812 | 0.0015993
17 | 0.99614 | -0.073051 | 0 | 0
18 | 0.991 | -0.17124 | 0 | 0
19 | 1 | 0 | -0.49527 | -0.12673
20 | 0.97866 | -0.41115 | 0 | 0
21 | 0.97976 | -0.38962 | 0 | 0
22 | 0.97805 | -0.42307 | 0.030597 | 0.0076683
23 | 0.98115 | -0.36266 | 0 | 0
24 | 0.98114 | -0.3629 | 0.0012958 | 0.00032475
25 | 0.98101 | -0.36554 | 0.0041369 | 0.0010368
26 | 0.98135 | -0.3588 | 0.018531 | 0.0046444
27 | 0.99054 | -0.18006 | 0.036566 | 0.0091643
28 | 0.98917 | -0.20619 | 0 | 0
29 | 0.98661 | -0.25619 | 0.0069398 | 0.0017393
30 | 0.97842 | -0.41479 | 0 | 0
31 | 0.97777 | -0.42755 | 0.04072 | 0.010205
32 | 0.97697 | -0.4431 | 0 | 0
33 | 0.98866 | -0.21612 | 0.03273 | 0.0082029
34 | 0.99043 | -0.18258 | 0 | 0
35 | 0.98697 | -0.2498 | 0 | 0
36 | 0.98838 | -0.22243 | 0 | 0
37 | 0.98691 | -0.25098 | 0.025546 | 0.0064025
38 | 0.98269 | -0.33226 | 0 | 0
39 | 0.98288 | -0.32861 | 0.0024001 | 0.00060151
40 | 0.9806 | -0.37305 | 0.022472 | 0.005632
41 | 0.98385 | -0.30968 | 0 | 0
42 | 0.98351 | -0.31663 | 0.0047374 | 0.0011873
43 | 0.98819 | -0.2261 | 0.033347 | 0.0083577
44 | 0.97626 | -0.45713 | 0.046779 | 0.011724
45 | 0.97617 | -0.4589 | 0.030939 | 0.007754
46 | 0.99037 | -0.18376 | 0.0080238 | 0.0020109
47 | 0.97556 | -0.47092 | 0.026666 | 0.0066832
48 | 0.98385 | -0.30973 | 0.0010647 | 0.00026683
49 | 0.98292 | -0.3281 | 0.0013165 | 0.00032994
50 | 0.98291 | -0.32825 | 0.0014411 | 0.00036117
51 | 0.983 | -0.32655 | 0.0055455 | 0.0013898
52 | 0.98291 | -0.32829 | 0.0024538 | 0.00061498
53 | 0.98305 | -0.32544 | 0.0050049 | 0.0012543
54 | 0.98337 | -0.31922 | 0.0057468 | 0.0014403
55 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.073473 | -0.018466 | 0.073577 | 0.018533 | 0.0001048 | 6.6782e-05 | 0.11109 | 0.11109 | 0.11109 | 0.98432 | -0.30088 | 0.98585 | -0.27105 | 30.519
1 | 0.054721 | 0.013767 | -0.054623 | -0.013704 | 9.8586e-05 | 6.2608e-05 | 0.082743 | 0.082743 | 0.082743 | 0.98432 | -0.30088 | 0.98238 | -0.33866 | 22.7315
2 | -0.087497 | -0.022021 | 0.087761 | 0.02219 | 0.00026412 | 0.00016852 | 0.1321 | 0.1321 | 0.1321 | 0.98585 | -0.27105 | 0.9891 | -0.2081 | 36.2909
3 | 0.03721 | 0.0093399 | -0.037184 | -0.0093237 | 2.5592e-05 | 1.6107e-05 | 0.056367 | 0.056367 | 0.056367 | 0.98238 | -0.33866 | 0.98164 | -0.3531 | 15.4854
4 | -0.187 | -0.047336 | 0.18729 | 0.047519 | 0.00028799 | 0.00018381 | 0.2815 | 0.2815 | 0.2815 | 0.9891 | -0.2081 | 0.99076 | -0.17607 | 38.6675
5 | 0.099243 | 0.025146 | -0.099143 | -0.025082 | 0.00010026 | 6.401e-05 | 0.1494 | 0.1494 | 0.1494 | 0.9891 | -0.2081 | 0.98801 | -0.22915 | 41.0442
6 | 0.013212 | 0.0033139 | -0.013203 | -0.0033091 | 8.6356e-06 | 4.8016e-06 | 0.020028 | 0.020029 | 0.020029 | 0.98164 | -0.3531 | 0.98094 | -0.36682 | 5.5024
7 | 0.023972 | 0.0060099 | -0.023968 | -0.0060072 | 4.3822e-06 | 2.6927e-06 | 0.036339 | 0.036339 | 0.036339 | 0.98164 | -0.3531 | 0.98145 | -0.35693 | 9.9832
8 | -0.20595 | -0.052195 | 0.20613 | 0.052309 | 0.00017996 | 0.00011414 | 0.30952 | 0.30952 | 0.30952 | 0.99076 | -0.17607 | 0.99171 | -0.1579 | 21.2582
9 | 0.099143 | 0.025082 | -0.099087 | -0.025046 | 5.6014e-05 | 3.5763e-05 | 0.1494 | 0.1494 | 0.1494 | 0.98801 | -0.22915 | 0.9874 | -0.24093 | 41.0442
10 | 0.023968 | 0.0060072 | -0.023966 | -0.0060058 | 2.1369e-06 | 1.3131e-06 | 0.036339 | 0.036339 | 0.036339 | 0.98145 | -0.35693 | 0.98135 | -0.3588 | 9.9832
11 | 0.06715 | 0.016918 | -0.067071 | -0.016868 | 7.9157e-05 | 5.0393e-05 | 0.10079 | 0.10079 | 0.10079 | 0.99171 | -0.1579 | 0.99043 | -0.18258 | 27.6889
12 | -0.27328 | -0.069228 | 0.2744 | 0.06994 | 0.0011188 | 0.00071233 | 0.41031 | 0.4103 | 0.41031 | 0.99171 | -0.1579 | 0.99614 | -0.073051 | 28.1804
13 | 0.0069448 | 0.0017409 | -0.0069398 | -0.0017393 | 5.0463e-06 | 1.6596e-06 | 0.010466 | 0.010467 | 0.010467 | 0.9874 | -0.24093 | 0.98661 | -0.25619 | 2.8754
14 | 0.092142 | 0.023305 | -0.092026 | -0.023231 | 0.00011605 | 7.4068e-05 | 0.13893 | 0.13893 | 0.13893 | 0.9874 | -0.24093 | 0.98604 | -0.26722 | 38.1689
15 | -0.058117 | -0.014684 | 0.058161 | 0.014712 | 4.4089e-05 | 2.8022e-05 | 0.087818 | 0.087818 | 0.087818 | 0.98522 | -0.28303 | 0.98604 | -0.26722 | 24.1258
16 | 0.058117 | 0.014684 | -0.058066 | -0.014652 | 5.0643e-05 | 3.2189e-05 | 0.087818 | 0.087818 | 0.087818 | 0.98522 | -0.28303 | 0.98429 | -0.30123 | 24.1258
17 | 0.033865 | 0.008519 | -0.033849 | -0.0085088 | 1.6214e-05 | 1.0166e-05 | 0.051117 | 0.051117 | 0.051117 | 0.98604 | -0.26722 | 0.98552 | -0.27725 | 14.0431
18 | 0.056793 | 0.014333 | -0.05677 | -0.014318 | 2.2977e-05 | 1.46e-05 | 0.085893 | 0.085893 | 0.085893 | 0.98429 | -0.30123 | 0.98385 | -0.30968 | 23.5971
19 | 0.032696 | 0.0082199 | -0.032655 | -0.008194 | 4.1419e-05 | 2.5932e-05 | 0.049377 | 0.049377 | 0.049377 | 0.98552 | -0.27725 | 0.98416 | -0.30381 | 13.565
20 | 0.032655 | 0.008194 | -0.032637 | -0.0081828 | 1.7884e-05 | 1.1198e-05 | 0.049377 | 0.049377 | 0.049377 | 0.98416 | -0.30381 | 0.98357 | -0.3153 | 13.5651
21 | 0.026256 | 0.0065835 | -0.026254 | -0.0065825 | 1.6615e-06 | 1.0277e-06 | 0.039723 | 0.039723 | 0.039723 | 0.98357 | -0.3153 | 0.98351 | -0.31663 | 10.9129
22 | 0.21748 | 0.055674 | -0.21645 | -0.055021 | 0.0010289 | 0.00065313 | 0.32529 | 0.32529 | 0.32529 | 0.99614 | -0.073051 | 0.991 | -0.17124 | 22.3412
23 | -0.49188 | -0.12561 | 0.49362 | 0.12673 | 0.0017436 | 0.0011141 | 0.73559 | 0.73559 | 0.73559 | 0.99614 | -0.073051 | 1 | 0 | 50.5214
24 | 0.036581 | 0.009174 | -0.036566 | -0.0091643 | 1.536e-05 | 9.6557e-06 | 0.05493 | 0.05493 | 0.05493 | 0.991 | -0.17124 | 0.99054 | -0.18006 | 15.0908
25 | 0.17987 | 0.045847 | -0.17957 | -0.045656 | 0.00030284 | 0.00019154 | 0.27036 | 0.27036 | 0.27036 | 0.991 | -0.17124 | 0.98917 | -0.20619 | 18.5686
26 | -0.030614 | -0.0076791 | 0.030646 | 0.0076988 | 3.145e-05 | 1.9641e-05 | 0.04655 | 0.04655 | 0.04655 | 0.97866 | -0.41115 | 0.97976 | -0.38962 | 12.7885
27 | 0.030614 | 0.0076791 | -0.030597 | -0.0076683 | 1.7389e-05 | 1.086e-05 | 0.04655 | 0.04655 | 0.04655 | 0.97866 | -0.41115 | 0.97805 | -0.42307 | 12.7885
28 | -0.030646 | -0.0076988 | 0.03067 | 0.0077139 | 2.4264e-05 | 1.5153e-05 | 0.04655 | 0.04655 | 0.04655 | 0.97976 | -0.38962 | 0.9806 | -0.37305 | 12.7885
29 | 0.0012958 | 0.00032463 | -0.0012958 | -0.00032475 | 1.4929e-08 | -1.2063e-07 | 0.0019651 | 0.0019652 | 0.0019652 | 0.98115 | -0.36266 | 0.98114 | -0.3629 | 0.53989
30 | 0.0041374 | 0.0010367 | -0.0041369 | -0.0010368 | 5.6746e-07 | -1.2214e-07 | 0.0062747 | 0.0062749 | 0.0062749 | 0.98115 | -0.36266 | 0.98101 | -0.36554 | 1.7239
31 | -0.0054332 | -0.0013613 | 0.0054342 | 0.0013614 | 9.9677e-07 | 1.4339e-07 | 0.0082399 | 0.0082397 | 0.0082399 | 0.98115 | -0.36266 | 0.98135 | -0.3588 | 2.2637
32 | 0.032746 | 0.0082126 | -0.03273 | -0.0082029 | 1.5493e-05 | 9.6969e-06 | 0.049261 | 0.049261 | 0.049261 | 0.98917 | -0.20619 | 0.98866 | -0.21612 | 13.5333
33 | 0.14682 | 0.037443 | -0.14536 | -0.036523 | 0.001463 | 0.00092008 | 0.2211 | 0.2211 | 0.2211 | 0.98917 | -0.20619 | 0.97842 | -0.41479 | 15.1857
34 | 0.040745 | 0.010221 | -0.04072 | -0.010205 | 2.4777e-05 | 1.5641e-05 | 0.06197 | 0.06197 | 0.06197 | 0.97842 | -0.41479 | 0.97777 | -0.42755 | 17.0248
35 | 0.10462 | 0.026302 | -0.10447 | -0.026214 | 0.00014125 | 8.7414e-05 | 0.15913 | 0.15913 | 0.15913 | 0.97842 | -0.41479 | 0.97697 | -0.4431 | 10.9296
36 | 0.046811 | 0.011744 | -0.046779 | -0.011724 | 3.1287e-05 | 1.9818e-05 | 0.071301 | 0.071301 | 0.071301 | 0.97697 | -0.4431 | 0.97626 | -0.45713 | 19.5882
37 | 0.057664 | 0.014471 | -0.05762 | -0.014446 | 4.3415e-05 | 2.4782e-05 | 0.087834 | 0.087835 | 0.087835 | 0.97697 | -0.4431 | 0.97617 | -0.4589 | 6.0326
38 | 0.0080242 | 0.0020111 | -0.0080238 | -0.0020109 | 4.5138e-07 | 1.823e-07 | 0.012056 | 0.012056 | 0.012056 | 0.99043 | -0.18258 | 0.99037 | -0.18376 | 3.312
39 | 0.059047 | 0.014857 | -0.058935 | -0.014785 | 0.0001122 | 7.1319e-05 | 0.088732 | 0.088732 | 0.088732 | 0.99043 | -0.18258 | 0.98838 | -0.22243 | 24.377
40 | -0.025548 | -0.0064034 | 0.025581 | 0.006424 | 3.3366e-05 | 2.0587e-05 | 0.038518 | 0.038517 | 0.038518 | 0.98697 | -0.2498 | 0.98838 | -0.22243 | 10.5818
41 | 0.025548 | 0.0064034 | -0.025546 | -0.0064025 | 1.4248e-06 | 8.7916e-07 | 0.038518 | 0.038518 | 0.038518 | 0.98697 | -0.2498 | 0.98691 | -0.25098 | 10.5818
42 | 0.033353 | 0.0083613 | -0.033347 | -0.0083577 | 5.8275e-06 | 3.6507e-06 | 0.050215 | 0.050215 | 0.050215 | 0.98838 | -0.22243 | 0.98819 | -0.2261 | 13.7953
43 | -0.053245 | -0.013412 | 0.053255 | 0.013418 | 9.3011e-06 | 5.9044e-06 | 0.08065 | 0.08065 | 0.08065 | 0.98269 | -0.33226 | 0.98288 | -0.32861 | 22.1565
44 | 0.053245 | 0.013412 | -0.053142 | -0.013346 | 0.00010364 | 6.5796e-05 | 0.08065 | 0.08065 | 0.08065 | 0.98269 | -0.33226 | 0.9806 | -0.37305 | 22.1566
45 | -0.055655 | -0.014019 | 0.055705 | 0.014051 | 5.0425e-05 | 3.2032e-05 | 0.084283 | 0.084283 | 0.084283 | 0.98288 | -0.32861 | 0.98385 | -0.30968 | 23.1547
46 | 0.0010647 | 0.0002668 | -0.0010647 | -0.00026683 | 2.5526e-09 | -3.1704e-08 | 0.0016102 | 0.0016103 | 0.0016103 | 0.98385 | -0.30968 | 0.98385 | -0.30973 | 0.44238
47 | 0.021517 | 0.0053952 | -0.021514 | -0.0053936 | 2.6509e-06 | 1.612e-06 | 0.032555 | 0.032555 | 0.032555 | 0.98351 | -0.31663 | 0.98337 | -0.31922 | 8.9437
48 | 0.026682 | 0.0066918 | -0.026666 | -0.0066832 | 1.5269e-05 | 8.5423e-06 | 0.040674 | 0.040674 | 0.040674 | 0.97617 | -0.4589 | 0.97556 | -0.47092 | 5.5871
49 | 0.0038949 | 0.00097613 | -0.0038949 | -0.00097614 | 2.9434e-08 | -9.7765e-09 | 0.0058964 | 0.0058964 | 0.0058964 | 0.98292 | -0.3281 | 0.98291 | -0.32825 | 1.6199
50 | -0.0052114 | -0.0013061 | 0.0052118 | 0.0013061 | 3.8349e-07 | 3.7165e-08 | 0.0078894 | 0.0078893 | 0.0078894 | 0.98292 | -0.3281 | 0.983 | -0.32655 | 2.1674
51 | 0.0024538 | 0.00061497 | -0.0024538 | -0.00061498 | 4.6708e-09 | -8.4508e-09 | 0.0037148 | 0.0037148 | 0.0037148 | 0.98291 | -0.32825 | 0.98291 | -0.32829 | 1.0205
52 | -0.010757 | -0.0026959 | 0.010758 | 0.0026962 | 5.7058e-07 | 2.9242e-07 | 0.016284 | 0.016284 | 0.016284 | 0.983 | -0.32655 | 0.98305 | -0.32544 | 4.4736
53 | -0.015763 | -0.0039506 | 0.015767 | 0.0039533 | 4.6723e-06 | 2.7127e-06 | 0.023859 | 0.023859 | 0.023859 | 0.98305 | -0.32544 | 0.98337 | -0.31922 | 6.5548

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51924 | 0.13273

## res_load
| p_mw | q_mvar
0 | 0.018751 | 0.0046995
1 | 0.01392 | 0.0034886
2 | 0.017413 | 0.0043641
3 | 0.018657 | 0.0046758
4 | 0.013203 | 0.0033091
5 | 0.0012732 | 0.0003191
6 | 0.0011527 | 0.00028891
7 | 0.0063812 | 0.0015993
8 | 0.023965 | 0.0060061
9 | 0.030597 | 0.0076683
10 | 0.0012958 | 0.00032475
11 | 0.0041369 | 0.0010368
12 | 0.018531 | 0.0046444
13 | 0.036566 | 0.0091643
14 | 0.0069398 | 0.0017393
15 | 0.04072 | 0.010205
16 | 0.03273 | 0.0082029
17 | 0.025546 | 0.0064025
18 | 0.0024001 | 0.00060151
19 | 0.022472 | 0.005632
20 | 0.0047374 | 0.0011873
21 | 0.033347 | 0.0083577
22 | 0.046779 | 0.011724
23 | 0.030939 | 0.007754
24 | 0.0080238 | 0.0020109
25 | 0.026666 | 0.0066832
26 | 0.0010647 | 0.00026683
27 | 0.0013165 | 0.00032994
28 | 0.0014411 | 0.00036117
29 | 0.0055455 | 0.0013898
30 | 0.0024538 | 0.00061498
31 | 0.0050049 | 0.0012543
32 | 0.0057468 | 0.0014403

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1