## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-36_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-36_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1061-36_0_6_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1061-36_0_6_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_1061-36_0_6_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_1061-36_0_6_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1061-36_0_6_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_1061-36_0_6_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1061-36_0_6_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1061-36_0_6_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_1061-36_0_6_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1061-36_0_6_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_1061-36_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1061-36_0_6_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1061-36_0_6_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1061-36_0_6_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1061-36_0_6_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1061-36_0_6_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1061-36_0_6_node_5 | 0.4 | n |  | TRUE
19 | bus_LV_1061-36_0_6_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1061-36_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1061-36_0_6_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1061-36_0_6_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1061-36_0_6_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1061-36_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1061-36_0_6_node_6 | 0.4 | n |  | TRUE
26 | bus_LV_1061-36_0_6_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_1061-36_0_6_node_26 | 0.4 | n |  | TRUE
28 | bus_MV_213_0_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-36_0_6_load_0 | 0 | 0.026948 | 0.0067539 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-36_0_6_load_22 | 3 | 0.041696 | 0.01045 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-36_0_6_load_21 | 4 | 0.042117 | 0.010555 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-36_0_6_load_27 | 6 | 0.0044907 | 0.0011255 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-36_0_6_load_29 | 8 | 0.0090446 | 0.0022668 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-36_0_6_load_28 | 11 | 0.045845 | 0.01149 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-36_0_6_load_25 | 14 | 0.03366 | 0.008436 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-36_0_6_load_24 | 15 | 0.068438 | 0.017152 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-36_0_6_load_7 | 17 | 0.0027168 | 0.00068088 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-36_0_6_load_5 | 18 | 0.0025573 | 0.00064091 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-36_0_6_load_9 | 19 | 0.035801 | 0.0089726 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-36_0_6_load_18 | 21 | 0.047807 | 0.011982 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-36_0_6_load_19 | 22 | 0.069508 | 0.01742 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-36_0_6_load_23 | 23 | 0.076821 | 0.019253 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-36_0_6_load_20 | 24 | 0.079006 | 0.019801 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-36_0_6_load_6 | 25 | 0.0039667 | 0.00099415 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-36_0_6_load_30 | 26 | 0.0084688 | 0.0021225 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-36_0_6_load_26 | 27 | 0.0043219 | 0.0010832 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-36_0_6_line_0 |  | 0 | 1 | 0.035419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-36_0_6_line_1 |  | 1 | 2 | 0.02365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-36_0_6_line_2 |  | 2 | 3 | 0.025475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-36_0_6_line_3 |  | 2 | 4 | 0.060665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1061-36_0_6_line_4 |  | 3 | 23 | 0.023312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-36_0_6_line_5 |  | 4 | 24 | 0.013993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1061-36_0_6_line_6 |  | 5 | 6 | 0.087242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-36_0_6_line_7 |  | 5 | 7 | 0.15416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-36_0_6_line_8 |  | 6 | 27 | 0.021377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-36_0_6_line_9 |  | 7 | 8 | 0.014829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-36_0_6_line_10 |  | 7 | 9 | 0.026083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-36_0_6_line_11 |  | 9 | 26 | 0.011726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-36_0_6_line_12 |  | 10 | 11 | 0.074534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-36_0_6_line_13 |  | 10 | 12 | 0.029526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-36_0_6_line_14 |  | 11 | 27 | 0.030142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-36_0_6_line_15 |  | 12 | 19 | 0.022402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-36_0_6_line_16 |  | 13 | 14 | 0.013152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-36_0_6_line_17 |  | 13 | 15 | 0.015876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1061-36_0_6_line_18 |  | 13 | 16 | 0.036295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1061-36_0_6_line_19 |  | 15 | 22 | 0.029609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1061-36_0_6_line_20 |  | 16 | 24 | 0.010185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1061-36_0_6_line_21 |  | 16 | 25 | 0.0069764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-36_0_6_line_22 |  | 17 | 18 | 0.01925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-36_0_6_line_23 |  | 18 | 25 | 0.019962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-36_0_6_line_24 |  | 19 | 20 | 0.015937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-36_0_6_line_25 |  | 20 | 21 | 0.022038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-36_0_6_line_26 |  | 20 | 22 | 0.01313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-36_0_6_trafo_20 | 0.63 MVA 20/0.4 kV | 28 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2666369.4189 | 1213318.8415 | 2666340.7284 | 1213298.0727
1 | 2666369.4189 | 1213318.8415 | 2666372.4574 | 1213314.0724 | 2666382.4691 | 1213299.1189
2 | 2666382.4691 | 1213299.1189 | 2666386.7967 | 1213295.9207 | 2666400.3366 | 1213290.9016 | 2666405.9819 | 1213290.5904
3 | 2666382.4691 | 1213299.1189 | 2666396.1999 | 1213267.3965 | 2666401.3829 | 1213267.8878 | 2666410.5264 | 1213249.1026
4 | 2666405.9819 | 1213290.5904 | 2666415.942 | 1213290.0414 | 2666428.9128 | 1213293.1433
5 | 2666414.9277 | 1213235.8409 | 2666411.3888 | 1213247.3309 | 2666410.5264 | 1213249.1026
6 | 2666376.862 | 1213126.5605 | 2666376.6217 | 1213131.0829 | 2666378.685 | 1213135.453 | 2666380.3915 | 1213137.7512 | 2666423.394 | 1213176.8764 | 2666435.9859 | 1213188.1194
7 | 2666376.862 | 1213126.5605 | 2666375.9365 | 1213125.7609 | 2666371.7756 | 1213122.1568 | 2666390.4383 | 1213106.6993 | 2666460.5279 | 1213149.5174 | 2666463.422 | 1213151.5843 | 2666465.3288 | 1213152.9508 | 2666467.3411 | 1213154.3852 | 2666466.0878 | 1213156.417 | 2666465.6392 | 1213157.1346 | 2666478.1855 | 1213165.6241 | 2666488.3479 | 1213173.3088 | 2666489.5213 | 1213174.3559
8 | 2666451.9318 | 1213202.3572 | 2666435.9859 | 1213188.1194
9 | 2666489.5213 | 1213174.3559 | 2666486.9872 | 1213177.474 | 2666486.5252 | 1213178.0248 | 2666485.9837 | 1213177.5407 | 2666478.9885 | 1213171.281
10 | 2666509.0027 | 1213191.7616 | 2666508.1453 | 1213190.9849 | 2666489.5213 | 1213174.3559
11 | 2666509.0027 | 1213191.7616 | 2666507.4563 | 1213193.501 | 2666506.5616 | 1213192.6683 | 2666505.5615 | 1213191.7455 | 2666504.8998 | 1213191.1377 | 2666502.8698 | 1213189.2473 | 2666500.554 | 1213187.0979
12 | 2666531.3186 | 1213270.337 | 2666524.5518 | 1213266.0923 | 2666520.3725 | 1213263.4663 | 2666474.4154 | 1213222.4322
13 | 2666508.703 | 1213267.6499 | 2666512.3184 | 1213263.621 | 2666524.1109 | 1213274.2813 | 2666531.3186 | 1213270.337
14 | 2666451.9318 | 1213202.3572 | 2666474.4154 | 1213222.4322
15 | 2666508.703 | 1213267.6499 | 2666491.8751 | 1213252.862
16 | 2666436.658 | 1213202.7735 | 2666432.7324 | 1213199.1942 | 2666429.055 | 1213195.8401 | 2666426.919 | 1213193.9349
17 | 2666436.658 | 1213202.7735 | 2666440.2151 | 1213206.0151 | 2666448.3909 | 1213213.4678
18 | 2666436.658 | 1213202.7735 | 2666426.5319 | 1213215.0128 | 2666420.4277 | 1213220.8373 | 2666410.0438 | 1213226.9032
19 | 2666470.2866 | 1213233.3999 | 2666453.526 | 1213218.1487 | 2666448.3909 | 1213213.4678
20 | 2666410.0438 | 1213226.9032 | 2666414.9277 | 1213235.8409 | 2666414.9277 | 1213235.8409
21 | 2666410.0438 | 1213226.9032 | 2666403.4932 | 1213229.3029
22 | 2666383.9902 | 1213231.8582 | 2666382.4204 | 1213231.8544 | 2666368.1392 | 1213229.0716 | 2666365.3628 | 1213227.6257
23 | 2666383.9902 | 1213231.8582 | 2666396.4358 | 1213231.8882 | 2666403.4932 | 1213229.3029
24 | 2666479.9977 | 1213242.2363 | 2666490.2118 | 1213251.4003 | 2666491.8751 | 1213252.862
25 | 2666479.9977 | 1213242.2363 | 2666476.2752 | 1213246.3419 | 2666469.7635 | 1213257.365 | 2666469.0161 | 1213260.9822
26 | 2666479.9977 | 1213242.2363 | 2666470.2866 | 1213233.3999

## bus_geodata
| x | y | coords
0 | 2666340.7284 | 1213298.0727
1 | 2666369.4189 | 1213318.8415
2 | 2666382.4691 | 1213299.1189
3 | 2666405.9819 | 1213290.5904
4 | 2666410.5264 | 1213249.1026
5 | 2666376.862 | 1213126.5605
6 | 2666435.9859 | 1213188.1194
7 | 2666489.5213 | 1213174.3559
8 | 2666478.9885 | 1213171.281
9 | 2666509.0027 | 1213191.7616
10 | 2666531.3186 | 1213270.337
11 | 2666474.4154 | 1213222.4322
12 | 2666508.703 | 1213267.6499
13 | 2666436.658 | 1213202.7735
14 | 2666426.919 | 1213193.9349
15 | 2666448.391 | 1213213.4678
16 | 2666410.0438 | 1213226.9032
17 | 2666365.3628 | 1213227.6257
18 | 2666383.9902 | 1213231.8582
19 | 2666491.8751 | 1213252.862
20 | 2666479.9977 | 1213242.2363
21 | 2666469.0161 | 1213260.9822
22 | 2666470.2866 | 1213233.3999
23 | 2666428.9128 | 1213293.1433
24 | 2666414.9277 | 1213235.8409
25 | 2666403.4932 | 1213229.3029
26 | 2666500.554 | 1213187.0979
27 | 2666451.9318 | 1213202.3572
28 | 2666410.0438 | 1213226.9032

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99371 | -0.12066 | 0.026948 | 0.0067539
1 | 0.99458 | -0.10383 | 0 | 0
2 | 0.99517 | -0.092606 | 0 | 0
3 | 0.9924 | -0.14589 | 0.041696 | 0.01045
4 | 0.9992 | -0.015263 | 0.042117 | 0.010555
5 | 0.97827 | -0.41951 | 0 | 0
6 | 0.97969 | -0.39171 | 0.0044907 | 0.0011255
7 | 0.97576 | -0.46882 | 0 | 0
8 | 0.97564 | -0.47128 | 0.0090446 | 0.0022668
9 | 0.97556 | -0.47287 | 0 | 0
10 | 0.98585 | -0.27181 | 0 | 0
11 | 0.98087 | -0.36878 | 0.045845 | 0.01149
12 | 0.98782 | -0.23366 | 0 | 0
13 | 0.99532 | -0.089379 | 0 | 0
14 | 0.99492 | -0.097171 | 0.03366 | 0.008436
15 | 0.99389 | -0.11677 | 0.068438 | 0.017152
16 | 0.99895 | -0.019942 | 0 | 0
17 | 0.99875 | -0.023821 | 0.0027168 | 0.00068088
18 | 0.9988 | -0.022907 | 0.0025573 | 0.00064091
19 | 0.98932 | -0.20482 | 0.035801 | 0.0089726
20 | 0.99091 | -0.17422 | 0 | 0
21 | 0.98994 | -0.19294 | 0.047807 | 0.011982
22 | 0.99185 | -0.15608 | 0.069508 | 0.01742
23 | 0.99076 | -0.17764 | 0.076821 | 0.019253
24 | 1 | 0 | -0.53025 | -0.13418
25 | 0.99889 | -0.021068 | 0.0039667 | 0.00099415
26 | 0.97547 | -0.47469 | 0.0084688 | 0.0021225
27 | 0.98013 | -0.38317 | 0.0043219 | 0.0010832
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026948 | -0.0067539 | 0.02697 | 0.0067673 | 2.1628e-05 | 1.3383e-05 | 0.040353 | 0.040353 | 0.040353 | 0.99371 | -0.12066 | 0.99458 | -0.10383 | 11.086
1 | -0.02697 | -0.0067673 | 0.026984 | 0.0067762 | 1.4442e-05 | 8.9356e-06 | 0.040353 | 0.040353 | 0.040353 | 0.99458 | -0.10383 | 0.99517 | -0.092606 | 11.086
2 | 0.11894 | 0.029971 | -0.11863 | -0.029777 | 0.00030233 | 0.00019316 | 0.1779 | 0.1779 | 0.1779 | 0.99517 | -0.092606 | 0.9924 | -0.14589 | 48.8725
3 | -0.14592 | -0.036747 | 0.14646 | 0.037092 | 0.00054181 | 0.00034517 | 0.21825 | 0.21825 | 0.21825 | 0.99517 | -0.092606 | 0.9992 | -0.015263 | 29.9792
4 | 0.076938 | 0.019327 | -0.076821 | -0.019253 | 0.00011637 | 7.4177e-05 | 0.11538 | 0.11538 | 0.11538 | 0.9924 | -0.14589 | 0.99076 | -0.17764 | 31.697
5 | -0.18858 | -0.047647 | 0.18872 | 0.047735 | 0.00013808 | 8.7822e-05 | 0.28097 | 0.28097 | 0.28097 | 0.9992 | -0.015263 | 1 | 0 | 25.7297
6 | -0.017558 | -0.0044153 | 0.017581 | 0.0044291 | 2.3344e-05 | 1.3843e-05 | 0.026712 | 0.026712 | 0.026712 | 0.97827 | -0.41951 | 0.97969 | -0.39171 | 7.3386
7 | 0.017558 | 0.0044153 | -0.017517 | -0.0043908 | 4.1253e-05 | 2.4471e-05 | 0.026712 | 0.026713 | 0.026713 | 0.97827 | -0.41951 | 0.97576 | -0.46882 | 7.3388
8 | -0.022072 | -0.0055546 | 0.022081 | 0.0055601 | 9.0141e-06 | 5.4997e-06 | 0.033533 | 0.033533 | 0.033533 | 0.97969 | -0.39171 | 0.98013 | -0.38317 | 9.2123
9 | 0.0090457 | 0.0022673 | -0.0090446 | -0.0022668 | 1.0582e-06 | 4.9203e-07 | 0.013795 | 0.013795 | 0.013795 | 0.97576 | -0.46882 | 0.97564 | -0.47128 | 3.7897
10 | 0.0084712 | 0.0021235 | -0.0084696 | -0.0021228 | 1.6324e-06 | 7.1899e-07 | 0.012919 | 0.012919 | 0.012919 | 0.97576 | -0.46882 | 0.97556 | -0.47287 | 3.5491
11 | 0.0084696 | 0.0021228 | -0.0084688 | -0.0021225 | 7.3387e-07 | 3.2328e-07 | 0.012919 | 0.012919 | 0.012919 | 0.97556 | -0.47287 | 0.97547 | -0.47469 | 3.5491
12 | 0.072603 | 0.018359 | -0.072266 | -0.018144 | 0.00033601 | 0.0002141 | 0.10964 | 0.10964 | 0.10964 | 0.98585 | -0.27181 | 0.98087 | -0.36878 | 30.1217
13 | -0.072603 | -0.018359 | 0.072736 | 0.018443 | 0.00013311 | 8.4811e-05 | 0.10964 | 0.10964 | 0.10964 | 0.98585 | -0.27181 | 0.98782 | -0.23366 | 30.1216
14 | 0.026421 | 0.0066545 | -0.026403 | -0.0066433 | 1.817e-05 | 1.1249e-05 | 0.040094 | 0.040094 | 0.040094 | 0.98087 | -0.36878 | 0.98013 | -0.38317 | 11.0149
15 | -0.072736 | -0.018443 | 0.072837 | 0.018508 | 0.00010099 | 6.4347e-05 | 0.10964 | 0.10964 | 0.10964 | 0.98782 | -0.23366 | 0.98932 | -0.20482 | 30.1216
16 | 0.033672 | 0.0084438 | -0.03366 | -0.008436 | 1.2499e-05 | 7.8287e-06 | 0.050342 | 0.050342 | 0.050342 | 0.99532 | -0.089379 | 0.99492 | -0.097171 | 13.8303
17 | 0.29554 | 0.07477 | -0.29516 | -0.074522 | 0.00038785 | 0.0002476 | 0.44209 | 0.44209 | 0.44209 | 0.99532 | -0.089379 | 0.99389 | -0.11677 | 40.4844
18 | -0.32922 | -0.083214 | 0.33032 | 0.083916 | 0.0011001 | 0.00070267 | 0.49243 | 0.49243 | 0.49243 | 0.99532 | -0.089379 | 0.99895 | -0.019942 | 45.0945
19 | 0.22672 | 0.05737 | -0.22629 | -0.057098 | 0.00042692 | 0.00027208 | 0.33963 | 0.33963 | 0.33963 | 0.99389 | -0.11677 | 0.99185 | -0.15608 | 31.1015
20 | -0.33956 | -0.086232 | 0.33988 | 0.086441 | 0.00032622 | 0.00020838 | 0.5062 | 0.5062 | 0.5062 | 0.99895 | -0.019942 | 1 | 0 | 46.3551
21 | 0.0092418 | 0.002316 | -0.0092413 | -0.0023158 | 4.9579e-07 | 2.2598e-07 | 0.013766 | 0.013766 | 0.013766 | 0.99895 | -0.019942 | 0.99889 | -0.021068 | 3.782
22 | -0.0027168 | -0.00068088 | 0.0027169 | 0.00068071 | 1.1826e-07 | -1.7624e-07 | 0.0040476 | 0.0040475 | 0.0040476 | 0.99875 | -0.023821 | 0.9988 | -0.022907 | 1.112
23 | -0.0052741 | -0.0013216 | 0.0052746 | 0.0013217 | 4.6214e-07 | 3.4495e-08 | 0.0078574 | 0.0078573 | 0.0078574 | 0.9988 | -0.022907 | 0.99889 | -0.021068 | 2.1586
24 | -0.10864 | -0.02748 | 0.1088 | 0.027582 | 0.00015974 | 0.00010203 | 0.16349 | 0.16349 | 0.16349 | 0.98932 | -0.20482 | 0.99091 | -0.17422 | 44.9149
25 | 0.04785 | 0.012009 | -0.047807 | -0.011982 | 4.2676e-05 | 2.7029e-05 | 0.07186 | 0.07186 | 0.07186 | 0.99091 | -0.17422 | 0.98994 | -0.19294 | 19.7418
26 | -0.15665 | -0.039591 | 0.15678 | 0.039678 | 0.00013636 | 8.6931e-05 | 0.23535 | 0.23535 | 0.23535 | 0.99091 | -0.17422 | 0.99185 | -0.15608 | 32.3283

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60926 | 0.15398

## res_load
| p_mw | q_mvar
0 | 0.026948 | 0.0067539
1 | 0.041696 | 0.01045
2 | 0.042117 | 0.010555
3 | 0.0044907 | 0.0011255
4 | 0.0090446 | 0.0022668
5 | 0.045845 | 0.01149
6 | 0.03366 | 0.008436
7 | 0.068438 | 0.017152
8 | 0.0027168 | 0.00068088
9 | 0.0025573 | 0.00064091
10 | 0.035801 | 0.0089726
11 | 0.047807 | 0.011982
12 | 0.069508 | 0.01742
13 | 0.076821 | 0.019253
14 | 0.079006 | 0.019801
15 | 0.0039667 | 0.00099415
16 | 0.0084688 | 0.0021225
17 | 0.0043219 | 0.0010832

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1