## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-44_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-44_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-44_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-44_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-44_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-44_0_6_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_1061-44_0_6_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1061-44_0_6_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1061-44_0_6_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1061-44_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1061-44_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1061-44_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1061-44_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1061-44_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1061-44_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1061-44_0_6_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1061-44_0_6_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1061-44_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1061-44_0_6_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1061-44_0_6_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_1061-44_0_6_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1061-44_0_6_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1061-44_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1061-44_0_6_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1061-44_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1061-44_0_6_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1061-44_0_6_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1061-44_0_6_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1061-44_0_6_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1061-44_0_6_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1061-44_0_6_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1061-44_0_6_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1061-44_0_6_node_24 | 0.4 | n |  | TRUE
33 | bus_MV_219_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-44_0_6_load_0 | 0 | 0.026403 | 0.0066173 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-44_0_6_load_1 | 1 | 0.017605 | 0.0044123 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-44_0_6_load_2 | 2 | 0.039977 | 0.010019 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-44_0_6_load_3 | 3 | 0.034542 | 0.0086571 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-44_0_6_load_4 | 4 | 0.030249 | 0.007581 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-44_0_6_load_25 | 5 | 0.023183 | 0.0058103 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-44_0_6_load_31 | 6 | 0.069035 | 0.017302 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-44_0_6_load_26 | 7 | 0.029634 | 0.0074269 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-44_0_6_load_5 | 9 | 0.0084596 | 0.0021202 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-44_0_6_load_6 | 10 | 0.024115 | 0.0060438 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-44_0_6_load_10 | 14 | 0.01635 | 0.0040976 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-44_0_6_load_28 | 15 | 0.016915 | 0.0042394 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-44_0_6_load_27 | 16 | 0.0045848 | 0.0011491 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-44_0_6_load_29 | 18 | 0.011731 | 0.0029401 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-44_0_6_load_32 | 19 | 0.03471 | 0.0086992 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-44_0_6_load_18 | 21 | 0.03001 | 0.0075212 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-44_0_6_load_30 | 23 | 0.027934 | 0.0070008 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-44_0_6_load_11 | 25 | 0.03327 | 0.0083383 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-44_0_6_load_17 | 26 | 0.011679 | 0.0029269 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-44_0_6_load_21 | 27 | 0.048805 | 0.012232 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-44_0_6_load_33 | 29 | 0.031071 | 0.007787 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-44_0_6_load_22 | 30 | 0.013335 | 0.003342 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-44_0_6_load_23 | 31 | 0.0072712 | 0.0018223 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-44_0_6_load_24 | 32 | 0.0068353 | 0.0017131 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-44_0_6_line_0 |  | 0 | 1 | 0.010137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-44_0_6_line_1 |  | 0 | 2 | 0.0010209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-44_0_6_line_2 |  | 1 | 3 | 0.0025274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-44_0_6_line_3 |  | 2 | 4 | 0.012561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1061-44_0_6_line_4 |  | 3 | 5 | 0.0076056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-44_0_6_line_5 |  | 4 | 6 | 0.0041679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_1061-44_0_6_line_6 |  | 5 | 7 | 0.0038861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-44_0_6_line_7 |  | 6 | 8 | 0.012346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1061-44_0_6_line_8 |  | 8 | 22 | 0.028465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1061-44_0_6_line_9 |  | 8 | 20 | 0.093272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1061-44_0_6_line_10 |  | 9 | 10 | 0.012008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_1061-44_0_6_line_11 |  | 9 | 11 | 0.022694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1061-44_0_6_line_12 |  | 10 | 12 | 0.0014867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1061-44_0_6_line_13 |  | 11 | 13 | 0.017571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1061-44_0_6_line_14 |  | 11 | 14 | 0.011293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-44_0_6_line_15 |  | 12 | 15 | 0.0079495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1061-44_0_6_line_16 |  | 12 | 16 | 0.0046429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-44_0_6_line_17 |  | 13 | 17 | 0.32258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1061-44_0_6_line_18 |  | 15 | 18 | 0.00011754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1061-44_0_6_line_19 |  | 17 | 19 | 0.013016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-44_0_6_line_20 |  | 18 | 24 | 0.0083497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1061-44_0_6_line_21 |  | 19 | 29 | 0.0095287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-44_0_6_line_22 |  | 20 | 21 | 0.01466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_1061-44_0_6_line_23 |  | 21 | 28 | 0.010625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_1061-44_0_6_line_24 |  | 22 | 26 | 0.027247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_1061-44_0_6_line_25 |  | 22 | 25 | 0.01088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-44_0_6_line_26 |  | 23 | 24 | 0.011288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-44_0_6_line_27 |  | 24 | 28 | 0.004086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1061-44_0_6_line_28 |  | 26 | 27 | 0.0045176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1061-44_0_6_line_29 |  | 27 | 30 | 0.013719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1061-44_0_6_line_30 |  | 30 | 31 | 0.0079512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-44_0_6_line_31 |  | 31 | 32 | 0.0039726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-44_0_6_trafo_22 | 0.63 MVA 20/0.4 kV | 33 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2666074.2479 | 1211728.6542 | 2666072.6071 | 1211728.1402 | 2666064.4908 | 1211725.9099
1 | 2666074.2479 | 1211728.6542 | 2666075.2221 | 1211728.9594
2 | 2666064.4908 | 1211725.9099 | 2666062.0537 | 1211725.2402
3 | 2666087.2086 | 1211732.7146 | 2666075.2221 | 1211728.9594
4 | 2666054.72 | 1211723.225 | 2666062.0537 | 1211725.2402
5 | 2666091.1859 | 1211733.9606 | 2666087.2086 | 1211732.7146
6 | 2666054.72 | 1211723.225 | 2666050.9728 | 1211722.1953
7 | 2666102.0746 | 1211739.7737 | 2666091.3333 | 1211734.0068 | 2666091.1859 | 1211733.9606
8 | 2666109.6294 | 1211714.2417 | 2666108.9328 | 1211733.2123 | 2666102.0746 | 1211739.7737
9 | 2666030.3011 | 1211742.9811 | 2666032.7139 | 1211743.2968 | 2666045.9401 | 1211744.9331 | 2666053.936 | 1211746.7894 | 2666084.7543 | 1211755.8251 | 2666093.3886 | 1211758.3557 | 2666099.9859 | 1211758.8846 | 2666100.9449 | 1211753.2584 | 2666105.6098 | 1211747.1397 | 2666102.0746 | 1211739.7737
10 | 2666022.3964 | 1211697.4288 | 2666033.8697 | 1211700.9719
11 | 2666000.7131 | 1211690.7326 | 2666022.3964 | 1211697.4288
12 | 2666035.2901 | 1211701.4106 | 2666033.8697 | 1211700.9719
13 | 2666000.7131 | 1211690.7326 | 2665992.583 | 1211696.8687 | 2665985.7355 | 1211699.728
14 | 2666000.7131 | 1211690.7326 | 2666005.4231 | 1211686.0262 | 2666007.4664 | 1211681.8661
15 | 2666035.2901 | 1211701.4106 | 2666034.7196 | 1211703.5278 | 2666033.2212 | 1211709.0861
16 | 2666035.2901 | 1211701.4106 | 2666039.7268 | 1211702.7791
17 | 2665985.7355 | 1211699.728 | 2665981.3326 | 1211700.7133 | 2665974.6373 | 1211699.4162 | 2665952.3676 | 1211688.9525 | 2665930.461 | 1211676.5583 | 2665919.0749 | 1211669.984 | 2665926.553 | 1211651.3329 | 2665936.661 | 1211622.9938 | 2665944.3976 | 1211602.9669 | 2665969.4603 | 1211609.6481 | 2665977.7564 | 1211611.8634 | 2665978.5272 | 1211608.8145 | 2665982.2088 | 1211594.0461 | 2665986.9539 | 1211582.0578 | 2666004.5273 | 1211588.4672 | 2666048.9076 | 1211611.4614 | 2666051.2593 | 1211613.8778 | 2666054.8731 | 1211617.5979 | 2666066.025 | 1211624.7257 | 2666074.3062 | 1211630.332 | 2666070.5816 | 1211640.0523
18 | 2666033.2212 | 1211709.0861 | 2666033.1906 | 1211709.1996
19 | 2666070.5816 | 1211640.0523 | 2666066.2559 | 1211652.3287
20 | 2666031.019 | 1211717.262 | 2666031.6926 | 1211714.7568 | 2666033.1906 | 1211709.1996
21 | 2666063.0893 | 1211661.3158 | 2666066.2559 | 1211652.3287
22 | 2666030.3011 | 1211742.9811 | 2666033.0378 | 1211728.5785
23 | 2666035.0213 | 1211718.1402 | 2666033.0378 | 1211728.5785
24 | 2666109.6294 | 1211714.2417 | 2666089.3579 | 1211713.4166 | 2666082.4375 | 1211712.6848
25 | 2666109.6294 | 1211714.2417 | 2666109.7626 | 1211703.3627
26 | 2666031.019 | 1211717.262 | 2666020.0455 | 1211714.6167
27 | 2666035.0213 | 1211718.1402 | 2666031.019 | 1211717.262
28 | 2666077.9699 | 1211712.0336 | 2666080.4324 | 1211712.4727 | 2666082.4375 | 1211712.6848
29 | 2666077.9699 | 1211712.0336 | 2666069.6637 | 1211710.5523 | 2666064.537 | 1211709.284
30 | 2666056.8186 | 1211707.3745 | 2666064.537 | 1211709.284
31 | 2666052.9622 | 1211706.4204 | 2666056.8186 | 1211707.3745

## bus_geodata
| x | y | coords
0 | 2666074.2479 | 1211728.6542
1 | 2666064.4908 | 1211725.9099
2 | 2666075.2221 | 1211728.9594
3 | 2666062.0537 | 1211725.2402
4 | 2666087.2086 | 1211732.7146
5 | 2666054.72 | 1211723.225
6 | 2666091.1859 | 1211733.9606
7 | 2666050.9728 | 1211722.1953
8 | 2666102.0746 | 1211739.7737
9 | 2666022.3964 | 1211697.4288
10 | 2666033.8697 | 1211700.9719
11 | 2666000.7131 | 1211690.7326
12 | 2666035.2901 | 1211701.4106
13 | 2665985.7355 | 1211699.728
14 | 2666007.4664 | 1211681.8661
15 | 2666033.2212 | 1211709.0861
16 | 2666039.7268 | 1211702.7791
17 | 2666070.5816 | 1211640.0523
18 | 2666033.1906 | 1211709.1996
19 | 2666066.2559 | 1211652.3287
20 | 2666030.3011 | 1211742.9811
21 | 2666033.0378 | 1211728.5785
22 | 2666109.6294 | 1211714.2417
23 | 2666020.0455 | 1211714.6167
24 | 2666031.019 | 1211717.262
25 | 2666109.7626 | 1211703.3627
26 | 2666082.4375 | 1211712.6848
27 | 2666077.9699 | 1211712.0336
28 | 2666035.0213 | 1211718.1402
29 | 2666063.0893 | 1211661.3158
30 | 2666064.537 | 1211709.284
31 | 2666056.8186 | 1211707.3745
32 | 2666052.9622 | 1211706.4204
33 | 2666052.9622 | 1211706.4204

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99122 | -0.16835 | 0.026403 | 0.0066173
1 | 0.99025 | -0.18724 | 0.017605 | 0.0044123
2 | 0.99134 | -0.16597 | 0.039977 | 0.010019
3 | 0.99004 | -0.19117 | 0.034542 | 0.0086571
4 | 0.99233 | -0.1469 | 0.030249 | 0.007581
5 | 0.98968 | -0.19831 | 0.023183 | 0.0058103
6 | 0.99248 | -0.14393 | 0.069035 | 0.017302
7 | 0.98957 | -0.20036 | 0.029634 | 0.0074269
8 | 0.99309 | -0.13211 | 0 | 0
9 | 0.98788 | -0.23257 | 0.0084596 | 0.0021202
10 | 0.98808 | -0.22868 | 0.024115 | 0.0060438
11 | 0.98754 | -0.23923 | 0 | 0
12 | 0.98811 | -0.22807 | 0 | 0
13 | 0.98732 | -0.24337 | 0 | 0
14 | 0.98737 | -0.24253 | 0.01635 | 0.0040976
15 | 0.98829 | -0.22469 | 0.016915 | 0.0042394
16 | 0.9881 | -0.22845 | 0.0045848 | 0.0011491
17 | 0.97747 | -0.43501 | 0 | 0
18 | 0.98829 | -0.22463 | 0.011731 | 0.0029401
19 | 0.97667 | -0.45065 | 0.03471 | 0.0086992
20 | 0.98955 | -0.20024 | 0 | 0
21 | 0.989 | -0.211 | 0.03001 | 0.0075212
22 | 0.99558 | -0.084284 | 0 | 0
23 | 0.98823 | -0.22585 | 0.027934 | 0.0070008
24 | 0.98852 | -0.22022 | 0 | 0
25 | 0.99525 | -0.090652 | 0.03327 | 0.0083383
26 | 0.99813 | -0.035553 | 0.011679 | 0.0029269
27 | 0.99857 | -0.027313 | 0.048805 | 0.012232
28 | 0.98865 | -0.21766 | 0 | 0
29 | 0.9764 | -0.45606 | 0.031071 | 0.007787
30 | 1 | 0 | -0.59143 | -0.14989
31 | 0.9999 | -0.0019552 | 0.0072712 | 0.0018223
32 | 0.99987 | -0.0024286 | 0.0068353 | 0.0017131
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.1051 | 0.026391 | -0.105 | -0.02633 | 9.464e-05 | 6.0439e-05 | 0.15779 | 0.15779 | 0.15779 | 0.99122 | -0.16835 | 0.99025 | -0.18724 | 43.3485
1 | -0.1315 | -0.033008 | 0.13151 | 0.033017 | 1.4921e-05 | 9.5364e-06 | 0.19742 | 0.19742 | 0.19742 | 0.99122 | -0.16835 | 0.99134 | -0.16597 | 54.2376
2 | 0.087396 | 0.021918 | -0.08738 | -0.021908 | 1.6347e-05 | 1.043e-05 | 0.13133 | 0.13133 | 0.13133 | 0.99025 | -0.18724 | 0.99004 | -0.19117 | 36.0806
3 | -0.17149 | -0.043037 | 0.17165 | 0.043136 | 0.00015608 | 9.9566e-05 | 0.25743 | 0.25743 | 0.25743 | 0.99134 | -0.16597 | 0.99233 | -0.1469 | 35.3613
4 | 0.052838 | 0.01325 | -0.05282 | -0.013239 | 1.7988e-05 | 1.1415e-05 | 0.079417 | 0.079417 | 0.079417 | 0.99004 | -0.19117 | 0.98968 | -0.19831 | 21.8179
5 | -0.2019 | -0.050717 | 0.20192 | 0.050735 | 2.8659e-05 | 1.8072e-05 | 0.30279 | 0.30279 | 0.30279 | 0.99233 | -0.1469 | 0.99248 | -0.14393 | 16.6367
6 | 0.029636 | 0.0074287 | -0.029634 | -0.0074269 | 2.8936e-06 | 1.802e-06 | 0.04456 | 0.04456 | 0.04456 | 0.98968 | -0.19831 | 0.98957 | -0.20036 | 12.2418
7 | -0.27096 | -0.068037 | 0.27111 | 0.068134 | 0.00015285 | 9.7025e-05 | 0.40629 | 0.40629 | 0.40629 | 0.99248 | -0.14393 | 0.99309 | -0.13211 | 22.3237
8 | -0.47864 | -0.12077 | 0.47974 | 0.12147 | 0.0010989 | 0.00070147 | 0.71746 | 0.71746 | 0.71746 | 0.99309 | -0.13211 | 0.99558 | -0.084284 | 39.4211
9 | 0.20753 | 0.052632 | -0.20685 | -0.052205 | 0.00067737 | 0.0004275 | 0.31117 | 0.31118 | 0.31118 | 0.99309 | -0.13211 | 0.98955 | -0.20024 | 17.0976
10 | -0.091297 | -0.023145 | 0.091314 | 0.023155 | 1.7055e-05 | 1.0146e-05 | 0.13761 | 0.13761 | 0.13761 | 0.98788 | -0.23257 | 0.98808 | -0.22868 | 7.5611
11 | 0.082837 | 0.021025 | -0.082811 | -0.02101 | 2.6539e-05 | 1.5533e-05 | 0.12487 | 0.12487 | 0.12487 | 0.98788 | -0.23257 | 0.98754 | -0.23923 | 6.861
12 | -0.11543 | -0.029199 | 0.11543 | 0.029201 | 3.373e-06 | 2.0635e-06 | 0.17393 | 0.17393 | 0.17393 | 0.98808 | -0.22868 | 0.98811 | -0.22807 | 9.5565
13 | 0.066459 | 0.016911 | -0.066445 | -0.016903 | 1.3239e-05 | 7.3493e-06 | 0.10023 | 0.10023 | 0.10023 | 0.98754 | -0.23923 | 0.98732 | -0.24337 | 5.5072
14 | 0.016352 | 0.0040991 | -0.01635 | -0.0040976 | 2.5711e-06 | 1.501e-06 | 0.02464 | 0.02464 | 0.02464 | 0.98754 | -0.23923 | 0.98737 | -0.24253 | 6.7691
15 | -0.12002 | -0.03035 | 0.12004 | 0.030362 | 1.9496e-05 | 1.1968e-05 | 0.18083 | 0.18083 | 0.18083 | 0.98811 | -0.22807 | 0.98829 | -0.22469 | 9.9358
16 | 0.0045849 | 0.0011491 | -0.0045848 | -0.0011491 | 8.3002e-08 | -6.3502e-09 | 0.0069045 | 0.0069045 | 0.0069045 | 0.98811 | -0.22807 | 0.9881 | -0.22845 | 1.8968
17 | 0.066445 | 0.016903 | -0.065838 | -0.016522 | 0.00060766 | 0.00038073 | 0.10023 | 0.10023 | 0.10023 | 0.98732 | -0.24337 | 0.97747 | -0.43501 | 13.7684
18 | -0.13695 | -0.034602 | 0.13695 | 0.034602 | 3.752e-07 | 2.3259e-07 | 0.2063 | 0.2063 | 0.2063 | 0.98829 | -0.22469 | 0.98829 | -0.22463 | 11.3352
19 | 0.065838 | 0.016522 | -0.065789 | -0.016491 | 4.904e-05 | 3.1222e-05 | 0.10023 | 0.10023 | 0.10023 | 0.97747 | -0.43501 | 0.97667 | -0.45065 | 27.5369
20 | -0.14868 | -0.037542 | 0.14872 | 0.037562 | 3.1412e-05 | 1.9568e-05 | 0.22396 | 0.22396 | 0.22396 | 0.98829 | -0.22463 | 0.98852 | -0.22022 | 12.3057
21 | 0.031079 | 0.007792 | -0.031071 | -0.007787 | 8.0118e-06 | 5.0083e-06 | 0.047351 | 0.047351 | 0.047351 | 0.97667 | -0.45065 | 0.9764 | -0.45606 | 13.0086
22 | 0.20685 | 0.052205 | -0.20674 | -0.052137 | 0.00010647 | 6.7198e-05 | 0.31118 | 0.31118 | 0.31118 | 0.98955 | -0.20024 | 0.989 | -0.211 | 17.0976
23 | 0.17673 | 0.044616 | -0.17668 | -0.044581 | 5.6394e-05 | 3.5411e-05 | 0.26602 | 0.26602 | 0.26602 | 0.989 | -0.211 | 0.98865 | -0.21766 | 14.6167
24 | -0.51302 | -0.12981 | 0.51422 | 0.13058 | 0.0012028 | 0.00076804 | 0.76721 | 0.76721 | 0.76721 | 0.99558 | -0.084284 | 0.99813 | -0.035553 | 42.1542
25 | 0.03328 | 0.0083446 | -0.03327 | -0.0083383 | 1.0095e-05 | 6.3194e-06 | 0.049743 | 0.049743 | 0.049743 | 0.99558 | -0.084284 | 0.99525 | -0.090652 | 13.6656
26 | -0.027934 | -0.0070008 | 0.027941 | 0.0070055 | 7.4885e-06 | 4.648e-06 | 0.042061 | 0.042061 | 0.042061 | 0.98823 | -0.22585 | 0.98852 | -0.22022 | 11.5551
27 | -0.17666 | -0.044567 | 0.17668 | 0.044581 | 2.1687e-05 | 1.3618e-05 | 0.26602 | 0.26602 | 0.26602 | 0.98852 | -0.22022 | 0.98865 | -0.21766 | 14.6167
28 | -0.5259 | -0.13351 | 0.52611 | 0.13364 | 0.00020859 | 0.0001332 | 0.78462 | 0.78462 | 0.78462 | 0.99813 | -0.035553 | 0.99857 | -0.027313 | 43.1108
29 | -0.57491 | -0.14587 | 0.57567 | 0.14636 | 0.00075627 | 0.00048311 | 0.85734 | 0.85734 | 0.85734 | 0.99857 | -0.027313 | 1 | 0 | 47.1067
30 | 0.014108 | 0.0035362 | -0.014107 | -0.0035355 | 1.314e-06 | 7.3669e-07 | 0.020993 | 0.020993 | 0.020993 | 1 | 0 | 0.9999 | -0.0019552 | 5.7673
31 | 0.0068354 | 0.0017131 | -0.0068353 | -0.0017131 | 1.5415e-07 | 4.655e-08 | 0.010172 | 0.010172 | 0.010172 | 0.9999 | -0.0019552 | 0.99987 | -0.0024286 | 2.7946

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60476 | 0.15323

## res_load
| p_mw | q_mvar
0 | 0.026403 | 0.0066173
1 | 0.017605 | 0.0044123
2 | 0.039977 | 0.010019
3 | 0.034542 | 0.0086571
4 | 0.030249 | 0.007581
5 | 0.023183 | 0.0058103
6 | 0.069035 | 0.017302
7 | 0.029634 | 0.0074269
8 | 0.0084596 | 0.0021202
9 | 0.024115 | 0.0060438
10 | 0.01635 | 0.0040976
11 | 0.016915 | 0.0042394
12 | 0.0045848 | 0.0011491
13 | 0.011731 | 0.0029401
14 | 0.03471 | 0.0086992
15 | 0.03001 | 0.0075212
16 | 0.027934 | 0.0070008
17 | 0.03327 | 0.0083383
18 | 0.011679 | 0.0029269
19 | 0.048805 | 0.012232
20 | 0.031071 | 0.007787
21 | 0.013335 | 0.003342
22 | 0.0072712 | 0.0018223
23 | 0.0068353 | 0.0017131

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1