## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-49_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-49_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-49_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-49_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-49_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1061-49_0_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1061-49_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1061-49_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1061-49_0_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_1061-49_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1061-49_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1061-49_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1061-49_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1061-49_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1061-49_0_3_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1061-49_0_3_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_1061-49_0_3_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_1061-49_0_3_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_1061-49_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1061-49_0_3_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_1061-49_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1061-49_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1061-49_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1061-49_0_3_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1061-49_0_3_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1061-49_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1061-49_0_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_1061-49_0_3_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1061-49_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1061-49_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1061-49_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1061-49_0_3_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1061-49_0_3_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1061-49_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1061-49_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_MV_219_0_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-49_0_3_load_0 | 0 | 0.009564 | 0.002397 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-49_0_3_load_1 | 1 | 0.0085796 | 0.0021502 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-49_0_3_load_2 | 2 | 0.0073349 | 0.0018383 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-49_0_3_load_3 | 3 | 0.019398 | 0.0048616 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-49_0_3_load_4 | 4 | 0.025269 | 0.0063329 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-49_0_3_load_23 | 6 | 0.011983 | 0.0030033 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-49_0_3_load_8 | 7 | 0.014597 | 0.0036583 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-49_0_3_load_24 | 8 | 0.0099346 | 0.0024898 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-49_0_3_load_5 | 9 | 0.022833 | 0.0057224 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-49_0_3_load_38 | 15 | 0.036533 | 0.009156 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-49_0_3_load_37 | 17 | 0.0086399 | 0.0021654 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-49_0_3_load_36 | 19 | 0.022077 | 0.0055331 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-49_0_3_load_15 | 20 | 0.024406 | 0.0061167 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-49_0_3_load_17 | 21 | 0.017554 | 0.0043994 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-49_0_3_load_32 | 23 | 0.014817 | 0.0037136 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-49_0_3_load_31 | 24 | 0.018473 | 0.0046298 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-49_0_3_load_19 | 25 | 0.027534 | 0.0069007 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-49_0_3_load_35 | 26 | 0.034973 | 0.008765 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-49_0_3_load_26 | 27 | 0.0086291 | 0.0021626 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-49_0_3_load_18 | 28 | 0.02029 | 0.0050851 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-49_0_3_load_20 | 29 | 0.012223 | 0.0030633 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1061-49_0_3_load_29 | 31 | 0.008537 | 0.0021396 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1061-49_0_3_load_33 | 32 | 0.017595 | 0.0044098 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1061-49_0_3_load_25 | 33 | 0.012425 | 0.0031141 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1061-49_0_3_load_27 | 34 | 0.035437 | 0.0088815 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-49_0_3_line_0 |  | 0 | 1 | 0.0056647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1061-49_0_3_line_1 |  | 0 | 2 | 0.0052682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1061-49_0_3_line_2 |  | 1 | 3 | 0.0091115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1061-49_0_3_line_3 |  | 2 | 4 | 0.0098684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1061-49_0_3_line_4 |  | 3 | 5 | 0.0027647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1061-49_0_3_line_5 |  | 4 | 6 | 0.011457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1061-49_0_3_line_6 |  | 5 | 7 | 0.01209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1061-49_0_3_line_7 |  | 6 | 8 | 0.0067015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1061-49_0_3_line_8 |  | 7 | 10 | 0.021986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1061-49_0_3_line_9 |  | 8 | 13 | 0.0026888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1061-49_0_3_line_10 |  | 9 | 10 | 0.016242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1061-49_0_3_line_11 |  | 9 | 11 | 0.0084124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1061-49_0_3_line_12 |  | 11 | 12 | 0.013924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1061-49_0_3_line_13 |  | 12 | 15 | 0.01885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-49_0_3_line_14 |  | 12 | 16 | 0.026944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1061-49_0_3_line_15 |  | 13 | 14 | 0.013835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1061-49_0_3_line_16 |  | 14 | 21 | 0.0095211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1061-49_0_3_line_17 |  | 14 | 20 | 0.017039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-49_0_3_line_18 |  | 16 | 26 | 0.03255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-49_0_3_line_19 |  | 16 | 27 | 0.0084316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1061-49_0_3_line_20 |  | 17 | 18 | 0.0093851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-49_0_3_line_21 |  | 18 | 19 | 0.01448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-49_0_3_line_22 |  | 18 | 32 | 0.0054776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-49_0_3_line_23 |  | 21 | 24 | 0.0013053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1061-49_0_3_line_24 |  | 22 | 23 | 0.026754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-49_0_3_line_25 |  | 22 | 24 | 0.011206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-49_0_3_line_26 |  | 22 | 25 | 0.013474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-49_0_3_line_27 |  | 23 | 32 | 0.0062223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-49_0_3_line_28 |  | 25 | 28 | 0.019108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-49_0_3_line_29 |  | 27 | 33 | 0.012716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1061-49_0_3_line_30 |  | 28 | 29 | 0.012596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-49_0_3_line_31 |  | 29 | 30 | 0.014907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-49_0_3_line_32 |  | 30 | 31 | 0.0090538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1061-49_0_3_line_33 |  | 33 | 34 | 0.0045722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-49_0_3_trafo_27 | 0.63 MVA 20/0.4 kV | 35 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2665932.2034 | 1211717.4931 | 2665936.3672 | 1211721.3338
1 | 2665932.2034 | 1211717.4931 | 2665928.331 | 1211713.9211
2 | 2665936.3672 | 1211721.3338 | 2665943.0647 | 1211727.5115
3 | 2665921.137 | 1211707.167 | 2665923.5768 | 1211709.5359 | 2665928.331 | 1211713.9211
4 | 2665945.0969 | 1211729.386 | 2665943.0647 | 1211727.5115
5 | 2665921.137 | 1211707.167 | 2665912.9174 | 1211699.1859
6 | 2665945.0969 | 1211729.386 | 2665952.5324 | 1211738.9192
7 | 2665908.1095 | 1211694.5176 | 2665912.9174 | 1211699.1859
8 | 2665966.0528 | 1211756.2564 | 2665958.1036 | 1211746.0623 | 2665952.5324 | 1211738.9192
9 | 2665906.1804 | 1211692.6445 | 2665908.1095 | 1211694.5176
10 | 2665966.0528 | 1211756.2564 | 2665950.9704 | 1211757.5683 | 2665949.8759 | 1211757.4377
11 | 2665941.5227 | 1211756.441 | 2665949.8759 | 1211757.4377
12 | 2665930.6316 | 1211747.7263 | 2665938.9394 | 1211754.3667 | 2665941.5227 | 1211756.441
13 | 2665930.6316 | 1211747.7263 | 2665930.3853 | 1211748.0127 | 2665923.3639 | 1211756.2958 | 2665918.5267 | 1211762.2015
14 | 2665912.2175 | 1211750.7359 | 2665922.008 | 1211739.4148 | 2665923.9928 | 1211741.3268 | 2665930.6316 | 1211747.7263
15 | 2665895.5494 | 1211683.7549 | 2665906.1804 | 1211692.6445
16 | 2665895.5494 | 1211683.7549 | 2665889.8408 | 1211691.3749
17 | 2665895.5494 | 1211683.7549 | 2665882.8515 | 1211672.3934
18 | 2665889.782 | 1211754.5905 | 2665899.3831 | 1211763.1573 | 2665902.7101 | 1211759.1361 | 2665904.2843 | 1211760.3875 | 2665907.0963 | 1211756.9053 | 2665912.2175 | 1211750.7359
19 | 2665912.2175 | 1211750.7359 | 2665905.9551 | 1211745.0901
20 | 2665864.56 | 1211734.8665 | 2665871.4376 | 1211741.2523
21 | 2665864.56 | 1211734.8665 | 2665865.0125 | 1211749.3393
22 | 2665864.56 | 1211734.8665 | 2665865.0761 | 1211729.4133
23 | 2665889.8408 | 1211691.3749 | 2665889.0582 | 1211692.4196
24 | 2665882.9871 | 1211701.794 | 2665867.9521 | 1211723.9232
25 | 2665882.9871 | 1211701.794 | 2665885.0914 | 1211697.7147 | 2665889.0582 | 1211692.4196
26 | 2665882.9871 | 1211701.794 | 2665875.3603 | 1211696.0952 | 2665871.9192 | 1211694.1502
27 | 2665867.9521 | 1211723.9232 | 2665866.635 | 1211725.8617 | 2665865.0761 | 1211729.4133
28 | 2665871.9192 | 1211694.1502 | 2665867.2953 | 1211691.5367 | 2665854.5784 | 1211686.1853
29 | 2665905.9551 | 1211745.0901 | 2665896.511 | 1211736.5758
30 | 2665842.9681 | 1211681.2996 | 2665854.5784 | 1211686.1853
31 | 2665829.2283 | 1211675.5178 | 2665842.9681 | 1211681.2996
32 | 2665829.2283 | 1211675.5178 | 2665825.8588 | 1211683.9212
33 | 2665893.1151 | 1211733.5143 | 2665896.511 | 1211736.5758

## bus_geodata
| x | y | coords
0 | 2665932.2034 | 1211717.4931
1 | 2665936.3672 | 1211721.3338
2 | 2665928.331 | 1211713.9211
3 | 2665943.0647 | 1211727.5115
4 | 2665921.137 | 1211707.167
5 | 2665945.0969 | 1211729.386
6 | 2665912.9174 | 1211699.1859
7 | 2665952.5324 | 1211738.9192
8 | 2665908.1095 | 1211694.5176
9 | 2665949.8759 | 1211757.4377
10 | 2665966.0528 | 1211756.2564
11 | 2665941.5227 | 1211756.441
12 | 2665930.6316 | 1211747.7263
13 | 2665906.1804 | 1211692.6445
14 | 2665895.5494 | 1211683.7549
15 | 2665918.5267 | 1211762.2015
16 | 2665912.2175 | 1211750.7359
17 | 2665871.4376 | 1211741.2523
18 | 2665864.56 | 1211734.8665
19 | 2665865.0125 | 1211749.3393
20 | 2665882.8515 | 1211672.3934
21 | 2665889.8408 | 1211691.3749
22 | 2665882.9871 | 1211701.794
23 | 2665867.9521 | 1211723.9232
24 | 2665889.0582 | 1211692.4196
25 | 2665871.9192 | 1211694.1502
26 | 2665889.782 | 1211754.5905
27 | 2665905.9551 | 1211745.0901
28 | 2665854.5784 | 1211686.1853
29 | 2665842.9681 | 1211681.2996
30 | 2665829.2283 | 1211675.5178
31 | 2665825.8588 | 1211683.9212
32 | 2665865.0761 | 1211729.4133
33 | 2665896.511 | 1211736.5758
34 | 2665893.1151 | 1211733.5143
35 | 2665912.2175 | 1211750.7359

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98564 | -0.27506 | 0.009564 | 0.002397
1 | 0.98609 | -0.26638 | 0.0085796 | 0.0021502
2 | 0.98524 | -0.28283 | 0.0073349 | 0.0018383
3 | 0.98683 | -0.25197 | 0.019398 | 0.0048616
4 | 0.98451 | -0.29698 | 0.025269 | 0.0063329
5 | 0.98707 | -0.24729 | 0 | 0
6 | 0.98375 | -0.31169 | 0.011983 | 0.0030033
7 | 0.98813 | -0.22682 | 0.014597 | 0.0036583
8 | 0.98333 | -0.31982 | 0.0099346 | 0.0024898
9 | 0.99165 | -0.15909 | 0.022833 | 0.0057224
10 | 0.99015 | -0.1878 | 0 | 0
11 | 0.99248 | -0.14311 | 0 | 0
12 | 0.99386 | -0.11673 | 0 | 0
13 | 0.98318 | -0.32293 | 0 | 0
14 | 0.98235 | -0.33892 | 0 | 0
15 | 0.99323 | -0.12889 | 0.036533 | 0.009156
16 | 0.99683 | -0.060136 | 0 | 0
17 | 0.97833 | -0.41773 | 0.0086399 | 0.0021654
18 | 0.9784 | -0.41625 | 0 | 0
19 | 0.97811 | -0.42207 | 0.022077 | 0.0055331
20 | 0.98197 | -0.34643 | 0.024406 | 0.0061167
21 | 0.98186 | -0.34854 | 0.017554 | 0.0043994
22 | 0.9804 | -0.37704 | 0 | 0
23 | 0.97884 | -0.40772 | 0.014817 | 0.0037136
24 | 0.98177 | -0.35031 | 0.018473 | 0.0046298
25 | 0.97955 | -0.39381 | 0.027534 | 0.0069007
26 | 0.99579 | -0.080125 | 0.034973 | 0.008765
27 | 0.99785 | -0.040774 | 0.0086291 | 0.0021626
28 | 0.97882 | -0.40807 | 0.02029 | 0.0050851
29 | 0.97858 | -0.41283 | 0.012223 | 0.0030633
30 | 0.97846 | -0.41515 | 0 | 0
31 | 0.97839 | -0.41655 | 0.008537 | 0.0021396
32 | 0.97856 | -0.41319 | 0.017595 | 0.0044098
33 | 0.99942 | -0.01101 | 0.012425 | 0.0031141
34 | 1 | 0 | -0.42148 | -0.1074
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.25737 | -0.064939 | 0.25747 | 0.065007 | 0.00010698 | 6.8252e-05 | 0.3887 | 0.3887 | 0.3887 | 0.98564 | -0.27506 | 0.98609 | -0.26638 | 35.5952
1 | 0.2478 | 0.062542 | -0.24771 | -0.062483 | 9.2241e-05 | 5.8833e-05 | 0.37426 | 0.37426 | 0.37426 | 0.98564 | -0.27506 | 0.98524 | -0.28283 | 34.273
2 | -0.26605 | -0.067157 | 0.26624 | 0.067275 | 0.00018373 | 0.00011724 | 0.40165 | 0.40165 | 0.40165 | 0.98609 | -0.26638 | 0.98683 | -0.25197 | 36.7808
3 | 0.24037 | 0.060645 | -0.24021 | -0.060541 | 0.00016271 | 0.00010376 | 0.36318 | 0.36318 | 0.36318 | 0.98524 | -0.28283 | 0.98451 | -0.29698 | 33.2585
4 | -0.28563 | -0.072136 | 0.2857 | 0.072177 | 6.4167e-05 | 4.0961e-05 | 0.4309 | 0.4309 | 0.4309 | 0.98683 | -0.25197 | 0.98707 | -0.24729 | 39.4593
5 | 0.21494 | 0.054208 | -0.21479 | -0.054112 | 0.00015126 | 9.6369e-05 | 0.32499 | 0.32499 | 0.32499 | 0.98451 | -0.29698 | 0.98375 | -0.31169 | 29.7611
6 | -0.2857 | -0.072177 | 0.28598 | 0.072356 | 0.0002806 | 0.00017912 | 0.4309 | 0.4309 | 0.4309 | 0.98707 | -0.24729 | 0.98813 | -0.22682 | 39.4593
7 | 0.20281 | 0.051108 | -0.20273 | -0.051058 | 7.8882e-05 | 5.0229e-05 | 0.30687 | 0.30687 | 0.30687 | 0.98375 | -0.31169 | 0.98333 | -0.31982 | 28.1013
8 | -0.30058 | -0.076015 | 0.30114 | 0.076375 | 0.00056366 | 0.00035989 | 0.45288 | 0.45288 | 0.45288 | 0.98813 | -0.22682 | 0.99015 | -0.1878 | 41.4723
9 | 0.19279 | 0.048568 | -0.19277 | -0.04855 | 2.8625e-05 | 1.8218e-05 | 0.29183 | 0.29183 | 0.29183 | 0.98333 | -0.31982 | 0.98318 | -0.32293 | 26.7246
10 | 0.30156 | 0.07664 | -0.30114 | -0.076375 | 0.00041639 | 0.00026586 | 0.45288 | 0.45288 | 0.45288 | 0.99165 | -0.15909 | 0.99015 | -0.1878 | 41.4722
11 | -0.32439 | -0.082363 | 0.32464 | 0.082522 | 0.00024954 | 0.00015938 | 0.48714 | 0.48714 | 0.48714 | 0.99165 | -0.15909 | 0.99248 | -0.14311 | 44.6097
12 | -0.32464 | -0.082522 | 0.32505 | 0.082786 | 0.00041303 | 0.0002638 | 0.48714 | 0.48714 | 0.48714 | 0.99248 | -0.14311 | 0.99386 | -0.11673 | 44.6097
13 | 0.036554 | 0.0091693 | -0.036533 | -0.009156 | 2.1175e-05 | 1.3308e-05 | 0.054732 | 0.054732 | 0.054732 | 0.99386 | -0.11673 | 0.99323 | -0.12889 | 15.0363
14 | -0.3616 | -0.091955 | 0.36259 | 0.092587 | 0.00098893 | 0.00063186 | 0.54187 | 0.54187 | 0.54187 | 0.99386 | -0.11673 | 0.99683 | -0.060136 | 49.6217
15 | 0.19277 | 0.04855 | -0.19262 | -0.048456 | 0.00014728 | 9.3736e-05 | 0.29183 | 0.29183 | 0.29183 | 0.98318 | -0.32293 | 0.98235 | -0.33892 | 26.7246
16 | 0.1682 | 0.042334 | -0.16813 | -0.042285 | 7.7298e-05 | 4.9109e-05 | 0.25485 | 0.25485 | 0.25485 | 0.98235 | -0.33892 | 0.98186 | -0.34854 | 23.3379
17 | 0.024414 | 0.006122 | -0.024406 | -0.0061167 | 8.7392e-06 | 5.3774e-06 | 0.036983 | 0.036983 | 0.036983 | 0.98235 | -0.33892 | 0.98197 | -0.34643 | 10.1601
18 | 0.035006 | 0.0087859 | -0.034973 | -0.008765 | 3.3336e-05 | 2.0911e-05 | 0.05226 | 0.05226 | 0.05226 | 0.99683 | -0.060136 | 0.99579 | -0.080125 | 14.3571
19 | -0.3976 | -0.10137 | 0.39797 | 0.10161 | 0.00037203 | 0.00023777 | 0.59413 | 0.59413 | 0.59413 | 0.99683 | -0.060136 | 0.99785 | -0.040774 | 54.4073
20 | -0.0086399 | -0.0021654 | 0.0086405 | 0.0021656 | 6.0776e-07 | 2.7111e-07 | 0.013141 | 0.013141 | 0.013141 | 0.97833 | -0.41773 | 0.9784 | -0.41625 | 3.6102
21 | 0.022083 | 0.0055368 | -0.022077 | -0.0055331 | 6.1253e-06 | 3.7384e-06 | 0.033586 | 0.033586 | 0.033586 | 0.9784 | -0.41625 | 0.97811 | -0.42207 | 9.2271
22 | -0.030724 | -0.0077024 | 0.030728 | 0.0077052 | 4.485e-06 | 2.8016e-06 | 0.046727 | 0.046727 | 0.046727 | 0.9784 | -0.41625 | 0.97856 | -0.41319 | 12.8372
23 | 0.15057 | 0.037886 | -0.15056 | -0.037878 | 1.275e-05 | 8.1272e-06 | 0.22825 | 0.22825 | 0.22825 | 0.98186 | -0.34854 | 0.98177 | -0.35031 | 31.3526
24 | 0.063246 | 0.015895 | -0.063153 | -0.015837 | 9.2476e-05 | 5.8848e-05 | 0.096008 | 0.096008 | 0.096008 | 0.9804 | -0.37704 | 0.97884 | -0.40772 | 26.3758
25 | -0.13192 | -0.03314 | 0.13209 | 0.033248 | 0.00016851 | 0.00010771 | 0.20025 | 0.20025 | 0.20025 | 0.9804 | -0.37704 | 0.98177 | -0.35031 | 55.0133
26 | 0.068673 | 0.017245 | -0.068618 | -0.01721 | 5.4902e-05 | 3.4967e-05 | 0.10424 | 0.10424 | 0.10424 | 0.9804 | -0.37704 | 0.97955 | -0.39381 | 28.6375
27 | 0.048336 | 0.012123 | -0.048324 | -0.012115 | 1.26e-05 | 7.9855e-06 | 0.073483 | 0.073483 | 0.073483 | 0.97884 | -0.40772 | 0.97856 | -0.41319 | 20.1876
28 | 0.041083 | 0.010309 | -0.041056 | -0.010291 | 2.7914e-05 | 1.7624e-05 | 0.062414 | 0.062414 | 0.062414 | 0.97955 | -0.39381 | 0.97882 | -0.40807 | 17.1467
29 | -0.4066 | -0.10377 | 0.40719 | 0.10415 | 0.00058562 | 0.0003743 | 0.607 | 0.607 | 0.607 | 0.99785 | -0.040774 | 0.99942 | -0.01101 | 55.5857
30 | 0.020766 | 0.0052064 | -0.020761 | -0.0052035 | 4.7077e-06 | 2.8546e-06 | 0.031569 | 0.031569 | 0.031569 | 0.97882 | -0.40807 | 0.97858 | -0.41283 | 8.6729
31 | 0.0085385 | 0.0021402 | -0.0085376 | -0.0021398 | 9.4234e-07 | 4.1585e-07 | 0.012984 | 0.012984 | 0.012984 | 0.97858 | -0.41283 | 0.97846 | -0.41515 | 3.567
32 | 0.0085376 | 0.0021398 | -0.008537 | -0.0021396 | 5.7235e-07 | 2.526e-07 | 0.012984 | 0.012984 | 0.012984 | 0.97846 | -0.41515 | 0.97839 | -0.41655 | 3.567
33 | -0.41961 | -0.10726 | 0.41983 | 0.1074 | 0.00022361 | 0.00014293 | 0.6255 | 0.6255 | 0.6255 | 0.99942 | -0.01101 | 1 | 0 | 57.2798

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45692 | 0.11629

## res_load
| p_mw | q_mvar
0 | 0.009564 | 0.002397
1 | 0.0085796 | 0.0021502
2 | 0.0073349 | 0.0018383
3 | 0.019398 | 0.0048616
4 | 0.025269 | 0.0063329
5 | 0.011983 | 0.0030033
6 | 0.014597 | 0.0036583
7 | 0.0099346 | 0.0024898
8 | 0.022833 | 0.0057224
9 | 0.036533 | 0.009156
10 | 0.0086399 | 0.0021654
11 | 0.022077 | 0.0055331
12 | 0.024406 | 0.0061167
13 | 0.017554 | 0.0043994
14 | 0.014817 | 0.0037136
15 | 0.018473 | 0.0046298
16 | 0.027534 | 0.0069007
17 | 0.034973 | 0.008765
18 | 0.0086291 | 0.0021626
19 | 0.02029 | 0.0050851
20 | 0.012223 | 0.0030633
21 | 0.008537 | 0.0021396
22 | 0.017595 | 0.0044098
23 | 0.012425 | 0.0031141
24 | 0.035437 | 0.0088815

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1