## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-75_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-75_0_3_node_11 | 0.4 | n |  | TRUE
2 | bus_LV_1061-75_0_3_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_1061-75_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-75_0_3_node_72 | 0.4 | n |  | TRUE
5 | bus_LV_1061-75_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1061-75_0_3_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_1061-75_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1061-75_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1061-75_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1061-75_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1061-75_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1061-75_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1061-75_0_3_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_1061-75_0_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1061-75_0_3_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1061-75_0_3_node_67 | 0.4 | n |  | TRUE
17 | bus_LV_1061-75_0_3_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_1061-75_0_3_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_1061-75_0_3_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_1061-75_0_3_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_1061-75_0_3_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_1061-75_0_3_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_1061-75_0_3_node_68 | 0.4 | n |  | TRUE
24 | bus_LV_1061-75_0_3_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_1061-75_0_3_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_1061-75_0_3_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_1061-75_0_3_node_58 | 0.4 | n |  | TRUE
28 | bus_MV_218_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-75_0_3_load_0 | 0 | 0.056042 | 0.014045 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-75_0_3_load_1 | 2 | 0.06893 | 0.017275 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-75_0_3_load_3 | 3 | 0.0090724 | 0.0022738 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-75_0_3_load_72 | 4 | 0.007929 | 0.0019872 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-75_0_3_load_7 | 5 | 0.0043617 | 0.0010931 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-75_0_3_load_41 | 6 | 0.0011419 | 0.00028619 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-75_0_3_load_6 | 7 | 0.0038502 | 0.00096496 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-75_0_3_load_8 | 8 | 0.0049997 | 0.0012531 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-75_0_3_load_9 | 9 | 0.014337 | 0.0035932 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-75_0_3_load_53 | 13 | 0.098685 | 0.024733 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-75_0_3_load_36 | 15 | 0.002393 | 0.00059974 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-75_0_3_load_67 | 16 | 0.0034276 | 0.00085904 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-75_0_3_load_37 | 17 | 0.0011041 | 0.00027672 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-75_0_3_load_40 | 20 | 0.0030043 | 0.00075295 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-75_0_3_load_39 | 21 | 0.0012642 | 0.00031684 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-75_0_3_load_59 | 22 | 0.0024875 | 0.00062342 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-75_0_3_load_68 | 23 | 0.0035415 | 0.00088758 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-75_0_3_load_55 | 24 | 0.011646 | 0.0029188 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-75_0_3_load_56 | 25 | 0.0028865 | 0.00072343 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-75_0_3_load_57 | 26 | 0.0026852 | 0.00067298 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-75_0_3_load_58 | 27 | 0.0055524 | 0.0013916 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-75_0_3_line_0 |  | 0 | 1 | 0.025746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-75_0_3_line_1 |  | 1 | 4 | 0.023281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-75_0_3_line_2 |  | 1 | 10 | 0.073344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-75_0_3_line_3 |  | 2 | 3 | 0.045568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1061-75_0_3_line_4 |  | 2 | 4 | 0.054307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-75_0_3_line_5 |  | 3 | 5 | 0.042523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-75_0_3_line_6 |  | 3 | 6 | 0.073825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1061-75_0_3_line_7 |  | 5 | 7 | 0.054745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-75_0_3_line_8 |  | 6 | 21 | 0.053411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1061-75_0_3_line_9 |  | 7 | 8 | 0.0084121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-75_0_3_line_10 |  | 9 | 10 | 0.020842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1061-75_0_3_line_11 |  | 11 | 12 | 0.04396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-75_0_3_line_12 |  | 11 | 13 | 0.023278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-75_0_3_line_13 |  | 12 | 14 | 0.00394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-75_0_3_line_14 |  | 12 | 15 | 0.038344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-75_0_3_line_15 |  | 14 | 16 | 0.017316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-75_0_3_line_16 |  | 15 | 17 | 0.02393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-75_0_3_line_17 |  | 17 | 18 | 0.019356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-75_0_3_line_18 |  | 18 | 19 | 0.003756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-75_0_3_line_19 |  | 18 | 20 | 0.0032597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1061-75_0_3_line_20 |  | 19 | 22 | 0.021953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-75_0_3_line_21 |  | 19 | 23 | 0.038178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-75_0_3_line_22 |  | 20 | 21 | 0.024898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-75_0_3_line_23 |  | 22 | 26 | 0.030381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-75_0_3_line_24 |  | 24 | 25 | 0.013038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-75_0_3_line_25 |  | 24 | 26 | 0.017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-75_0_3_line_26 |  | 25 | 27 | 0.052475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-75_0_3_trafo_1 | 0.63 MVA 20/0.4 kV | 28 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2663906.5631 | 1213130.7227 | 2663886.9492 | 1213147.4
1 | 2663906.5631 | 1213130.7227 | 2663887.7897 | 1213116.9551
2 | 2663906.5631 | 1213130.7227 | 2663948.4823 | 1213070.4681
3 | 2663820.8467 | 1213163.5602 | 2663828.7618 | 1213132.4464 | 2663833.5609 | 1213119.8678
4 | 2663887.7897 | 1213116.9551 | 2663833.5609 | 1213119.8678
5 | 2663820.8467 | 1213163.5602 | 2663816.0097 | 1213182.5742 | 2663815.5154 | 1213205.4721
6 | 2663747.9466 | 1213175.2094 | 2663820.8467 | 1213163.5602
7 | 2663839.1303 | 1213206.5946 | 2663822.1783 | 1213228.6908 | 2663815.1209 | 1213223.7456 | 2663815.5154 | 1213205.4721
8 | 2663747.9466 | 1213175.2094 | 2663752.8329 | 1213122.0223
9 | 2663844.2507 | 1213199.9204 | 2663839.1303 | 1213206.5946
10 | 2663948.4823 | 1213070.4681 | 2663929.5299 | 1213061.7964
11 | 2663776.8952 | 1213015.6198 | 2663785.8954 | 1213019.3628 | 2663798.3906 | 1213024.4884 | 2663817.3672 | 1213033.0411
12 | 2663817.3672 | 1213033.0411 | 2663813.1353 | 1213055.9317
13 | 2663773.2264 | 1213014.1575 | 2663774.0887 | 1213014.5002 | 2663776.8952 | 1213015.6198
14 | 2663776.8952 | 1213015.6198 | 2663767.244 | 1213039.3535 | 2663763.7105 | 1213051.5765
15 | 2663773.2264 | 1213014.1575 | 2663769.098 | 1213024.4085 | 2663766.8951 | 1213030.2731
16 | 2663758.3745 | 1213074.8553 | 2663759.9865 | 1213064.458 | 2663763.7105 | 1213051.5765
17 | 2663755.409 | 1213093.9829 | 2663758.3745 | 1213074.8553
18 | 2663751.6768 | 1213093.476 | 2663755.409 | 1213093.9829
19 | 2663755.409 | 1213093.9829 | 2663755.1108 | 1213097.2289
20 | 2663751.6768 | 1213093.476 | 2663729.9193 | 1213090.5505
21 | 2663751.6768 | 1213093.476 | 2663749.4846 | 1213113.7762 | 2663747.8704 | 1213131.462
22 | 2663755.1108 | 1213097.2289 | 2663752.8329 | 1213122.0223
23 | 2663729.9193 | 1213090.5505 | 2663709.1883 | 1213087.763 | 2663707.8493 | 1213079.4214 | 2663707.9636 | 1213078.413
24 | 2663709.9435 | 1213060.942 | 2663711.2295 | 1213049.5947 | 2663711.3561 | 1213047.9811
25 | 2663709.9435 | 1213060.942 | 2663707.9636 | 1213078.413
26 | 2663711.3561 | 1213047.9811 | 2663712.408 | 1213034.5758 | 2663707.7994 | 1213027.2109 | 2663703.1408 | 1213024.5262 | 2663691.583 | 1213019.1217 | 2663679.5105 | 1213017.3274

## bus_geodata
| x | y | coords
0 | 2663886.9492 | 1213147.4
1 | 2663906.5631 | 1213130.7227
2 | 2663833.5609 | 1213119.8678
3 | 2663820.8467 | 1213163.5602
4 | 2663887.7897 | 1213116.9551
5 | 2663815.5154 | 1213205.4721
6 | 2663747.9466 | 1213175.2094
7 | 2663839.1303 | 1213206.5946
8 | 2663844.2507 | 1213199.9204
9 | 2663929.5299 | 1213061.7964
10 | 2663948.4823 | 1213070.4681
11 | 2663817.3672 | 1213033.0411
12 | 2663776.8952 | 1213015.6198
13 | 2663813.1353 | 1213055.9317
14 | 2663773.2264 | 1213014.1575
15 | 2663763.7105 | 1213051.5765
16 | 2663766.8951 | 1213030.2731
17 | 2663758.3745 | 1213074.8553
18 | 2663755.409 | 1213093.9829
19 | 2663751.6768 | 1213093.476
20 | 2663755.1108 | 1213097.2289
21 | 2663752.8329 | 1213122.0223
22 | 2663729.9193 | 1213090.5505
23 | 2663747.8704 | 1213131.462
24 | 2663709.9435 | 1213060.942
25 | 2663711.3561 | 1213047.9811
26 | 2663707.9636 | 1213078.413
27 | 2663679.5105 | 1213017.3274
28 | 2663938.123 | 1213188.5187

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99331 | -0.1287 | 0.056042 | 0.014045
1 | 0.99462 | -0.10324 | 0 | 0
2 | 1 | 0 | -0.24598 | -0.06275
3 | 0.99657 | -0.064605 | 0.0090724 | 0.0022738
4 | 0.99612 | -0.074416 | 0.007929 | 0.0019872
5 | 0.99605 | -0.074471 | 0.0043617 | 0.0010931
6 | 0.99175 | -0.15563 | 0.0011419 | 0.00028619
7 | 0.99561 | -0.082988 | 0.0038502 | 0.00096496
8 | 0.99557 | -0.083727 | 0.0049997 | 0.0012531
9 | 0.99339 | -0.12706 | 0.014337 | 0.0035932
10 | 0.99366 | -0.12179 | 0 | 0
11 | 0.97274 | -0.52352 | 0 | 0
12 | 0.97679 | -0.44394 | 0 | 0
13 | 0.97059 | -0.56593 | 0.098685 | 0.024733
14 | 0.97678 | -0.44418 | 0 | 0
15 | 0.98045 | -0.37268 | 0.002393 | 0.00059974
16 | 0.97673 | -0.44527 | 0.0034276 | 0.00085904
17 | 0.98279 | -0.32744 | 0.0011041 | 0.00027672
18 | 0.9847 | -0.29062 | 0 | 0
19 | 0.9846 | -0.29257 | 0 | 0
20 | 0.98511 | -0.28275 | 0.0030043 | 0.00075295
21 | 0.9883 | -0.22149 | 0.0012642 | 0.00031684
22 | 0.98409 | -0.30254 | 0.0024875 | 0.00062342
23 | 0.98448 | -0.295 | 0.0035415 | 0.00088758
24 | 0.98313 | -0.32137 | 0.011646 | 0.0029188
25 | 0.98303 | -0.32335 | 0.0028865 | 0.00072343
26 | 0.98345 | -0.315 | 0.0026852 | 0.00067298
27 | 0.98276 | -0.32861 | 0.0055524 | 0.0013916
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.056042 | -0.014045 | 0.05611 | 0.014089 | 6.8048e-05 | 4.3217e-05 | 0.083954 | 0.083954 | 0.083954 | 0.99331 | -0.1287 | 0.99462 | -0.10324 | 23.0642
1 | -0.070463 | -0.017691 | 0.070561 | 0.017753 | 9.7038e-05 | 6.1802e-05 | 0.10543 | 0.10543 | 0.10543 | 0.99462 | -0.10324 | 0.99612 | -0.074416 | 28.9639
2 | 0.014353 | 0.0036024 | -0.014341 | -0.0035952 | 1.2685e-05 | 7.1671e-06 | 0.021475 | 0.021475 | 0.021475 | 0.99462 | -0.10324 | 0.99366 | -0.12179 | 5.8999
3 | 0.16556 | 0.042831 | -0.16504 | -0.042499 | 0.00052058 | 0.00033198 | 0.24684 | 0.24684 | 0.24684 | 1 | 0 | 0.99657 | -0.064605 | 33.9065
4 | 0.07877 | 0.019919 | -0.078489 | -0.01974 | 0.00028008 | 0.00017854 | 0.11727 | 0.11727 | 0.11727 | 1 | 0 | 0.99612 | -0.074416 | 32.2179
5 | 0.013222 | 0.0033162 | -0.013215 | -0.0033127 | 6.2154e-06 | 3.4241e-06 | 0.019743 | 0.019743 | 0.019743 | 0.99657 | -0.064605 | 0.99605 | -0.074471 | 5.4239
6 | 0.14275 | 0.03691 | -0.14212 | -0.036507 | 0.00063126 | 0.00040209 | 0.21355 | 0.21355 | 0.21355 | 0.99657 | -0.064605 | 0.99175 | -0.15563 | 29.334
7 | 0.0088537 | 0.0022196 | -0.0088501 | -0.002218 | 3.5917e-06 | 1.5865e-06 | 0.013227 | 0.013227 | 0.013227 | 0.99605 | -0.074471 | 0.99561 | -0.082988 | 3.6338
8 | 0.14098 | 0.036221 | -0.14053 | -0.035935 | 0.00044941 | 0.00028625 | 0.21184 | 0.21184 | 0.21184 | 0.99175 | -0.15563 | 0.9883 | -0.22149 | 29.0987
9 | 0.0049999 | 0.0012531 | -0.0049997 | -0.0012531 | 1.7616e-07 | 3.3494e-09 | 0.0074727 | 0.0074728 | 0.0074728 | 0.99561 | -0.082988 | 0.99557 | -0.083727 | 2.053
10 | -0.014337 | -0.0035932 | 0.014341 | 0.0035952 | 3.6046e-06 | 2.0371e-06 | 0.021476 | 0.021475 | 0.021476 | 0.99339 | -0.12706 | 0.99366 | -0.12179 | 5.8999
11 | -0.098885 | -0.02486 | 0.099262 | 0.025101 | 0.00037734 | 0.00024095 | 0.15129 | 0.15129 | 0.15129 | 0.97274 | -0.52352 | 0.97679 | -0.44394 | 41.5642
12 | 0.098885 | 0.02486 | -0.098685 | -0.024733 | 0.00019981 | 0.00012759 | 0.15129 | 0.15129 | 0.15129 | 0.97274 | -0.52352 | 0.97059 | -0.56593 | 41.5642
13 | 0.0034278 | 0.00085891 | -0.0034278 | -0.00085894 | 4.0287e-08 | -2.3534e-08 | 0.0052218 | 0.0052218 | 0.0052218 | 0.97679 | -0.44394 | 0.97678 | -0.44418 | 1.4346
14 | -0.10269 | -0.02596 | 0.10304 | 0.026185 | 0.00035225 | 0.00022496 | 0.15652 | 0.15652 | 0.15652 | 0.97679 | -0.44394 | 0.98045 | -0.37268 | 42.9987
15 | 0.0034278 | 0.00085894 | -0.0034276 | -0.00085904 | 1.7706e-07 | -1.0341e-07 | 0.0052218 | 0.0052219 | 0.0052219 | 0.97678 | -0.44418 | 0.97673 | -0.44527 | 1.4346
16 | -0.10544 | -0.026785 | 0.10567 | 0.026932 | 0.00023015 | 0.000147 | 0.16015 | 0.16015 | 0.16015 | 0.98045 | -0.37268 | 0.98279 | -0.32744 | 43.9964
17 | -0.10677 | -0.027209 | 0.10696 | 0.02733 | 0.00019007 | 0.0001214 | 0.16182 | 0.16182 | 0.16182 | 0.98279 | -0.32744 | 0.9847 | -0.29062 | 44.4556
18 | 0.028836 | 0.0072391 | -0.028833 | -0.0072375 | 2.675e-06 | 1.6642e-06 | 0.04358 | 0.04358 | 0.04358 | 0.9847 | -0.29062 | 0.9846 | -0.29257 | 11.9724
19 | -0.1358 | -0.034569 | 0.13585 | 0.034602 | 5.157e-05 | 3.2964e-05 | 0.2054 | 0.2054 | 0.2054 | 0.9847 | -0.29062 | 0.98511 | -0.28275 | 56.4279
20 | 0.025292 | 0.0063501 | -0.025279 | -0.0063427 | 1.203e-05 | 7.4202e-06 | 0.038227 | 0.038227 | 0.038227 | 0.9846 | -0.29257 | 0.98409 | -0.30254 | 10.5019
21 | 0.0035419 | 0.00088736 | -0.0035415 | -0.00088758 | 4.1021e-07 | -2.2296e-07 | 0.0053527 | 0.0053529 | 0.0053529 | 0.9846 | -0.29257 | 0.98448 | -0.295 | 1.4706
22 | -0.13885 | -0.035355 | 0.13926 | 0.035618 | 0.00041149 | 0.00026304 | 0.20994 | 0.20994 | 0.20994 | 0.98511 | -0.28275 | 0.9883 | -0.22149 | 57.6746
23 | 0.022792 | 0.0057193 | -0.022778 | -0.005711 | 1.3533e-05 | 8.2756e-06 | 0.034466 | 0.034466 | 0.034466 | 0.98409 | -0.30254 | 0.98345 | -0.315 | 9.4686
24 | 0.0084411 | 0.0021156 | -0.0084403 | -0.0021152 | 7.981e-07 | 3.4547e-07 | 0.012776 | 0.012776 | 0.012776 | 0.98313 | -0.32137 | 0.98303 | -0.32335 | 3.5099
25 | -0.020087 | -0.0050343 | 0.020093 | 0.005038 | 6.0947e-06 | 3.6776e-06 | 0.030403 | 0.030403 | 0.030403 | 0.98313 | -0.32137 | 0.98345 | -0.315 | 8.3525
26 | 0.0055538 | 0.0013918 | -0.0055524 | -0.0013916 | 1.3908e-06 | 2.2503e-07 | 0.0084068 | 0.0084071 | 0.0084071 | 0.98303 | -0.32335 | 0.98276 | -0.32861 | 2.3096

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31491 | 0.080026

## res_load
| p_mw | q_mvar
0 | 0.056042 | 0.014045
1 | 0.06893 | 0.017275
2 | 0.0090724 | 0.0022738
3 | 0.007929 | 0.0019872
4 | 0.0043617 | 0.0010931
5 | 0.0011419 | 0.00028619
6 | 0.0038502 | 0.00096496
7 | 0.0049997 | 0.0012531
8 | 0.014337 | 0.0035932
9 | 0.098685 | 0.024733
10 | 0.002393 | 0.00059974
11 | 0.0034276 | 0.00085904
12 | 0.0011041 | 0.00027672
13 | 0.0030043 | 0.00075295
14 | 0.0012642 | 0.00031684
15 | 0.0024875 | 0.00062342
16 | 0.0035415 | 0.00088758
17 | 0.011646 | 0.0029188
18 | 0.0028865 | 0.00072343
19 | 0.0026852 | 0.00067298
20 | 0.0055524 | 0.0013916

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1