## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-83_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-83_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-83_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1061-83_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1061-83_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_1061-83_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1061-83_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1061-83_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1061-83_0_4_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_1061-83_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_1061-83_0_4_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1061-83_0_4_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1061-83_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1061-83_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1061-83_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1061-83_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1061-83_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1061-83_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1061-83_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1061-83_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1061-83_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1061-83_0_4_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_1061-83_0_4_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_1061-83_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1061-83_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_1061-83_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1061-83_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1061-83_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1061-83_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1061-83_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1061-83_0_4_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1061-83_0_4_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_1061-83_0_4_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1061-83_0_4_node_38 | 0.4 | n |  | TRUE
34 | bus_MV_213_0_node_148 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-83_0_4_load_0 | 0 | 0.019886 | 0.004984 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-83_0_4_load_12 | 4 | 0.012098 | 0.0030321 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-83_0_4_load_17 | 6 | 0.086161 | 0.021594 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-83_0_4_load_30 | 9 | 0.0058441 | 0.0014647 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-83_0_4_load_13 | 10 | 0.019388 | 0.0048592 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-83_0_4_load_28 | 12 | 0.0069062 | 0.0017309 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-83_0_4_load_29 | 13 | 0.018065 | 0.0045275 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-83_0_4_load_25 | 14 | 0.0076024 | 0.0019053 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-83_0_4_load_6 | 15 | 0.015679 | 0.0039295 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-83_0_4_load_9 | 18 | 0.01624 | 0.0040702 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-83_0_4_load_10 | 19 | 0.0067662 | 0.0016958 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-83_0_4_load_11 | 20 | 0.016886 | 0.004232 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-83_0_4_load_33 | 21 | 0.013578 | 0.003403 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-83_0_4_load_32 | 24 | 0.0054121 | 0.0013564 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-83_0_4_load_16 | 25 | 0.044132 | 0.01106 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-83_0_4_load_14 | 26 | 0.0039755 | 0.00099636 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1061-83_0_4_load_24 | 27 | 0.0061406 | 0.001539 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1061-83_0_4_load_35 | 29 | 0.017802 | 0.0044615 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1061-83_0_4_load_34 | 30 | 0.015563 | 0.0039005 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1061-83_0_4_load_37 | 32 | 0.012579 | 0.0031526 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1061-83_0_4_load_38 | 33 | 0.0044348 | 0.0011115 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-83_0_4_line_0 |  | 0 | 1 | 0.032239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-83_0_4_line_1 |  | 1 | 2 | 0.007867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-83_0_4_line_2 |  | 1 | 3 | 0.034742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1061-83_0_4_line_3 |  | 2 | 4 | 0.014297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1061-83_0_4_line_4 |  | 3 | 5 | 0.044223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-83_0_4_line_5 |  | 5 | 6 | 0.006297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-83_0_4_line_6 |  | 6 | 7 | 0.044986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1061-83_0_4_line_7 |  | 7 | 10 | 0.033072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1061-83_0_4_line_8 |  | 7 | 8 | 0.033075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-83_0_4_line_9 |  | 8 | 9 | 0.040974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-83_0_4_line_10 |  | 10 | 26 | 0.012052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1061-83_0_4_line_11 |  | 11 | 12 | 0.017985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1061-83_0_4_line_12 |  | 11 | 13 | 0.045361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-83_0_4_line_13 |  | 11 | 14 | 0.056284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-83_0_4_line_14 |  | 12 | 24 | 0.026772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-83_0_4_line_15 |  | 14 | 27 | 0.053017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-83_0_4_line_16 |  | 15 | 16 | 0.042016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1061-83_0_4_line_17 |  | 15 | 17 | 0.018303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1061-83_0_4_line_18 |  | 16 | 18 | 0.011721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1061-83_0_4_line_19 |  | 16 | 19 | 0.022417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1061-83_0_4_line_20 |  | 17 | 20 | 0.020169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-83_0_4_line_21 |  | 18 | 21 | 0.047201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-83_0_4_line_22 |  | 19 | 22 | 0.012813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1061-83_0_4_line_23 |  | 21 | 23 | 0.027764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-83_0_4_line_24 |  | 22 | 24 | 0.01114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-83_0_4_line_25 |  | 22 | 25 | 0.03391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1061-83_0_4_line_26 |  | 23 | 28 | 0.055973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-83_0_4_line_27 |  | 25 | 26 | 0.01371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1061-83_0_4_line_28 |  | 28 | 29 | 0.054267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1061-83_0_4_line_29 |  | 29 | 30 | 0.032429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1061-83_0_4_line_30 |  | 30 | 31 | 0.021878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1061-83_0_4_line_31 |  | 31 | 32 | 0.010019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1061-83_0_4_line_32 |  | 32 | 33 | 0.023216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-83_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 34 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2667207.1876 | 1211992.6529 | 2667174.97 | 1211991.4755
1 | 2667215.0708 | 1211992.9863 | 2667207.1876 | 1211992.6529
2 | 2667207.1876 | 1211992.6529 | 2667207.1889 | 1211991.1853 | 2667207.2094 | 1211986.6716 | 2667229.3784 | 1211986.9215 | 2667230.4471 | 1211980.4184
3 | 2667215.0708 | 1211992.9863 | 2667214.9051 | 1211996.9091 | 2667214.3871 | 1212007.2666
4 | 2667230.4471 | 1211980.4184 | 2667240.3894 | 1211980.7529 | 2667241.7718 | 1211980.8018 | 2667257.5351 | 1211981.0797 | 2667268.1904 | 1211981.5334 | 2667268.056 | 1211983.3441 | 2667267.7348 | 1211987.5653 | 2667267.7074 | 1211987.9764
5 | 2667267.7074 | 1211987.9764 | 2667267.6567 | 1211989.0987 | 2667267.479 | 1211993.3994 | 2667267.4389 | 1211994.2661
6 | 2667267.4389 | 1211994.2661 | 2667292.5109 | 1211995.1383 | 2667297.9647 | 1211995.2888 | 2667312.5339 | 1211995.6756
7 | 2667312.5339 | 1211995.6756 | 2667311.0289 | 1212021.2967 | 2667310.2914 | 1212028.6671
8 | 2667312.5339 | 1211995.6756 | 2667312.9654 | 1211988.4093 | 2667322.8405 | 1211988.6431 | 2667320.8846 | 1211982.8618 | 2667317.7375 | 1211973.565
9 | 2667317.7375 | 1211973.565 | 2667276.7906 | 1211972.0811
10 | 2667310.2914 | 1212028.6671 | 2667309.0914 | 1212040.6594
11 | 2667356.3873 | 1212108.3403 | 2667351.9346 | 1212108.3568 | 2667345.3242 | 1212106.3476 | 2667339.3053 | 1212103.5836
12 | 2667356.3873 | 1212108.3403 | 2667358.4641 | 1212100.0475 | 2667358.1784 | 1212084.9794 | 2667358.2324 | 1212068.0918 | 2667358.0918 | 1212063.2405
13 | 2667356.3873 | 1212108.3403 | 2667355.3692 | 1212112.3758 | 2667355.9992 | 1212113.1056 | 2667358.7455 | 1212115.4936 | 2667359.497 | 1212116.903 | 2667360.1526 | 1212119.4008 | 2667359.89 | 1212122.4664 | 2667356.4221 | 1212132.1666 | 2667346.305 | 1212155.4002 | 2667344.4862 | 1212159.6475
14 | 2667314.9758 | 1212092.4112 | 2667339.3053 | 1212103.5836
15 | 2667323.5193 | 1212208.3428 | 2667334.2324 | 1212183.5925 | 2667344.4862 | 1212159.6475
16 | 2667270.8308 | 1212078.8568 | 2667229.3543 | 1212072.1472
17 | 2667211.2862 | 1212069.2243 | 2667229.3543 | 1212072.1472
18 | 2667270.8308 | 1212078.8568 | 2667259.9878 | 1212079.5684 | 2667259.1434 | 1212079.4371
19 | 2667270.8308 | 1212078.8568 | 2667292.7013 | 1212083.7757
20 | 2667211.2862 | 1212069.2243 | 2667191.3266 | 1212066.3276
21 | 2667212.482 | 1212072.3246 | 2667220.4327 | 1212073.4188 | 2667259.1434 | 1212079.4371
22 | 2667304.7678 | 1212087.9563 | 2667297.0614 | 1212084.7563 | 2667292.7013 | 1212083.7757
23 | 2667184.9569 | 1212068.6941 | 2667196.0576 | 1212070.0644 | 2667212.482 | 1212072.3246
24 | 2667304.7678 | 1212087.9563 | 2667310.1524 | 1212090.1962 | 2667314.9758 | 1212092.4112
25 | 2667304.7678 | 1212087.9563 | 2667306.4447 | 1212082.1049 | 2667308.1108 | 1212054.3319
26 | 2667166.6551 | 1212104.2545 | 2667166.8305 | 1212103.5227 | 2667167.0943 | 1212102.3583 | 2667172.8239 | 1212103.6569 | 2667173.2639 | 1212101.0158 | 2667170.8778 | 1212100.3663 | 2667173.4593 | 1212082.9957 | 2667183.0326 | 1212084.3821 | 2667184.6273 | 1212072.993 | 2667184.9569 | 1212068.6941
27 | 2667308.1108 | 1212054.3319 | 2667308.6909 | 1212044.6626 | 2667309.0914 | 1212040.6594
28 | 2667166.6551 | 1212104.2545 | 2667199.0292 | 1212112.4797 | 2667218.929 | 1212118.7502
29 | 2667249.6599 | 1212129.0472 | 2667245.6587 | 1212127.3143 | 2667227.0957 | 1212121.3236 | 2667218.929 | 1212118.7502
30 | 2667267.5818 | 1212141.2256 | 2667261.9212 | 1212135.8362 | 2667255.0421 | 1212131.3781 | 2667249.6599 | 1212129.0472
31 | 2667267.5818 | 1212141.2256 | 2667271.5134 | 1212144.9611 | 2667274.255 | 1212148.6493
32 | 2667283.5456 | 1212169.5115 | 2667282.0012 | 1212161.5785 | 2667278.3393 | 1212154.1438 | 2667274.255 | 1212148.6493

## bus_geodata
| x | y | coords
0 | 2667174.97 | 1211991.4755
1 | 2667207.1876 | 1211992.6529
2 | 2667215.0708 | 1211992.9863
3 | 2667230.4471 | 1211980.4184
4 | 2667214.3871 | 1212007.2666
5 | 2667267.7074 | 1211987.9764
6 | 2667267.4389 | 1211994.2661
7 | 2667312.5339 | 1211995.6756
8 | 2667317.7375 | 1211973.565
9 | 2667276.7906 | 1211972.0811
10 | 2667310.2914 | 1212028.6671
11 | 2667356.3873 | 1212108.3403
12 | 2667339.3053 | 1212103.5836
13 | 2667358.0918 | 1212063.2405
14 | 2667344.4862 | 1212159.6475
15 | 2667229.3543 | 1212072.1472
16 | 2667270.8308 | 1212078.8568
17 | 2667211.2862 | 1212069.2243
18 | 2667259.1434 | 1212079.4371
19 | 2667292.7013 | 1212083.7757
20 | 2667191.3266 | 1212066.3276
21 | 2667212.482 | 1212072.3246
22 | 2667304.7678 | 1212087.9563
23 | 2667184.9569 | 1212068.6941
24 | 2667314.9758 | 1212092.4112
25 | 2667308.1108 | 1212054.3319
26 | 2667309.0914 | 1212040.6594
27 | 2667323.5193 | 1212208.3428
28 | 2667166.6551 | 1212104.2545
29 | 2667218.929 | 1212118.7502
30 | 2667249.6599 | 1212129.0472
31 | 2667267.5818 | 1212141.2256
32 | 2667274.255 | 1212148.6493
33 | 2667283.5456 | 1212169.5115
34 | 2667304.7678 | 1212087.9563

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97958 | -0.39378 | 0.019886 | 0.004984
1 | 0.98018 | -0.38214 | 0 | 0
2 | 0.98009 | -0.38387 | 0 | 0
3 | 0.98121 | -0.362 | 0 | 0
4 | 0.97993 | -0.38701 | 0.012098 | 0.0030321
5 | 0.98251 | -0.33643 | 0 | 0
6 | 0.9827 | -0.33279 | 0.086161 | 0.021594
7 | 0.98761 | -0.23734 | 0 | 0
8 | 0.98743 | -0.24079 | 0 | 0
9 | 0.98721 | -0.24508 | 0.0058441 | 0.0014647
10 | 0.9914 | -0.16434 | 0.019388 | 0.0048592
11 | 0.9942 | -0.11092 | 0 | 0
12 | 0.99472 | -0.10084 | 0.0069062 | 0.0017309
13 | 0.99345 | -0.12538 | 0.018065 | 0.0045275
14 | 0.99349 | -0.12457 | 0.0076024 | 0.0019053
15 | 0.99876 | -0.023878 | 0.015679 | 0.0039295
16 | 1 | 0 | -0.36019 | -0.091167
17 | 0.99848 | -0.02928 | 0 | 0
18 | 0.99914 | -0.016399 | 0.01624 | 0.0040702
19 | 0.9975 | -0.047473 | 0.0067662 | 0.0016958
20 | 0.99817 | -0.035236 | 0.016886 | 0.004232
21 | 0.99638 | -0.069259 | 0.013578 | 0.003403
22 | 0.99612 | -0.073953 | 0 | 0
23 | 0.99509 | -0.093851 | 0 | 0
24 | 0.99567 | -0.082593 | 0.0054121 | 0.0013564
25 | 0.99313 | -0.13116 | 0.044132 | 0.01106
26 | 0.9922 | -0.14903 | 0.0039755 | 0.00099636
27 | 0.9932 | -0.13032 | 0.0061406 | 0.001539
28 | 0.99251 | -0.14362 | 0 | 0
29 | 0.99 | -0.19212 | 0.017802 | 0.0044615
30 | 0.98903 | -0.21092 | 0.015563 | 0.0039005
31 | 0.98869 | -0.21756 | 0 | 0
32 | 0.98854 | -0.2206 | 0.012579 | 0.0031526
33 | 0.98844 | -0.22244 | 0.0044348 | 0.0011115
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.019886 | -0.004984 | 0.019897 | 0.0049907 | 1.1032e-05 | 6.6544e-06 | 0.030208 | 0.030208 | 0.030208 | 0.97958 | -0.39378 | 0.98018 | -0.38214 | 8.2989
1 | 0.012101 | 0.0030336 | -0.0121 | -0.003033 | 9.9563e-07 | 5.3805e-07 | 0.018371 | 0.018371 | 0.018371 | 0.98018 | -0.38214 | 0.98009 | -0.38387 | 5.0469
2 | -0.031998 | -0.0080242 | 0.032029 | 0.0080435 | 3.0745e-05 | 1.9239e-05 | 0.048579 | 0.048579 | 0.048579 | 0.98018 | -0.38214 | 0.98121 | -0.362 | 13.3458
3 | 0.0121 | 0.003033 | -0.012098 | -0.0030321 | 1.8094e-06 | 9.7785e-07 | 0.018371 | 0.018371 | 0.018371 | 0.98009 | -0.38387 | 0.97993 | -0.38701 | 5.0469
4 | -0.032029 | -0.0080435 | 0.032068 | 0.008068 | 3.9135e-05 | 2.4487e-05 | 0.048579 | 0.048578 | 0.048579 | 0.98121 | -0.362 | 0.98251 | -0.33643 | 13.3458
5 | -0.032068 | -0.008068 | 0.032074 | 0.0080715 | 5.5725e-06 | 3.4866e-06 | 0.048578 | 0.048578 | 0.048578 | 0.98251 | -0.33643 | 0.9827 | -0.33279 | 13.3457
6 | -0.11823 | -0.029665 | 0.11878 | 0.030011 | 0.00054079 | 0.00034553 | 0.17904 | 0.17904 | 0.17904 | 0.9827 | -0.33279 | 0.98761 | -0.23734 | 49.1879
7 | -0.12462 | -0.031476 | 0.12506 | 0.031756 | 0.00043765 | 0.00027967 | 0.18785 | 0.18785 | 0.18785 | 0.98761 | -0.23734 | 0.9914 | -0.16434 | 51.6078
8 | 0.0058463 | 0.0014651 | -0.0058453 | -0.0014649 | 9.6237e-07 | 1.9276e-07 | 0.0088085 | 0.0088086 | 0.0088086 | 0.98761 | -0.23734 | 0.98743 | -0.24079 | 2.42
9 | 0.0058453 | 0.0014649 | -0.0058441 | -0.0014647 | 1.1922e-06 | 2.3903e-07 | 0.0088086 | 0.0088088 | 0.0088088 | 0.98743 | -0.24079 | 0.98721 | -0.24508 | 2.42
10 | -0.14445 | -0.036615 | 0.14455 | 0.036683 | 0.00010636 | 6.7762e-05 | 0.21695 | 0.21695 | 0.21695 | 0.9914 | -0.16434 | 0.9922 | -0.14903 | 29.8012
11 | -0.031831 | -0.0079846 | 0.031846 | 0.0079941 | 1.5309e-05 | 9.5645e-06 | 0.047644 | 0.047644 | 0.047644 | 0.9942 | -0.11092 | 0.99472 | -0.10084 | 13.0889
12 | 0.018077 | 0.0045349 | -0.018065 | -0.0045275 | 1.2454e-05 | 7.3826e-06 | 0.027058 | 0.027058 | 0.027058 | 0.9942 | -0.11092 | 0.99345 | -0.12538 | 7.4335
13 | 0.013754 | 0.0034497 | -0.013745 | -0.0034447 | 8.9447e-06 | 4.9952e-06 | 0.020586 | 0.020586 | 0.020586 | 0.9942 | -0.11092 | 0.99349 | -0.12457 | 5.6555
14 | -0.038752 | -0.009725 | 0.038786 | 0.0097462 | 3.3744e-05 | 2.1248e-05 | 0.057975 | 0.057975 | 0.057975 | 0.99472 | -0.10084 | 0.99567 | -0.082593 | 15.9271
15 | 0.0061423 | 0.0015394 | -0.0061406 | -0.001539 | 1.6827e-06 | 3.9059e-07 | 0.0091996 | 0.0091999 | 0.0091999 | 0.99349 | -0.12457 | 0.9932 | -0.13032 | 2.5274
16 | -0.032574 | -0.0081668 | 0.032611 | 0.00819 | 3.711e-05 | 2.32e-05 | 0.048532 | 0.048531 | 0.048532 | 0.99876 | -0.023878 | 1 | 0 | 13.3328
17 | 0.016895 | 0.0042373 | -0.016891 | -0.0042348 | 4.3491e-06 | 2.5439e-06 | 0.025172 | 0.025172 | 0.025172 | 0.99876 | -0.023878 | 0.99848 | -0.02928 | 6.9155
18 | 0.080759 | 0.020455 | -0.080695 | -0.020414 | 6.3552e-05 | 4.052e-05 | 0.12025 | 0.12025 | 0.12025 | 1 | 0 | 0.99914 | -0.016399 | 33.0346
19 | 0.24517 | 0.062522 | -0.24461 | -0.062163 | 0.00056056 | 0.00035817 | 0.36519 | 0.36519 | 0.36519 | 1 | 0 | 0.9975 | -0.047473 | 50.1638
20 | 0.016891 | 0.0042348 | -0.016886 | -0.004232 | 4.7924e-06 | 2.8034e-06 | 0.025172 | 0.025172 | 0.025172 | 0.99848 | -0.02928 | 0.99817 | -0.035236 | 6.9155
21 | 0.064455 | 0.016344 | -0.064291 | -0.01624 | 0.00016333 | 0.00010391 | 0.096059 | 0.09606 | 0.09606 | 0.99914 | -0.016399 | 0.99638 | -0.069259 | 26.39
22 | 0.23784 | 0.060468 | -0.23754 | -0.060274 | 0.00030295 | 0.00019355 | 0.3551 | 0.3551 | 0.3551 | 0.9975 | -0.047473 | 0.99612 | -0.073953 | 48.7774
23 | 0.050713 | 0.012837 | -0.050653 | -0.012799 | 5.9792e-05 | 3.7906e-05 | 0.075782 | 0.075782 | 0.075782 | 0.99638 | -0.069259 | 0.99509 | -0.093851 | 20.8191
24 | 0.044216 | 0.011114 | -0.044198 | -0.011103 | 1.8231e-05 | 1.1523e-05 | 0.066063 | 0.066063 | 0.066063 | 0.99612 | -0.073953 | 0.99567 | -0.082593 | 18.1491
25 | 0.19332 | 0.04916 | -0.19279 | -0.048821 | 0.00053117 | 0.00033907 | 0.28904 | 0.28904 | 0.28904 | 0.99612 | -0.073953 | 0.99313 | -0.13116 | 39.7029
26 | 0.050653 | 0.012799 | -0.050533 | -0.012723 | 0.00012054 | 7.6422e-05 | 0.075782 | 0.075782 | 0.075782 | 0.99509 | -0.093851 | 0.99251 | -0.14362 | 20.8192
27 | 0.14866 | 0.03776 | -0.14853 | -0.037679 | 0.00012774 | 8.1396e-05 | 0.22291 | 0.22291 | 0.22291 | 0.99313 | -0.13116 | 0.9922 | -0.14903 | 30.6201
28 | 0.050533 | 0.012723 | -0.050416 | -0.012649 | 0.00011687 | 7.4097e-05 | 0.075782 | 0.075782 | 0.075782 | 0.99251 | -0.14362 | 0.99 | -0.19212 | 20.8193
29 | 0.032614 | 0.0081874 | -0.032585 | -0.0081691 | 2.9229e-05 | 1.829e-05 | 0.049026 | 0.049026 | 0.049026 | 0.99 | -0.19212 | 0.98903 | -0.21092 | 13.4686
30 | 0.017022 | 0.0042686 | -0.017017 | -0.0042654 | 5.3814e-06 | 3.1634e-06 | 0.025611 | 0.025611 | 0.025611 | 0.98903 | -0.21092 | 0.98869 | -0.21756 | 7.0359
31 | 0.017017 | 0.0042654 | -0.017014 | -0.004264 | 2.4643e-06 | 1.4487e-06 | 0.025611 | 0.025611 | 0.025611 | 0.98869 | -0.21756 | 0.98854 | -0.2206 | 7.036
32 | 0.0044351 | 0.0011114 | -0.0044348 | -0.0011115 | 3.8803e-07 | -4.9265e-08 | 0.0066761 | 0.0066762 | 0.0066762 | 0.98854 | -0.2206 | 0.98844 | -0.22244 | 1.8341

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36019 | 0.091167

## res_load
| p_mw | q_mvar
0 | 0.019886 | 0.004984
1 | 0.012098 | 0.0030321
2 | 0.086161 | 0.021594
3 | 0.0058441 | 0.0014647
4 | 0.019388 | 0.0048592
5 | 0.0069062 | 0.0017309
6 | 0.018065 | 0.0045275
7 | 0.0076024 | 0.0019053
8 | 0.015679 | 0.0039295
9 | 0.01624 | 0.0040702
10 | 0.0067662 | 0.0016958
11 | 0.016886 | 0.004232
12 | 0.013578 | 0.003403
13 | 0.0054121 | 0.0013564
14 | 0.044132 | 0.01106
15 | 0.0039755 | 0.00099636
16 | 0.0061406 | 0.001539
17 | 0.017802 | 0.0044615
18 | 0.015563 | 0.0039005
19 | 0.012579 | 0.0031526
20 | 0.0044348 | 0.0011115

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1