## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1061-87_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1061-87_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1061-87_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1061-87_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1061-87_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1061-87_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1061-87_0_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1061-87_0_3_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1061-87_0_3_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_1061-87_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1061-87_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1061-87_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1061-87_0_3_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1061-87_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1061-87_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1061-87_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1061-87_0_3_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_1061-87_0_3_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1061-87_0_3_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1061-87_0_3_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1061-87_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1061-87_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1061-87_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1061-87_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1061-87_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1061-87_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1061-87_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1061-87_0_3_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1061-87_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1061-87_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_MV_213_0_node_110 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1061-87_0_3_load_0 | 0 | 0.011663 | 0.002923 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1061-87_0_3_load_9 | 5 | 0.022781 | 0.0057095 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1061-87_0_3_load_20 | 7 | 0.020809 | 0.0052152 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1061-87_0_3_load_32 | 8 | 0.020295 | 0.0050864 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1061-87_0_3_load_21 | 11 | 0.019928 | 0.0049945 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1061-87_0_3_load_33 | 15 | 0.049791 | 0.012479 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1061-87_0_3_load_28 | 16 | 0.05372 | 0.013463 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1061-87_0_3_load_25 | 17 | 0.0072339 | 0.001813 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1061-87_0_3_load_23 | 18 | 0.0066574 | 0.0016685 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1061-87_0_3_load_30 | 19 | 0.0093587 | 0.0023455 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1061-87_0_3_load_12 | 23 | 0.032952 | 0.0082585 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1061-87_0_3_load_18 | 25 | 0.060518 | 0.015167 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1061-87_0_3_load_29 | 26 | 0.029418 | 0.0073728 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1061-87_0_3_load_26 | 27 | 0.022624 | 0.0056702 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1061-87_0_3_load_19 | 28 | 0.014001 | 0.003509 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1061-87_0_3_load_27 | 29 | 0.029972 | 0.0075116 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1061-87_0_3_line_0 |  | 0 | 1 | 0.012827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1061-87_0_3_line_1 |  | 0 | 2 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1061-87_0_3_line_2 |  | 1 | 3 | 0.089148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1061-87_0_3_line_3 |  | 1 | 4 | 0.064125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1061-87_0_3_line_4 |  | 2 | 5 | 0.025231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1061-87_0_3_line_5 |  | 3 | 6 | 0.007295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1061-87_0_3_line_6 |  | 3 | 7 | 0.036415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1061-87_0_3_line_7 |  | 4 | 8 | 0.029499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1061-87_0_3_line_8 |  | 6 | 17 | 0.0068512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1061-87_0_3_line_9 |  | 6 | 18 | 0.016438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1061-87_0_3_line_10 |  | 7 | 11 | 0.032125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1061-87_0_3_line_11 |  | 8 | 15 | 0.046245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1061-87_0_3_line_12 |  | 9 | 10 | 0.004393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1061-87_0_3_line_13 |  | 9 | 11 | 0.042251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1061-87_0_3_line_14 |  | 10 | 12 | 0.05455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1061-87_0_3_line_15 |  | 12 | 19 | 0.062325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1061-87_0_3_line_16 |  | 13 | 14 | 0.013583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1061-87_0_3_line_17 |  | 13 | 15 | 0.049077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1061-87_0_3_line_18 |  | 14 | 16 | 0.05091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1061-87_0_3_line_19 |  | 16 | 29 | 0.038395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1061-87_0_3_line_20 |  | 20 | 21 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1061-87_0_3_line_21 |  | 20 | 22 | 0.085401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1061-87_0_3_line_22 |  | 20 | 23 | 0.025775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1061-87_0_3_line_23 |  | 21 | 26 | 0.019218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1061-87_0_3_line_24 |  | 21 | 27 | 0.038133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1061-87_0_3_line_25 |  | 22 | 28 | 0.011982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1061-87_0_3_line_26 |  | 23 | 24 | 0.031244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1061-87_0_3_line_27 |  | 24 | 25 | 0.02859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1061-87_0_3_line_28 |  | 27 | 29 | 0.038494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1061-87_0_3_trafo_26 | 0.63 MVA 20/0.4 kV | 30 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2667120.9126 | 1212056.4879 | 2667108.4512 | 1212053.4468
1 | 2667096.9454 | 1212050.637 | 2667105.1517 | 1212052.6416 | 2667108.4512 | 1212053.4468
2 | 2667044.5491 | 1212061.3769 | 2667047.6812 | 1212054.4745 | 2667051.7562 | 1212050.2065 | 2667054.3839 | 1212049.6468 | 2667058.588 | 1212048.7601 | 2667063.3349 | 1212049.614 | 2667070.1401 | 1212052.559 | 2667073.6487 | 1212054.0661 | 2667079.0401 | 1212056.3948 | 2667084.1518 | 1212057.9087 | 2667087.9019 | 1212058.8848 | 2667106.4726 | 1212062.8739 | 2667111.9676 | 1212063.4138 | 2667115.55 | 1212063.0873 | 2667118.2256 | 1212062.3169 | 2667119.7379 | 1212060.9442 | 2667120.1269 | 1212059.4587 | 2667120.9126 | 1212056.4879
3 | 2667120.9126 | 1212056.4879 | 2667120.1269 | 1212059.4587 | 2667112.7941 | 1212058.1643 | 2667111.8159 | 1212057.9865 | 2667102.052 | 1212056.6537 | 2667089.4314 | 1212053.9545 | 2667080.1688 | 1212051.2932 | 2667061.6208 | 1212043.2575
4 | 2667096.9454 | 1212050.637 | 2667097.0621 | 1212025.4115
5 | 2667044.5491 | 1212061.3769 | 2667043.3103 | 1212064.1091 | 2667042.7836 | 1212068.3725
6 | 2667044.5491 | 1212061.3769 | 2667048.2182 | 1212062.7968 | 2667048.6193 | 1212062.9458 | 2667048.3982 | 1212065.0335 | 2667049.0344 | 1212067.242 | 2667050.4097 | 1212069.2698 | 2667052.3287 | 1212070.9146 | 2667067.0784 | 1212076.1726 | 2667073.586 | 1212078.8027
7 | 2667061.6208 | 1212043.2575 | 2667035.5769 | 1212029.4053
8 | 2667042.7836 | 1212068.3725 | 2667035.9417 | 1212068.0176
9 | 2667042.7836 | 1212068.3725 | 2667044.9355 | 1212071.6098 | 2667056.5667 | 1212076.3255
10 | 2667103.6699 | 1212090.0136 | 2667092.0918 | 1212086.2823 | 2667073.586 | 1212078.8027
11 | 2667035.5769 | 1212029.4053 | 2667032.6851 | 1212027.8673 | 2667005.8991 | 1212015.9034 | 2666993.1877 | 1212010.9757
12 | 2667143.767 | 1212103.8077 | 2667144.4998 | 1212100.803 | 2667144.8028 | 1212099.539
13 | 2667144.8028 | 1212099.539 | 2667123.7591 | 1212095.2106 | 2667109.8223 | 1212091.9963 | 2667103.6699 | 1212090.0136
14 | 2667135.3805 | 1212153.5776 | 2667146.9203 | 1212108.5239 | 2667142.8284 | 1212107.5328 | 2667143.0036 | 1212106.8232 | 2667143.767 | 1212103.8077
15 | 2667135.3805 | 1212153.5776 | 2667113.4755 | 1212150.1846 | 2667074.9836 | 1212138.7364
16 | 2666936.3581 | 1211986.9716 | 2666945.5437 | 1211990.4213 | 2666947.223 | 1211993.7978
17 | 2666947.223 | 1211993.7978 | 2666962.7769 | 1211999.1867 | 2666993.1877 | 1212010.9757
18 | 2666936.3581 | 1211986.9716 | 2666937.0499 | 1211984.2333 | 2666937.5428 | 1211982.2931 | 2666951.5784 | 1211983.5069 | 2666978.3141 | 1211985.0857 | 2666983.5253 | 1211985.2391
19 | 2666983.5253 | 1211985.2391 | 2667021.9041 | 1211986.369
20 | 2667098.4925 | 1211988.7716 | 2667098.5433 | 1211987.6381 | 2667098.7401 | 1211982.9708 | 2667098.9505 | 1211977.781 | 2667098.9929 | 1211976.7142
21 | 2667062.3451 | 1211928.8614 | 2667061.5892 | 1211954.8579 | 2667100.1986 | 1211955.9927 | 2667099.8541 | 1211967.7072 | 2667098.9929 | 1211976.7142
22 | 2667098.9929 | 1211976.7142 | 2667078.7266 | 1211976.186 | 2667073.2329 | 1211975.8833
23 | 2667098.4925 | 1211988.7716 | 2667110.8812 | 1211989.1334 | 2667117.7007 | 1211989.3826
24 | 2667098.4925 | 1211988.7716 | 2667069.3417 | 1211987.7654 | 2667060.381 | 1211987.5017
25 | 2667062.3451 | 1211928.8614 | 2667050.3678 | 1211928.5236
26 | 2667042.0119 | 1211974.8169 | 2667059.7123 | 1211975.1383 | 2667073.2329 | 1211975.8833
27 | 2667031.9086 | 1211954.3241 | 2667033.3426 | 1211954.507 | 2667034.9596 | 1211954.6363 | 2667037.4782 | 1211954.9982 | 2667039.546 | 1211955.5773 | 2667040.989 | 1211956.3162 | 2667042.2065 | 1211957.5084 | 2667043.0304 | 1211959.241 | 2667042.4367 | 1211966.7723 | 2667042.0372 | 1211972.5714 | 2667042.0119 | 1211974.8169
28 | 2667021.9041 | 1211986.369 | 2667060.381 | 1211987.5017

## bus_geodata
| x | y | coords
0 | 2667108.4512 | 1212053.4468
1 | 2667120.9126 | 1212056.4879
2 | 2667096.9454 | 1212050.637
3 | 2667044.5491 | 1212061.3769
4 | 2667061.6208 | 1212043.2575
5 | 2667097.0621 | 1212025.4115
6 | 2667042.7836 | 1212068.3725
7 | 2667073.586 | 1212078.8027
8 | 2667035.5769 | 1212029.4053
9 | 2667144.8028 | 1212099.539
10 | 2667143.767 | 1212103.8077
11 | 2667103.6699 | 1212090.0136
12 | 2667135.3805 | 1212153.5776
13 | 2666947.223 | 1211993.7978
14 | 2666936.3581 | 1211986.9716
15 | 2666993.1877 | 1212010.9757
16 | 2666983.5253 | 1211985.2391
17 | 2667035.9417 | 1212068.0176
18 | 2667056.5667 | 1212076.3255
19 | 2667074.9836 | 1212138.7364
20 | 2667098.9929 | 1211976.7142
21 | 2667098.4925 | 1211988.7716
22 | 2667062.3451 | 1211928.8614
23 | 2667073.2329 | 1211975.8833
24 | 2667042.0119 | 1211974.8169
25 | 2667031.9086 | 1211954.3241
26 | 2667117.7007 | 1211989.3826
27 | 2667060.381 | 1211987.5017
28 | 2667050.3678 | 1211928.5236
29 | 2667021.9041 | 1211986.369
30 | 2667098.4925 | 1211988.7716

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97541 | -0.47332 | 0.011663 | 0.002923
1 | 0.97582 | -0.46523 | 0 | 0
2 | 0.97515 | -0.47826 | 0 | 0
3 | 0.97316 | -0.51759 | 0 | 0
4 | 0.97876 | -0.40762 | 0 | 0
5 | 0.97462 | -0.4888 | 0.022781 | 0.0057095
6 | 0.97306 | -0.51945 | 0 | 0
7 | 0.9723 | -0.53439 | 0.020809 | 0.0052152
8 | 0.98011 | -0.38124 | 0.020295 | 0.0050864
9 | 0.9715 | -0.55037 | 0 | 0
10 | 0.97146 | -0.55113 | 0 | 0
11 | 0.97187 | -0.54307 | 0.019928 | 0.0049945
12 | 0.97098 | -0.56057 | 0 | 0
13 | 0.98651 | -0.25719 | 0 | 0
14 | 0.98757 | -0.23671 | 0 | 0
15 | 0.98267 | -0.33155 | 0.049791 | 0.012479
16 | 0.99156 | -0.16034 | 0.05372 | 0.013463
17 | 0.97301 | -0.52036 | 0.0072339 | 0.001813
18 | 0.97296 | -0.52147 | 0.0066574 | 0.0016685
19 | 0.97044 | -0.57136 | 0.0093587 | 0.0023455
20 | 0.99403 | -0.11427 | 0 | 0
21 | 0.99522 | -0.091422 | 0 | 0
22 | 0.99294 | -0.13539 | 0 | 0
23 | 0.99183 | -0.15686 | 0.032952 | 0.0082585
24 | 0.99009 | -0.19043 | 0 | 0
25 | 0.9885 | -0.22124 | 0.060518 | 0.015167
26 | 0.99471 | -0.10138 | 0.029418 | 0.0073728
27 | 1 | 0 | -0.39609 | -0.10092
28 | 0.99279 | -0.13836 | 0.014001 | 0.003509
29 | 0.99551 | -0.085 | 0.029972 | 0.0075116
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034461 | -0.0086427 | 0.034474 | 0.0086511 | 1.3295e-05 | 8.3486e-06 | 0.052573 | 0.052573 | 0.052573 | 0.97541 | -0.47332 | 0.97582 | -0.46523 | 14.4432
1 | 0.022798 | 0.0057198 | -0.022793 | -0.0057165 | 5.373e-06 | 3.291e-06 | 0.034781 | 0.034781 | 0.034781 | 0.97541 | -0.47332 | 0.97515 | -0.47826 | 9.5553
2 | 0.064215 | 0.016176 | -0.064054 | -0.016076 | 0.00016037 | 0.00010042 | 0.09795 | 0.097951 | 0.097951 | 0.97582 | -0.46523 | 0.97316 | -0.51759 | 13.4548
3 | -0.098689 | -0.024827 | 0.098961 | 0.025 | 0.00027242 | 0.00017274 | 0.15052 | 0.15052 | 0.15052 | 0.97582 | -0.46523 | 0.97876 | -0.40762 | 20.6763
4 | 0.022793 | 0.0057165 | -0.022781 | -0.0057095 | 1.1446e-05 | 7.0109e-06 | 0.034781 | 0.034781 | 0.034781 | 0.97515 | -0.47826 | 0.97462 | -0.4888 | 9.5553
5 | 0.013893 | 0.0034825 | -0.013892 | -0.0034818 | 1.2346e-06 | 6.9953e-07 | 0.021244 | 0.021244 | 0.021244 | 0.97316 | -0.51759 | 0.97306 | -0.51945 | 5.8363
6 | 0.050161 | 0.012593 | -0.050121 | -0.012568 | 4.0175e-05 | 2.4808e-05 | 0.076707 | 0.076707 | 0.076707 | 0.97316 | -0.51759 | 0.9723 | -0.53439 | 10.5367
7 | -0.098961 | -0.025 | 0.099086 | 0.025079 | 0.00012532 | 7.946e-05 | 0.15052 | 0.15052 | 0.15052 | 0.97876 | -0.40762 | 0.98011 | -0.38124 | 20.6762
8 | 0.0072342 | 0.0018131 | -0.0072339 | -0.001813 | 3.1442e-07 | 1.1613e-07 | 0.011063 | 0.011063 | 0.011063 | 0.97306 | -0.51945 | 0.97301 | -0.52036 | 3.0392
9 | 0.006658 | 0.0016687 | -0.0066574 | -0.0016685 | 6.3902e-07 | 2.048e-07 | 0.010182 | 0.010182 | 0.010182 | 0.97306 | -0.51945 | 0.97296 | -0.52147 | 2.7971
10 | 0.029312 | 0.007353 | -0.029299 | -0.007346 | 1.2122e-05 | 6.9617e-06 | 0.044861 | 0.044861 | 0.044861 | 0.9723 | -0.53439 | 0.97187 | -0.54307 | 6.1623
11 | -0.11938 | -0.030166 | 0.11967 | 0.030347 | 0.00028512 | 0.00018131 | 0.18133 | 0.18133 | 0.18133 | 0.98011 | -0.38124 | 0.98267 | -0.33155 | 24.9085
12 | 0.0093681 | 0.00235 | -0.0093677 | -0.0023498 | 3.3921e-07 | 1.627e-07 | 0.01435 | 0.01435 | 0.01435 | 0.9715 | -0.55037 | 0.97146 | -0.55113 | 3.9422
13 | -0.0093681 | -0.00235 | 0.0093713 | 0.0023516 | 3.2624e-06 | 1.5646e-06 | 0.01435 | 0.014349 | 0.01435 | 0.9715 | -0.55037 | 0.97187 | -0.54307 | 3.9422
14 | 0.0093677 | 0.0023498 | -0.0093635 | -0.0023478 | 4.2123e-06 | 2.0208e-06 | 0.01435 | 0.01435 | 0.01435 | 0.97146 | -0.55113 | 0.97098 | -0.56057 | 3.9423
15 | 0.0093635 | 0.0023478 | -0.0093587 | -0.0023455 | 4.8128e-06 | 2.3097e-06 | 0.01435 | 0.01435 | 0.01435 | 0.97098 | -0.56057 | 0.97044 | -0.57136 | 3.9423
16 | -0.17006 | -0.043213 | 0.17023 | 0.04332 | 0.00016786 | 0.00010708 | 0.25673 | 0.25673 | 0.25673 | 0.98651 | -0.25719 | 0.98757 | -0.23671 | 35.265
17 | 0.17006 | 0.043213 | -0.16946 | -0.042826 | 0.0006065 | 0.00038691 | 0.25673 | 0.25673 | 0.25673 | 0.98651 | -0.25719 | 0.98267 | -0.33155 | 35.265
18 | -0.17023 | -0.04332 | 0.17086 | 0.043721 | 0.00062915 | 0.00040135 | 0.25673 | 0.25673 | 0.25673 | 0.98757 | -0.23671 | 0.99156 | -0.16034 | 35.265
19 | -0.22458 | -0.057184 | 0.2254 | 0.057708 | 0.00081927 | 0.00052334 | 0.33734 | 0.33734 | 0.33734 | 0.99156 | -0.16034 | 0.99551 | -0.085 | 46.3385
20 | -0.10786 | -0.027184 | 0.10798 | 0.027259 | 0.00011806 | 7.5403e-05 | 0.16152 | 0.16152 | 0.16152 | 0.99403 | -0.11427 | 0.99522 | -0.091422 | 44.3734
21 | 0.014017 | 0.003518 | -0.014003 | -0.0035101 | 1.4103e-05 | 7.92e-06 | 0.020985 | 0.020985 | 0.020985 | 0.99403 | -0.11427 | 0.99294 | -0.13539 | 5.7651
22 | 0.093846 | 0.023666 | -0.093655 | -0.023544 | 0.0001909 | 0.00012184 | 0.14053 | 0.14053 | 0.14053 | 0.99403 | -0.11427 | 0.99183 | -0.15686 | 38.6084
23 | 0.029432 | 0.0073815 | -0.029418 | -0.0073728 | 1.3957e-05 | 8.6828e-06 | 0.044007 | 0.044007 | 0.044007 | 0.99522 | -0.091422 | 0.99471 | -0.10138 | 12.0899
24 | -0.13741 | -0.034641 | 0.13802 | 0.035027 | 0.00060404 | 0.00038609 | 0.20553 | 0.20553 | 0.20553 | 0.99522 | -0.091422 | 1 | 0 | 56.4633
25 | 0.014003 | 0.0035101 | -0.014001 | -0.003509 | 1.9787e-06 | 1.1114e-06 | 0.020985 | 0.020985 | 0.020985 | 0.99294 | -0.13539 | 0.99279 | -0.13836 | 5.7651
26 | 0.060704 | 0.015286 | -0.060606 | -0.015224 | 9.7235e-05 | 6.1828e-05 | 0.091098 | 0.091098 | 0.091098 | 0.99183 | -0.15686 | 0.99009 | -0.19043 | 25.027
27 | 0.060606 | 0.015224 | -0.060518 | -0.015167 | 8.8974e-05 | 5.6576e-05 | 0.091098 | 0.091098 | 0.091098 | 0.99009 | -0.19043 | 0.9885 | -0.22124 | 25.027
28 | 0.25643 | 0.065893 | -0.25537 | -0.065219 | 0.001054 | 0.00067355 | 0.38214 | 0.38214 | 0.38214 | 1 | 0 | 0.99551 | -0.085 | 52.4922

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41872 | 0.10659

## res_load
| p_mw | q_mvar
0 | 0.011663 | 0.002923
1 | 0.022781 | 0.0057095
2 | 0.020809 | 0.0052152
3 | 0.020295 | 0.0050864
4 | 0.019928 | 0.0049945
5 | 0.049791 | 0.012479
6 | 0.05372 | 0.013463
7 | 0.0072339 | 0.001813
8 | 0.0066574 | 0.0016685
9 | 0.0093587 | 0.0023455
10 | 0.032952 | 0.0082585
11 | 0.060518 | 0.015167
12 | 0.029418 | 0.0073728
13 | 0.022624 | 0.0056702
14 | 0.014001 | 0.003509
15 | 0.029972 | 0.0075116

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1