## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1063-3_0_10_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1063-3_0_10_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1063-3_0_10_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1063-3_0_10_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1063-3_0_10_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1063-3_0_10_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_1063-3_0_10_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1063-3_0_10_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1063-3_0_10_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_1063-3_0_10_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1063-3_0_10_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_1063-3_0_10_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1063-3_0_10_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1063-3_0_10_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1063-3_0_10_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_1063-3_0_10_node_55 | 0.4 | n |  | TRUE
16 | bus_LV_1063-3_0_10_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1063-3_0_10_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1063-3_0_10_node_133 | 0.4 | n |  | TRUE
19 | bus_LV_1063-3_0_10_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1063-3_0_10_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1063-3_0_10_node_105 | 0.4 | n |  | TRUE
22 | bus_LV_1063-3_0_10_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1063-3_0_10_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_1063-3_0_10_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_1063-3_0_10_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1063-3_0_10_node_50 | 0.4 | n |  | TRUE
27 | bus_LV_1063-3_0_10_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_1063-3_0_10_node_65 | 0.4 | n |  | TRUE
29 | bus_LV_1063-3_0_10_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_1063-3_0_10_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_1063-3_0_10_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_1063-3_0_10_node_66 | 0.4 | n |  | TRUE
33 | bus_LV_1063-3_0_10_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_1063-3_0_10_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1063-3_0_10_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_1063-3_0_10_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_1063-3_0_10_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_1063-3_0_10_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_1063-3_0_10_node_69 | 0.4 | n |  | TRUE
40 | bus_LV_1063-3_0_10_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_1063-3_0_10_node_134 | 0.4 | n |  | TRUE
42 | bus_LV_1063-3_0_10_node_104 | 0.4 | n |  | TRUE
43 | bus_LV_1063-3_0_10_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_1063-3_0_10_node_106 | 0.4 | n |  | TRUE
45 | bus_LV_1063-3_0_10_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_1063-3_0_10_node_82 | 0.4 | n |  | TRUE
47 | bus_LV_1063-3_0_10_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_1063-3_0_10_node_81 | 0.4 | n |  | TRUE
49 | bus_LV_1063-3_0_10_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_1063-3_0_10_node_95 | 0.4 | n |  | TRUE
51 | bus_LV_1063-3_0_10_node_130 | 0.4 | n |  | TRUE
52 | bus_LV_1063-3_0_10_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_1063-3_0_10_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_1063-3_0_10_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_1063-3_0_10_node_28 | 0.4 | n |  | TRUE
56 | bus_LV_1063-3_0_10_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_1063-3_0_10_node_129 | 0.4 | n |  | TRUE
58 | bus_LV_1063-3_0_10_node_29 | 0.4 | n |  | TRUE
59 | bus_LV_1063-3_0_10_node_119 | 0.4 | n |  | TRUE
60 | bus_LV_1063-3_0_10_node_127 | 0.4 | n |  | TRUE
61 | bus_LV_1063-3_0_10_node_132 | 0.4 | n |  | TRUE
62 | bus_LV_1063-3_0_10_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_1063-3_0_10_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_1063-3_0_10_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_1063-3_0_10_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_1063-3_0_10_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_1063-3_0_10_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_1063-3_0_10_node_77 | 0.4 | n |  | TRUE
69 | bus_LV_1063-3_0_10_node_75 | 0.4 | n |  | TRUE
70 | bus_LV_1063-3_0_10_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_1063-3_0_10_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_1063-3_0_10_node_84 | 0.4 | n |  | TRUE
73 | bus_LV_1063-3_0_10_node_80 | 0.4 | n |  | TRUE
74 | bus_LV_1063-3_0_10_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_1063-3_0_10_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_1063-3_0_10_node_79 | 0.4 | n |  | TRUE
77 | bus_LV_1063-3_0_10_node_131 | 0.4 | n |  | TRUE
78 | bus_LV_1063-3_0_10_node_90 | 0.4 | n |  | TRUE
79 | bus_LV_1063-3_0_10_node_107 | 0.4 | n |  | TRUE
80 | bus_LV_1063-3_0_10_node_117 | 0.4 | n |  | TRUE
81 | bus_LV_1063-3_0_10_node_125 | 0.4 | n |  | TRUE
82 | bus_LV_1063-3_0_10_node_34 | 0.4 | n |  | TRUE
83 | bus_LV_1063-3_0_10_node_35 | 0.4 | n |  | TRUE
84 | bus_LV_1063-3_0_10_node_36 | 0.4 | n |  | TRUE
85 | bus_LV_1063-3_0_10_node_37 | 0.4 | n |  | TRUE
86 | bus_LV_1063-3_0_10_node_39 | 0.4 | n |  | TRUE
87 | bus_LV_1063-3_0_10_node_38 | 0.4 | n |  | TRUE
88 | bus_LV_1063-3_0_10_node_109 | 0.4 | n |  | TRUE
89 | bus_LV_1063-3_0_10_node_41 | 0.4 | n |  | TRUE
90 | bus_LV_1063-3_0_10_node_46 | 0.4 | n |  | TRUE
91 | bus_LV_1063-3_0_10_node_56 | 0.4 | n |  | TRUE
92 | bus_LV_1063-3_0_10_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_1063-3_0_10_node_51 | 0.4 | n |  | TRUE
94 | bus_LV_1063-3_0_10_node_52 | 0.4 | n |  | TRUE
95 | bus_LV_1063-3_0_10_node_53 | 0.4 | n |  | TRUE
96 | bus_LV_1063-3_0_10_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_1063-3_0_10_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_1063-3_0_10_node_62 | 0.4 | n |  | TRUE
99 | bus_LV_1063-3_0_10_node_63 | 0.4 | n |  | TRUE
100 | bus_LV_1063-3_0_10_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_1063-3_0_10_node_85 | 0.4 | n |  | TRUE
102 | bus_LV_1063-3_0_10_node_100 | 0.4 | n |  | TRUE
103 | bus_LV_1063-3_0_10_node_102 | 0.4 | n |  | TRUE
104 | bus_LV_1063-3_0_10_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_1063-3_0_10_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_1063-3_0_10_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_1063-3_0_10_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_1063-3_0_10_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_1063-3_0_10_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_1063-3_0_10_node_91 | 0.4 | n |  | TRUE
111 | bus_LV_1063-3_0_10_node_92 | 0.4 | n |  | TRUE
112 | bus_LV_1063-3_0_10_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_1063-3_0_10_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_1063-3_0_10_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_1063-3_0_10_node_122 | 0.4 | n |  | TRUE
116 | bus_LV_1063-3_0_10_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_1063-3_0_10_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_1063-3_0_10_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_1063-3_0_10_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_1063-3_0_10_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_1063-3_0_10_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_1063-3_0_10_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_1063-3_0_10_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_1063-3_0_10_node_128 | 0.4 | n |  | TRUE
125 | bus_LV_1063-3_0_10_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_1063-3_0_10_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_1063-3_0_10_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_1063-3_0_10_node_121 | 0.4 | n |  | TRUE
129 | bus_LV_1063-3_0_10_node_123 | 0.4 | n |  | TRUE
130 | bus_LV_1063-3_0_10_node_126 | 0.4 | n |  | TRUE
131 | bus_MV_211_1_node_165 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1063-3_0_10_load_0 | 0 | 0.0037685 | 0.00094448 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1063-3_0_10_load_4 | 4 | 0.0054695 | 0.0013708 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1063-3_0_10_load_24 | 5 | 0.0016474 | 0.00041288 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1063-3_0_10_load_32 | 8 | 0.0022871 | 0.00057321 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1063-3_0_10_load_43 | 13 | 0.0033473 | 0.00083892 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1063-3_0_10_load_68 | 14 | 0.0032841 | 0.00082308 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1063-3_0_10_load_55 | 15 | 0.0036479 | 0.00091424 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1063-3_0_10_load_25 | 16 | 0.003358 | 0.00084159 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1063-3_0_10_load_133 | 18 | 0.0027739 | 0.00069519 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1063-3_0_10_load_105 | 21 | 0.015662 | 0.0039254 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1063-3_0_10_load_47 | 23 | 0.0021902 | 0.0005489 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1063-3_0_10_load_45 | 24 | 0.0019397 | 0.00048613 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1063-3_0_10_load_50 | 26 | 0.002272 | 0.00056942 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1063-3_0_10_load_65 | 28 | 0.022204 | 0.0055648 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1063-3_0_10_load_74 | 29 | 0.0013355 | 0.00033471 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1063-3_0_10_load_67 | 31 | 0.0090554 | 0.0022695 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1063-3_0_10_load_76 | 35 | 0.011672 | 0.0029253 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1063-3_0_10_load_72 | 37 | 0.0012919 | 0.00032379 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1063-3_0_10_load_73 | 38 | 0.0050457 | 0.0012646 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1063-3_0_10_load_69 | 39 | 0.015391 | 0.0038572 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1063-3_0_10_load_134 | 41 | 0.015316 | 0.0038385 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1063-3_0_10_load_104 | 42 | 0.0093023 | 0.0023314 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1063-3_0_10_load_106 | 44 | 0.0026024 | 0.00065223 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1063-3_0_10_load_60 | 47 | 0.0017592 | 0.00044091 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1063-3_0_10_load_33 | 49 | 0.0017413 | 0.00043641 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1063-3_0_10_load_130 | 51 | 0.011672 | 0.0029252 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1063-3_0_10_load_108 | 54 | 0.0022862 | 0.00057299 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1063-3_0_10_load_129 | 57 | 0.012543 | 0.0031437 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1063-3_0_10_load_127 | 60 | 0.003551 | 0.00088997 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1063-3_0_10_load_132 | 61 | 0.012543 | 0.0031437 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1063-3_0_10_load_49 | 62 | 0.0034714 | 0.00087002 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1063-3_0_10_load_40 | 63 | 0.0017595 | 0.00044096 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1063-3_0_10_load_42 | 64 | 0.0050223 | 0.0012587 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1063-3_0_10_load_54 | 65 | 0.0048608 | 0.0012182 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1063-3_0_10_load_44 | 66 | 0.0023107 | 0.00057911 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1063-3_0_10_load_64 | 67 | 0.014181 | 0.0035542 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1063-3_0_10_load_77 | 68 | 0.0028893 | 0.00072412 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1063-3_0_10_load_75 | 69 | 0.0049143 | 0.0012316 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1063-3_0_10_load_70 | 70 | 0.010524 | 0.0026376 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1063-3_0_10_load_71 | 71 | 0.0097223 | 0.0024366 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1063-3_0_10_load_84 | 72 | 0.0016827 | 0.00042173 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1063-3_0_10_load_80 | 73 | 0.0039534 | 0.00099081 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1063-3_0_10_load_61 | 74 | 0.0038801 | 0.00097244 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1063-3_0_10_load_83 | 75 | 0.0010031 | 0.00025141 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1063-3_0_10_load_79 | 76 | 0.0010031 | 0.00025139 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1063-3_0_10_load_131 | 77 | 0.011674 | 0.0029258 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1063-3_0_10_load_107 | 79 | 0.002001 | 0.00050151 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1063-3_0_10_load_117 | 80 | 0.0022576 | 0.00056581 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1063-3_0_10_load_34 | 82 | 0.0050746 | 0.0012718 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1063-3_0_10_load_36 | 84 | 0.0032508 | 0.00081473 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1063-3_0_10_load_37 | 85 | 0.0010481 | 0.00026268 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1063-3_0_10_load_39 | 86 | 0.0026243 | 0.00065772 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1063-3_0_10_load_109 | 88 | 0.004741 | 0.0011882 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1063-3_0_10_load_41 | 89 | 0.0031576 | 0.00079137 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1063-3_0_10_load_46 | 90 | 0.017296 | 0.0043347 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1063-3_0_10_load_56 | 91 | 0.0034722 | 0.00087021 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1063-3_0_10_load_57 | 92 | 0.0024114 | 0.00060436 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1063-3_0_10_load_51 | 93 | 0.002463 | 0.00061728 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1063-3_0_10_load_52 | 94 | 0.0048625 | 0.0012187 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1063-3_0_10_load_53 | 95 | 0.0030434 | 0.00076275 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1063-3_0_10_load_58 | 96 | 0.0024863 | 0.00062314 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1063-3_0_10_load_59 | 97 | 0.0024126 | 0.00060467 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1063-3_0_10_load_62 | 98 | 0.0036574 | 0.00091664 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1063-3_0_10_load_63 | 99 | 0.0047949 | 0.0012017 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1063-3_0_10_load_78 | 100 | 0.0088384 | 0.0022151 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1063-3_0_10_load_85 | 101 | 0.003602 | 0.00090276 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1063-3_0_10_load_100 | 102 | 0.0029318 | 0.00073478 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1063-3_0_10_load_102 | 103 | 0.00099604 | 0.00024963 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1063-3_0_10_load_101 | 105 | 0.0021654 | 0.00054269 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1063-3_0_10_load_86 | 106 | 0.0018505 | 0.00046379 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1063-3_0_10_load_87 | 107 | 0.003431 | 0.00085989 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1063-3_0_10_load_91 | 110 | 0.011695 | 0.0029311 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1063-3_0_10_load_92 | 111 | 0.0019447 | 0.00048739 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1063-3_0_10_load_93 | 112 | 0.0033013 | 0.00082738 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1063-3_0_10_load_94 | 113 | 0.011698 | 0.0029317 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1063-3_0_10_load_113 | 114 | 0.001944 | 0.00048721 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1063-3_0_10_load_96 | 116 | 0.0016611 | 0.00041632 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1063-3_0_10_load_97 | 117 | 0.001919 | 0.00048094 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1063-3_0_10_load_99 | 118 | 0.0021181 | 0.00053086 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1063-3_0_10_load_103 | 119 | 0.0076712 | 0.0019226 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1063-3_0_10_load_115 | 122 | 0.0020313 | 0.00050908 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1063-3_0_10_load_124 | 123 | 0.0013078 | 0.00032777 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1063-3_0_10_load_128 | 124 | 0.0020313 | 0.00050908 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1063-3_0_10_load_116 | 126 | 0.0020646 | 0.00051745 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1063-3_0_10_load_121 | 128 | 0.0086499 | 0.0021679 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1063-3_0_10_load_123 | 129 | 0.0019682 | 0.00049327 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1063-3_0_10_load_126 | 130 | 0.0019682 | 0.00049327 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1063-3_0_10_line_0 |  | 0 | 1 | 0.045647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1063-3_0_10_line_1 |  | 0 | 2 | 0.011857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1063-3_0_10_line_2 |  | 1 | 3 | 0.002747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1063-3_0_10_line_3 |  | 1 | 4 | 0.026513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1063-3_0_10_line_4 |  | 2 | 5 | 0.038182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1063-3_0_10_line_5 |  | 2 | 6 | 0.044637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1063-3_0_10_line_6 |  | 3 | 7 | 0.023542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1063-3_0_10_line_7 |  | 4 | 8 | 0.026885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1063-3_0_10_line_8 |  | 5 | 49 | 0.00077654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1063-3_0_10_line_9 |  | 6 | 16 | 0.0079256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1063-3_0_10_line_10 |  | 6 | 11 | 0.10936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1063-3_0_10_line_11 |  | 7 | 50 | 0.026065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1063-3_0_10_line_12 |  | 7 | 51 | 0.028064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1063-3_0_10_line_13 |  | 8 | 53 | 0.018525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1063-3_0_10_line_14 |  | 9 | 10 | 0.011779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1063-3_0_10_line_15 |  | 9 | 11 | 0.055128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1063-3_0_10_line_16 |  | 9 | 12 | 0.14646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1063-3_0_10_line_17 |  | 9 | 13 | 0.013163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1063-3_0_10_line_18 |  | 10 | 62 | 0.010264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1063-3_0_10_line_19 |  | 10 | 63 | 0.019708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1063-3_0_10_line_20 |  | 11 | 14 | 0.051267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1063-3_0_10_line_21 |  | 11 | 15 | 0.015067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1063-3_0_10_line_22 |  | 12 | 23 | 0.040219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1063-3_0_10_line_23 |  | 12 | 24 | 0.020556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1063-3_0_10_line_24 |  | 13 | 64 | 0.015997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1063-3_0_10_line_25 |  | 14 | 19 | 0.030604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1063-3_0_10_line_26 |  | 15 | 65 | 0.004058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1063-3_0_10_line_27 |  | 17 | 18 | 0.015378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1063-3_0_10_line_28 |  | 17 | 19 | 0.041246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1063-3_0_10_line_29 |  | 19 | 48 | 0.017955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1063-3_0_10_line_30 |  | 20 | 21 | 0.018718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1063-3_0_10_line_31 |  | 20 | 22 | 0.047675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1063-3_0_10_line_32 |  | 22 | 29 | 0.086742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1063-3_0_10_line_33 |  | 23 | 25 | 0.022861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1063-3_0_10_line_34 |  | 24 | 66 | 0.002682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1063-3_0_10_line_35 |  | 25 | 26 | 0.045678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1063-3_0_10_line_36 |  | 25 | 27 | 0.052737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1063-3_0_10_line_37 |  | 27 | 28 | 0.027373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1063-3_0_10_line_38 |  | 28 | 67 | 0.02195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1063-3_0_10_line_39 |  | 29 | 37 | 0.003148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1063-3_0_10_line_40 |  | 30 | 31 | 0.0073645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1063-3_0_10_line_41 |  | 30 | 32 | 0.017043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1063-3_0_10_line_42 |  | 31 | 42 | 0.017603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1063-3_0_10_line_43 |  | 32 | 67 | 0.022965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1063-3_0_10_line_44 |  | 33 | 34 | 0.11651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1063-3_0_10_line_45 |  | 33 | 35 | 0.10119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1063-3_0_10_line_46 |  | 34 | 42 | 0.093758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1063-3_0_10_line_47 |  | 34 | 40 | 0.097678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1063-3_0_10_line_48 |  | 35 | 68 | 0.034959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1063-3_0_10_line_49 |  | 36 | 37 | 0.013983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1063-3_0_10_line_50 |  | 36 | 38 | 0.0030128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1063-3_0_10_line_51 |  | 36 | 39 | 0.056129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1063-3_0_10_line_52 |  | 38 | 69 | 0.018076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_1063-3_0_10_line_53 |  | 39 | 70 | 0.054464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1063-3_0_10_line_54 |  | 40 | 41 | 0.004394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1063-3_0_10_line_55 |  | 43 | 44 | 0.0050888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1063-3_0_10_line_56 |  | 43 | 45 | 0.082301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1063-3_0_10_line_57 |  | 43 | 46 | 0.046662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1063-3_0_10_line_58 |  | 45 | 47 | 0.0044272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1063-3_0_10_line_59 |  | 46 | 72 | 0.017585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1063-3_0_10_line_60 |  | 46 | 73 | 0.040948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1063-3_0_10_line_61 |  | 47 | 74 | 0.0069924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1063-3_0_10_line_62 |  | 48 | 75 | 0.016025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1063-3_0_10_line_63 |  | 48 | 76 | 0.010944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1063-3_0_10_line_64 |  | 50 | 77 | 0.020207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1063-3_0_10_line_65 |  | 50 | 78 | 0.031171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1063-3_0_10_line_66 |  | 52 | 53 | 0.008442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1063-3_0_10_line_67 |  | 52 | 54 | 0.023149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1063-3_0_10_line_68 |  | 54 | 79 | 0.11043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1063-3_0_10_line_69 |  | 55 | 56 | 0.048797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1063-3_0_10_line_70 |  | 55 | 57 | 0.012612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1063-3_0_10_line_71 |  | 56 | 61 | 0.021184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1063-3_0_10_line_72 |  | 56 | 59 | 0.024187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1063-3_0_10_line_73 |  | 58 | 59 | 0.016038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1063-3_0_10_line_74 |  | 58 | 60 | 0.019068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1063-3_0_10_line_75 |  | 59 | 80 | 0.00046995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1063-3_0_10_line_76 |  | 60 | 81 | 0.0046095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1063-3_0_10_line_77 |  | 62 | 91 | 0.02767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1063-3_0_10_line_78 |  | 63 | 85 | 0.0081354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1063-3_0_10_line_79 |  | 64 | 89 | 0.024254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1063-3_0_10_line_80 |  | 65 | 94 | 0.015011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1063-3_0_10_line_81 |  | 66 | 90 | 0.018844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1063-3_0_10_line_82 |  | 68 | 100 | 0.007793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1063-3_0_10_line_83 |  | 69 | 100 | 0.0093419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_1063-3_0_10_line_84 |  | 70 | 71 | 0.010833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1063-3_0_10_line_85 |  | 72 | 102 | 0.024782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1063-3_0_10_line_86 |  | 73 | 76 | 0.024126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1063-3_0_10_line_87 |  | 75 | 101 | 0.0087902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1063-3_0_10_line_88 |  | 78 | 113 | 0.03549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1063-3_0_10_line_89 |  | 78 | 108 | 0.009215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1063-3_0_10_line_90 |  | 79 | 87 | 0.0097209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1063-3_0_10_line_91 |  | 80 | 126 | 0.0082731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1063-3_0_10_line_92 |  | 81 | 123 | 0.013966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1063-3_0_10_line_93 |  | 81 | 130 | 0.021958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1063-3_0_10_line_94 |  | 82 | 83 | 0.025726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1063-3_0_10_line_95 |  | 83 | 84 | 0.019039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1063-3_0_10_line_96 |  | 83 | 85 | 0.043172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1063-3_0_10_line_97 |  | 84 | 86 | 0.032119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1063-3_0_10_line_98 |  | 87 | 88 | 0.079624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1063-3_0_10_line_99 |  | 91 | 92 | 0.0028616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1063-3_0_10_line_100 |  | 92 | 96 | 0.0075701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1063-3_0_10_line_101 |  | 93 | 94 | 0.014275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1063-3_0_10_line_102 |  | 93 | 95 | 0.0071594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1063-3_0_10_line_103 |  | 96 | 97 | 0.015254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1063-3_0_10_line_104 |  | 97 | 98 | 0.00025902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1063-3_0_10_line_105 |  | 98 | 99 | 0.0037499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1063-3_0_10_line_106 |  | 101 | 103 | 0.0063737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1063-3_0_10_line_107 |  | 102 | 104 | 0.011285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1063-3_0_10_line_108 |  | 103 | 105 | 0.0075232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1063-3_0_10_line_109 |  | 104 | 118 | 0.0095633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1063-3_0_10_line_110 |  | 104 | 117 | 0.014571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1063-3_0_10_line_111 |  | 105 | 119 | 0.017737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1063-3_0_10_line_112 |  | 106 | 107 | 0.029768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1063-3_0_10_line_113 |  | 106 | 108 | 0.037581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1063-3_0_10_line_114 |  | 107 | 109 | 0.0064813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1063-3_0_10_line_115 |  | 108 | 110 | 0.021656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1063-3_0_10_line_116 |  | 109 | 111 | 0.030977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1063-3_0_10_line_117 |  | 109 | 112 | 0.028512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1063-3_0_10_line_118 |  | 111 | 114 | 0.0079529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1063-3_0_10_line_119 |  | 114 | 115 | 0.014809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1063-3_0_10_line_120 |  | 115 | 125 | 0.006511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1063-3_0_10_line_121 |  | 116 | 117 | 0.023409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1063-3_0_10_line_122 |  | 120 | 121 | 0.010255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1063-3_0_10_line_123 |  | 120 | 122 | 0.021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1063-3_0_10_line_124 |  | 121 | 123 | 0.0026231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1063-3_0_10_line_125 |  | 122 | 124 | 0.0080258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1063-3_0_10_line_126 |  | 125 | 129 | 0.0061514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1063-3_0_10_line_127 |  | 126 | 127 | 0.016102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1063-3_0_10_line_128 |  | 127 | 128 | 0.020781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1063-3_0_10_line_129 |  | 129 | 130 | 0.0079353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1063-3_0_10_trafo_6 | 0.63 MVA 20/0.4 kV | 131 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2670035.129 | 1211485.7932 | 2670035.2122 | 1211491.6534 | 2670024.9951 | 1211503.641 | 2670020.35 | 1211506.4104 | 2670008.8437 | 1211511.0672 | 2670004.1784 | 1211515.1719
1 | 2669995.2762 | 1211523.0044 | 2670004.1784 | 1211515.1719
2 | 2670035.129 | 1211485.7932 | 2670035.0929 | 1211483.0466
3 | 2670035.129 | 1211485.7932 | 2670061.2847 | 1211481.4529
4 | 2669995.2762 | 1211523.0044 | 2669998.8192 | 1211527.382 | 2670005.3106 | 1211536.2748 | 2670010.4251 | 1211547.2417 | 2670016.2125 | 1211552.6796 | 2670017.407 | 1211553.5833
5 | 2669960.9395 | 1211495.5512 | 2669964.4174 | 1211500.2949 | 2669968.7928 | 1211506.2611 | 2669987.2352 | 1211518.5851 | 2669995.2762 | 1211523.0044
6 | 2670035.0929 | 1211483.0466 | 2670045.3021 | 1211481.4321 | 2670044.0541 | 1211475.7584 | 2670041.4225 | 1211468.8454
7 | 2670087.807 | 1211477.0517 | 2670061.2847 | 1211481.4529
8 | 2670017.407 | 1211553.5833 | 2670018.0263 | 1211554.0517
9 | 2669960.9395 | 1211495.5512 | 2669968.7547 | 1211494.2333
10 | 2669885.8611 | 1211483.9197 | 2669880.8622 | 1211501.3276 | 2669878.5634 | 1211508.7942 | 2669960.9395 | 1211495.5512
11 | 2670021.1361 | 1211452.4081 | 2670041.4225 | 1211468.8454
12 | 2670041.4225 | 1211468.8454 | 2670059.4331 | 1211462.942 | 2670066.6042 | 1211457.3227
13 | 2670106.0825 | 1211474.019 | 2670087.807 | 1211477.0517
14 | 2669870.8514 | 1211548.9178 | 2669874.0921 | 1211537.5932
15 | 2669874.0921 | 1211537.5932 | 2669877.8234 | 1211519.4144 | 2669878.2167 | 1211513.7377 | 2669878.5634 | 1211508.7942 | 2669880.8622 | 1211501.3276 | 2669885.8611 | 1211483.9197
16 | 2669757.306 | 1211528.9991 | 2669783.5154 | 1211527.6381 | 2669810.8816 | 1211524.8342 | 2669840.7579 | 1211522.4712 | 2669847.1683 | 1211521.4456 | 2669867.339 | 1211516.6343 | 2669878.2167 | 1211513.7377 | 2669877.8234 | 1211519.4144 | 2669874.0921 | 1211537.5932
17 | 2669874.0921 | 1211537.5932 | 2669887.121 | 1211535.7215
18 | 2669870.8514 | 1211548.9178 | 2669863.4196 | 1211549.5757 | 2669860.8339 | 1211550.6571
19 | 2669870.8514 | 1211548.9178 | 2669866.1279 | 1211568.0512
20 | 2669885.8611 | 1211483.9197 | 2669888.7995 | 1211445.8748 | 2669890.0576 | 1211432.8266
21 | 2669885.8611 | 1211483.9197 | 2669900.5736 | 1211480.6693
22 | 2669757.306 | 1211528.9991 | 2669730.0455 | 1211529.9144 | 2669717.103 | 1211529.8113
23 | 2669757.306 | 1211528.9991 | 2669756.8169 | 1211549.549
24 | 2669887.121 | 1211535.7215 | 2669902.9557 | 1211533.4468
25 | 2669892.995 | 1211402.3635 | 2669890.0576 | 1211432.8266
26 | 2669904.536 | 1211479.7939 | 2669900.5736 | 1211480.6693
27 | 2669847.979 | 1211378.2658 | 2669853.7768 | 1211375.0539 | 2669856.9288 | 1211374.546 | 2669859.8431 | 1211374.2133 | 2669862.4671 | 1211374.6665
28 | 2669862.4671 | 1211374.6665 | 2669868.1191 | 1211379.3578 | 2669887.6356 | 1211397.998 | 2669890.6841 | 1211400.4797 | 2669892.995 | 1211402.3635
29 | 2669897.56 | 1211385.0284 | 2669894.8802 | 1211393.2354 | 2669892.995 | 1211402.3635
30 | 2669747.5827 | 1211316.2528 | 2669732.7742 | 1211327.7536
31 | 2669691.947 | 1211309.921 | 2669693.9287 | 1211312.0121 | 2669695.4347 | 1211313.8531 | 2669698.869 | 1211316.4949 | 2669701.8064 | 1211317.4409 | 2669706.2822 | 1211318.1047 | 2669713.3081 | 1211317.7421 | 2669720.5108 | 1211317.8596 | 2669726.6917 | 1211320.2222 | 2669730.4749 | 1211324.2245 | 2669732.7742 | 1211327.7536
32 | 2669691.947 | 1211309.921 | 2669689.5558 | 1211311.6497 | 2669686.2507 | 1211313.5568 | 2669680.8434 | 1211315.2169 | 2669673.0589 | 1211316.7714 | 2669663.3824 | 1211319.6046 | 2669657.7256 | 1211323.1186 | 2669654.3309 | 1211325.536 | 2669650.8927 | 1211329.0759 | 2669648.5874 | 1211333.863 | 2669645.9402 | 1211340.603 | 2669643.4356 | 1211346.1884 | 2669640.2837 | 1211353.2004 | 2669635.5489 | 1211357.8036 | 2669628.3512 | 1211360.1459
33 | 2669694.2427 | 1211529.6293 | 2669717.103 | 1211529.8113
34 | 2669756.8169 | 1211549.549 | 2669756.7531 | 1211552.2302
35 | 2669694.2427 | 1211529.6293 | 2669694.5759 | 1211532.9797 | 2669696.2964 | 1211534.0116 | 2669697.5587 | 1211537.1838 | 2669697.5637 | 1211538.7071 | 2669696.3574 | 1211541.7949 | 2669695.3161 | 1211543.7617 | 2669691.7688 | 1211542.3417 | 2669691.4478 | 1211543.1495 | 2669689.1566 | 1211547.3921 | 2669679.7471 | 1211546.2704 | 2669674.2557 | 1211545.3946 | 2669669.1005 | 1211544.2652
36 | 2669650.0138 | 1211522.7419 | 2669650.7575 | 1211527.3757 | 2669663.3239 | 1211526.2661 | 2669667.2558 | 1211525.9896 | 2669681.3925 | 1211525.1097 | 2669693.7532 | 1211524.6983 | 2669694.2427 | 1211529.6293
37 | 2669650.0138 | 1211522.7419 | 2669642.77 | 1211518.3546 | 2669634.7986 | 1211514.4592 | 2669625.0098 | 1211511.9767
38 | 2669625.0098 | 1211511.9767 | 2669618.9224 | 1211510.7271 | 2669610.5153 | 1211509.6506 | 2669603.2882 | 1211510.3445
39 | 2669628.3512 | 1211360.1459 | 2669625.3577 | 1211361.1201
40 | 2669571.637 | 1211534.5794 | 2669569.1093 | 1211533.6938 | 2669564.4984 | 1211534.5303
41 | 2669571.637 | 1211534.5794 | 2669576.5023 | 1211530.5002 | 2669584.7286 | 1211523.6252
42 | 2669547.2254 | 1211537.9199 | 2669562.5452 | 1211534.8847 | 2669564.4984 | 1211534.5303
43 | 2669584.7286 | 1211523.6252 | 2669593.8246 | 1211515.8042 | 2669599.4541 | 1211512.0119 | 2669603.2882 | 1211510.3445
44 | 2669457.2914 | 1211546.0767 | 2669456.3917 | 1211546.333 | 2669450.628 | 1211547.9558 | 2669435.3755 | 1211494.5784 | 2669442.5717 | 1211482.8326 | 2669468.8257 | 1211458.7343 | 2669466.1727 | 1211454.901
45 | 2669466.1727 | 1211454.901 | 2669471.3591 | 1211450.0028 | 2669487.5586 | 1211437.1056 | 2669498.4933 | 1211429.3058 | 2669515.544 | 1211419.6651 | 2669533.3815 | 1211410.3227 | 2669551.1479 | 1211400.7231
46 | 2669457.2914 | 1211546.0767 | 2669459.9611 | 1211549.1208 | 2669462.6208 | 1211551.0752 | 2669465.9174 | 1211552.4922 | 2669470.0604 | 1211553.0074 | 2669490.427 | 1211548.3083 | 2669527.0903 | 1211541.9092 | 2669547.2254 | 1211537.9199
47 | 2669374.0321 | 1211585.755 | 2669435.1703 | 1211565.7092 | 2669438.0992 | 1211564.1201 | 2669440.8993 | 1211561.8402 | 2669444.2933 | 1211554.8975 | 2669444.6928 | 1211551.9114 | 2669444.3458 | 1211549.7394 | 2669445.3293 | 1211549.4618 | 2669450.628 | 1211547.9558 | 2669456.3917 | 1211546.333 | 2669457.2914 | 1211546.0767
48 | 2669551.1479 | 1211400.7231 | 2669559.1834 | 1211396.3814 | 2669581.8964 | 1211384.0902
49 | 2669614.5924 | 1211370 | 2669621.1747 | 1211364.0175 | 2669625.3577 | 1211361.1201
50 | 2669614.5924 | 1211370 | 2669612.9424 | 1211367.4792
51 | 2669614.5924 | 1211370 | 2669615.5691 | 1211374.87 | 2669588.6763 | 1211389.7989 | 2669570.5918 | 1211399.2456
52 | 2669612.9424 | 1211367.4792 | 2669596.9805 | 1211375.962
53 | 2669570.5918 | 1211399.2456 | 2669562.0693 | 1211403.6974 | 2669533.7896 | 1211418.9884 | 2669522.6754 | 1211425.1333
54 | 2669374.0321 | 1211585.755 | 2669369.8812 | 1211587.2299
55 | 2669949.3909 | 1211275.1227 | 2669953.4942 | 1211272.1129
56 | 2669949.3909 | 1211275.1227 | 2669940.3663 | 1211262.5313 | 2669931.8687 | 1211253.5928 | 2669914.5635 | 1211234.2891 | 2669893.4653 | 1211215.0522
57 | 2669949.3909 | 1211275.1227 | 2669942.0476 | 1211280.5178 | 2669926.7203 | 1211314.8262
58 | 2669893.4653 | 1211215.0522 | 2669889.873 | 1211212.4646
59 | 2669926.7203 | 1211314.8262 | 2669941.8435 | 1211323.8005
60 | 2669926.7203 | 1211314.8262 | 2669911.0129 | 1211352.6413
61 | 2669889.873 | 1211212.4646 | 2669884.1993 | 1211208.3777
62 | 2669897.56 | 1211385.0284 | 2669910.683 | 1211394.2255
63 | 2669897.56 | 1211385.0284 | 2669901.7582 | 1211374.9214
64 | 2670033.2266 | 1211436.1955 | 2670021.1361 | 1211452.4081
65 | 2669996.0882 | 1211433.7582 | 2670021.1361 | 1211452.4081
66 | 2670114.4348 | 1211472.6385 | 2670106.0825 | 1211474.019
67 | 2670114.4348 | 1211472.6385 | 2670114.575 | 1211473.6408 | 2670111.9636 | 1211488.9308 | 2670110.6436 | 1211495.4235
68 | 2670074.8714 | 1211598.9881 | 2670079.4655 | 1211588.9115 | 2670084.0758 | 1211580.6938 | 2670091.493 | 1211568.351 | 2670094.7302 | 1211560.5953 | 2670098.2572 | 1211549.5076 | 2670101.6226 | 1211534.7157 | 2670106.6646 | 1211514.9959 | 2670110.6436 | 1211495.4235
69 | 2670089.7945 | 1211408.3534 | 2670108.3566 | 1211407.2708 | 2670109.9576 | 1211412.0036 | 2670114.0207 | 1211426.427 | 2670112.0768 | 1211432.7637 | 2670108.8895 | 1211431.103
70 | 2670108.8895 | 1211431.103 | 2670096.4024 | 1211432.8751
71 | 2670068.5859 | 1211409.6051 | 2670089.7945 | 1211408.3534
72 | 2670089.7945 | 1211408.3534 | 2670084.3569 | 1211384.7859
73 | 2670100.404 | 1211383.6848 | 2670084.3569 | 1211384.7859
74 | 2670100.404 | 1211383.6848 | 2670099.8091 | 1211381.9323 | 2670092.5416 | 1211366.3238
75 | 2670084.3569 | 1211384.7859 | 2670083.8881 | 1211384.8182
76 | 2670090.596 | 1211362.1451 | 2670092.5416 | 1211366.3238
77 | 2669834.6553 | 1211558.185 | 2669843.0688 | 1211558.0872 | 2669860.8339 | 1211550.6571
78 | 2669866.1279 | 1211568.0512 | 2669864.178 | 1211575.9495
79 | 2669926.9631 | 1211529.9981 | 2669902.9557 | 1211533.4468
80 | 2669904.536 | 1211479.7939 | 2669907.0793 | 1211479.232 | 2669919.3528 | 1211477.4194
81 | 2669756.3047 | 1211571.0692 | 2669756.7531 | 1211552.2302
82 | 2669588.7501 | 1211380.3812 | 2669581.8964 | 1211384.0902
83 | 2669588.7501 | 1211380.3812 | 2669593.4131 | 1211377.8578 | 2669596.9805 | 1211375.962
84 | 2669522.6754 | 1211425.1333 | 2669513.1951 | 1211430.3749
85 | 2669963.1555 | 1211336.4472 | 2669941.8435 | 1211323.8005
86 | 2669901.7582 | 1211374.9214 | 2669911.0129 | 1211352.6413
87 | 2669916.5751 | 1211400.7138 | 2669911.4511 | 1211394.7638 | 2669910.683 | 1211394.2255
88 | 2669970.7238 | 1211456.3192 | 2669982.7951 | 1211452.0915 | 2669984.0279 | 1211451.2943 | 2669996.0882 | 1211433.7582
89 | 2669996.0882 | 1211433.7582 | 2669988.683 | 1211428.2456
90 | 2670070.8389 | 1211607.8331 | 2670074.8714 | 1211598.9881
91 | 2670075.6347 | 1211385.3877 | 2670083.8881 | 1211384.8182
92 | 2670090.596 | 1211362.1451 | 2670088.9506 | 1211358.6013 | 2670082.9092 | 1211350.5584
93 | 2670090.596 | 1211362.1451 | 2670068.6829 | 1211363.5469
94 | 2669861.0205 | 1211618.7908 | 2669838.1172 | 1211630.5078
95 | 2669861.0205 | 1211618.7908 | 2669842.5097 | 1211614.337
96 | 2669861.0205 | 1211618.7908 | 2669860.9459 | 1211607.0048 | 2669860.8532 | 1211592.8615 | 2669863.1691 | 1211580.0362 | 2669864.178 | 1211575.9495
97 | 2669811.282 | 1211606.8234 | 2669842.5097 | 1211614.337
98 | 2670070.8389 | 1211607.8331 | 2670088.3375 | 1211626.706 | 2670103.559 | 1211639.5483 | 2670110.7141 | 1211644.3243 | 2670114.8014 | 1211643.7497 | 2670115.1735 | 1211638.5953 | 2670110.8887 | 1211629.4726 | 2670106.6548 | 1211625.2287
99 | 2669834.6553 | 1211558.185 | 2669831.7939 | 1211558.2183
100 | 2669831.7939 | 1211558.2183 | 2669824.2243 | 1211558.3064
101 | 2669933.4751 | 1211475.3338 | 2669919.3528 | 1211477.4194
102 | 2669940.5577 | 1211474.2879 | 2669933.4751 | 1211475.3338
103 | 2669808.9714 | 1211558.4838 | 2669824.2243 | 1211558.3064
104 | 2669808.7124 | 1211558.4868 | 2669808.9714 | 1211558.4838
105 | 2669804.9628 | 1211558.5304 | 2669808.7124 | 1211558.4868
106 | 2669916.5751 | 1211400.7138 | 2669920.7343 | 1211405.5434
107 | 2669972.8607 | 1211342.2064 | 2669963.1555 | 1211336.4472
108 | 2669925.6436 | 1211411.2441 | 2669920.7343 | 1211405.5434
109 | 2669972.8607 | 1211342.2064 | 2669981.1513 | 1211346.9732
110 | 2669972.8607 | 1211342.2064 | 2669969.3793 | 1211350.0594 | 2669967.3356 | 1211355.68
111 | 2669937.2183 | 1211424.6845 | 2669925.6436 | 1211411.2441
112 | 2669976.4723 | 1211399.6735 | 2669977.4225 | 1211397.0497 | 2669990.8965 | 1211373.6785
113 | 2669988.683 | 1211428.2456 | 2669973.2529 | 1211417.5803 | 2669976.7454 | 1211411.3618 | 2669976.4723 | 1211399.6735 | 2669976.4723 | 1211399.6735
114 | 2669994.4782 | 1211368.2873 | 2669992.1997 | 1211371.4181 | 2669990.8965 | 1211373.6785
115 | 2670001.9772 | 1211411.1242 | 2669988.683 | 1211428.2456
116 | 2669994.4782 | 1211368.2873 | 2670025.3918 | 1211366.3111
117 | 2669994.4782 | 1211368.2873 | 2670001.7029 | 1211360.0447 | 2670014.7666 | 1211348.3229
118 | 2670025.3918 | 1211366.3111 | 2670033.3285 | 1211365.8037
119 | 2670048.1076 | 1211364.8589 | 2670033.3285 | 1211365.8037
120 | 2670054.6249 | 1211364.4463 | 2670048.1076 | 1211364.8589
121 | 2669966.131 | 1211378.7463 | 2669964.9795 | 1211373.3668 | 2669964.9177 | 1211368.9188 | 2669967.3062 | 1211355.7608 | 2669967.3356 | 1211355.68
122 | 2670073.8323 | 1211341.4464 | 2670081.3338 | 1211348.4611
123 | 2670073.8323 | 1211341.4464 | 2670052.6828 | 1211342.7242
124 | 2670081.3338 | 1211348.4611 | 2670082.9092 | 1211350.5584
125 | 2670044.6716 | 1211343.2082 | 2670052.6828 | 1211342.7242
126 | 2670054.6249 | 1211364.4463 | 2670060.7638 | 1211364.0536
127 | 2670059.5713 | 1211386.4959 | 2670075.6347 | 1211385.3877
128 | 2670038.7786 | 1211387.9194 | 2670059.5713 | 1211386.4959
129 | 2670060.7638 | 1211364.0536 | 2670068.6829 | 1211363.5469

## bus_geodata
| x | y | coords
0 | 2670004.1784 | 1211515.1719
1 | 2670035.129 | 1211485.7932
2 | 2669995.2762 | 1211523.0044
3 | 2670035.0929 | 1211483.0466
4 | 2670061.2847 | 1211481.4529
5 | 2670017.407 | 1211553.5833
6 | 2669960.9395 | 1211495.5512
7 | 2670041.4225 | 1211468.8454
8 | 2670087.807 | 1211477.0517
9 | 2669874.0921 | 1211537.5932
10 | 2669870.8514 | 1211548.9178
11 | 2669885.8611 | 1211483.9197
12 | 2669757.306 | 1211528.9991
13 | 2669887.121 | 1211535.7215
14 | 2669890.0576 | 1211432.8266
15 | 2669900.5736 | 1211480.6693
16 | 2669968.7547 | 1211494.2333
17 | 2669862.4671 | 1211374.6665
18 | 2669847.979 | 1211378.2658
19 | 2669892.995 | 1211402.3635
20 | 2669732.7742 | 1211327.7536
21 | 2669747.5827 | 1211316.2528
22 | 2669691.947 | 1211309.921
23 | 2669717.103 | 1211529.8113
24 | 2669756.8169 | 1211549.549
25 | 2669694.2427 | 1211529.6293
26 | 2669669.1005 | 1211544.2652
27 | 2669650.0138 | 1211522.7419
28 | 2669625.0098 | 1211511.9767
29 | 2669628.3512 | 1211360.1459
30 | 2669571.637 | 1211534.5794
31 | 2669564.4984 | 1211534.5303
32 | 2669584.7286 | 1211523.6252
33 | 2669466.1727 | 1211454.901
34 | 2669457.2914 | 1211546.0767
35 | 2669551.1479 | 1211400.7231
36 | 2669614.5924 | 1211370
37 | 2669625.3577 | 1211361.1201
38 | 2669612.9424 | 1211367.4792
39 | 2669570.5918 | 1211399.2456
40 | 2669374.0321 | 1211585.755
41 | 2669369.8812 | 1211587.2299
42 | 2669547.2254 | 1211537.9199
43 | 2669949.3909 | 1211275.1227
44 | 2669953.4942 | 1211272.1129
45 | 2669893.4653 | 1211215.0522
46 | 2669926.7203 | 1211314.8262
47 | 2669889.873 | 1211212.4646
48 | 2669897.56 | 1211385.0284
49 | 2670018.0263 | 1211554.0517
50 | 2670021.1361 | 1211452.4081
51 | 2670066.6042 | 1211457.3227
52 | 2670114.4348 | 1211472.6385
53 | 2670106.0825 | 1211474.019
54 | 2670110.6436 | 1211495.4235
55 | 2670108.8895 | 1211431.103
56 | 2670089.7945 | 1211408.3534
57 | 2670096.4024 | 1211432.8751
58 | 2670100.404 | 1211383.6848
59 | 2670084.3569 | 1211384.7859
60 | 2670092.5416 | 1211366.3238
61 | 2670068.5859 | 1211409.6051
62 | 2669860.8339 | 1211550.6571
63 | 2669866.1279 | 1211568.0512
64 | 2669902.9557 | 1211533.4468
65 | 2669904.536 | 1211479.7939
66 | 2669756.7531 | 1211552.2302
67 | 2669603.2882 | 1211510.3445
68 | 2669581.8964 | 1211384.0902
69 | 2669596.9805 | 1211375.962
70 | 2669522.6754 | 1211425.1333
71 | 2669513.1951 | 1211430.3749
72 | 2669941.8435 | 1211323.8005
73 | 2669911.0129 | 1211352.6413
74 | 2669884.1993 | 1211208.3777
75 | 2669910.683 | 1211394.2255
76 | 2669901.7582 | 1211374.9214
77 | 2670033.2266 | 1211436.1955
78 | 2669996.0882 | 1211433.7582
79 | 2670074.8714 | 1211598.9881
80 | 2670083.8881 | 1211384.8182
81 | 2670090.596 | 1211362.1451
82 | 2669838.1172 | 1211630.5078
83 | 2669861.0205 | 1211618.7908
84 | 2669842.5097 | 1211614.337
85 | 2669864.178 | 1211575.9495
86 | 2669811.282 | 1211606.8234
87 | 2670070.8389 | 1211607.8331
88 | 2670106.6548 | 1211625.2287
89 | 2669926.9631 | 1211529.9981
90 | 2669756.3047 | 1211571.0692
91 | 2669834.6553 | 1211558.1851
92 | 2669831.7939 | 1211558.2183
93 | 2669933.4751 | 1211475.3338
94 | 2669919.3528 | 1211477.4194
95 | 2669940.5577 | 1211474.2879
96 | 2669824.2243 | 1211558.3064
97 | 2669808.9714 | 1211558.4838
98 | 2669808.7124 | 1211558.4868
99 | 2669804.9628 | 1211558.5304
100 | 2669588.7501 | 1211380.3812
101 | 2669916.5751 | 1211400.7138
102 | 2669963.1555 | 1211336.4472
103 | 2669920.7343 | 1211405.5434
104 | 2669972.8607 | 1211342.2064
105 | 2669925.6436 | 1211411.2441
106 | 2669976.4723 | 1211399.6735
107 | 2669990.8965 | 1211373.6785
108 | 2669988.683 | 1211428.2456
109 | 2669994.4782 | 1211368.2873
110 | 2670001.9772 | 1211411.1242
111 | 2670025.3918 | 1211366.3111
112 | 2670014.7666 | 1211348.3229
113 | 2669970.7238 | 1211456.3192
114 | 2670033.3285 | 1211365.8037
115 | 2670048.1076 | 1211364.8589
116 | 2669966.131 | 1211378.7463
117 | 2669967.3356 | 1211355.68
118 | 2669981.1513 | 1211346.9732
119 | 2669937.2183 | 1211424.6845
120 | 2670073.8323 | 1211341.4464
121 | 2670081.3338 | 1211348.4611
122 | 2670052.6828 | 1211342.7242
123 | 2670082.9092 | 1211350.5584
124 | 2670044.6716 | 1211343.2082
125 | 2670054.6249 | 1211364.4463
126 | 2670075.6347 | 1211385.3877
127 | 2670059.5713 | 1211386.4959
128 | 2670038.7786 | 1211387.9194
129 | 2670060.7638 | 1211364.0536
130 | 2670068.6829 | 1211363.5469
131 | 2669878.5634 | 1211508.7942

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99479 | -0.098864 | 0.0037685 | 0.00094448
1 | 0.99345 | -0.12441 | 0 | 0
2 | 0.99515 | -0.092042 | 0 | 0
3 | 0.99317 | -0.12976 | 0 | 0
4 | 0.99305 | -0.13228 | 0.0054695 | 0.0013708
5 | 0.99503 | -0.09432 | 0.0016474 | 0.00041288
6 | 0.99653 | -0.065739 | 0 | 0
7 | 0.99077 | -0.17569 | 0 | 0
8 | 0.99277 | -0.13766 | 0.0022871 | 0.00057321
9 | 0.99705 | -0.055766 | 0 | 0
10 | 0.99666 | -0.0633 | 0 | 0
11 | 1 | 0 | -0.4403 | -0.11219
12 | 0.99083 | -0.17427 | 0 | 0
13 | 0.99692 | -0.058427 | 0.0033473 | 0.00083892
14 | 0.9979 | -0.040316 | 0.0032841 | 0.00082308
15 | 0.99974 | -0.0049592 | 0.0036479 | 0.00091424
16 | 0.99651 | -0.066206 | 0.003358 | 0.00084159
17 | 0.99663 | -0.064708 | 0 | 0
18 | 0.99659 | -0.065457 | 0.0027739 | 0.00069519
19 | 0.99673 | -0.0627 | 0 | 0
20 | 0.97248 | -0.53118 | 0 | 0
21 | 0.97221 | -0.53658 | 0.015662 | 0.0039254
22 | 0.97318 | -0.51742 | 0 | 0
23 | 0.98932 | -0.20322 | 0.0021902 | 0.0005489
24 | 0.99043 | -0.18214 | 0.0019397 | 0.00048613
25 | 0.98848 | -0.21948 | 0 | 0
26 | 0.98838 | -0.22134 | 0.002272 | 0.00056942
27 | 0.98655 | -0.25658 | 0 | 0
28 | 0.98555 | -0.27589 | 0.022204 | 0.0055648
29 | 0.97445 | -0.49245 | 0.0013355 | 0.00033471
30 | 0.98374 | -0.31099 | 0 | 0
31 | 0.98353 | -0.315 | 0.0090554 | 0.0022695
32 | 0.98422 | -0.30171 | 0 | 0
33 | 0.97847 | -0.41357 | 0 | 0
34 | 0.98084 | -0.36738 | 0 | 0
35 | 0.97641 | -0.45387 | 0.011672 | 0.0029253
36 | 0.97474 | -0.48677 | 0 | 0
37 | 0.9745 | -0.49147 | 0.0012919 | 0.00032379
38 | 0.97489 | -0.48379 | 0.0050457 | 0.0012646
39 | 0.97287 | -0.52354 | 0.015391 | 0.0038572
40 | 0.97945 | -0.39453 | 0 | 0
41 | 0.97939 | -0.39575 | 0.015316 | 0.0038385
42 | 0.98307 | -0.32389 | 0.0093023 | 0.0023314
43 | 0.99432 | -0.10922 | 0 | 0
44 | 0.99431 | -0.10945 | 0.0026024 | 0.00065223
45 | 0.9939 | -0.11741 | 0 | 0
46 | 0.99467 | -0.10244 | 0 | 0
47 | 0.99388 | -0.11785 | 0.0017592 | 0.00044091
48 | 0.9961 | -0.07498 | 0 | 0
49 | 0.99503 | -0.094344 | 0.0017413 | 0.00043641
50 | 0.9884 | -0.22137 | 0 | 0
51 | 0.99047 | -0.18151 | 0.011672 | 0.0029252
52 | 0.99255 | -0.14197 | 0 | 0
53 | 0.99261 | -0.14062 | 0 | 0
54 | 0.99235 | -0.14567 | 0.0022862 | 0.00057299
55 | 0.97383 | -0.5052 | 0 | 0
56 | 0.9744 | -0.49395 | 0 | 0
57 | 0.97368 | -0.5081 | 0.012543 | 0.0031437
58 | 0.97553 | -0.47163 | 0 | 0
59 | 0.97496 | -0.48282 | 0 | 0
60 | 0.9762 | -0.45835 | 0.003551 | 0.00088997
61 | 0.97415 | -0.49883 | 0.012543 | 0.0031437
62 | 0.99645 | -0.067391 | 0.0034714 | 0.00087002
63 | 0.99642 | -0.068061 | 0.0017595 | 0.00044096
64 | 0.9968 | -0.060722 | 0.0050223 | 0.0012587
65 | 0.99969 | -0.0060371 | 0.0048608 | 0.0012182
66 | 0.99038 | -0.18307 | 0.0023107 | 0.00057911
67 | 0.98486 | -0.28921 | 0.014181 | 0.0035542
68 | 0.97579 | -0.46596 | 0.0028893 | 0.00072412
69 | 0.97538 | -0.47402 | 0.0049143 | 0.0012316
70 | 0.97184 | -0.54387 | 0.010524 | 0.0026376
71 | 0.97174 | -0.54581 | 0.0097223 | 0.0024366
72 | 0.99451 | -0.10563 | 0.0016827 | 0.00042173
73 | 0.99537 | -0.089056 | 0.0039534 | 0.00099081
74 | 0.99385 | -0.11833 | 0.0038801 | 0.00097244
75 | 0.99587 | -0.079328 | 0.0010031 | 0.00025141
76 | 0.99586 | -0.079504 | 0.0010031 | 0.00025139
77 | 0.98818 | -0.22558 | 0.011674 | 0.0029258
78 | 0.98589 | -0.26977 | 0 | 0
79 | 0.99167 | -0.15887 | 0.002001 | 0.00050151
80 | 0.97496 | -0.48293 | 0.0022576 | 0.00056581
81 | 0.97638 | -0.45484 | 0 | 0
82 | 0.99578 | -0.080376 | 0.0050746 | 0.0012718
83 | 0.9959 | -0.078081 | 0 | 0
84 | 0.9958 | -0.080047 | 0.0032508 | 0.00081473
85 | 0.99633 | -0.069775 | 0.0010481 | 0.00026268
86 | 0.99572 | -0.081529 | 0.0026243 | 0.00065772
87 | 0.99163 | -0.15969 | 0 | 0
88 | 0.99129 | -0.16638 | 0.004741 | 0.0011882
89 | 0.99673 | -0.062066 | 0.0031576 | 0.00079137
90 | 0.99008 | -0.18887 | 0.017296 | 0.0043347
91 | 0.99597 | -0.076739 | 0.0034722 | 0.00087021
92 | 0.99593 | -0.077532 | 0.0024114 | 0.00060436
93 | 0.99947 | -0.010124 | 0.002463 | 0.00061728
94 | 0.99954 | -0.0087523 | 0.0048625 | 0.0012187
95 | 0.99945 | -0.010504 | 0.0030434 | 0.00076275
96 | 0.99583 | -0.079308 | 0.0024863 | 0.00062314
97 | 0.99568 | -0.082221 | 0.0024126 | 0.00060467
98 | 0.99568 | -0.08226 | 0.0036574 | 0.00091664
99 | 0.99566 | -0.082576 | 0.0047949 | 0.0012017
100 | 0.97566 | -0.46855 | 0.0088384 | 0.0022151
101 | 0.99576 | -0.081558 | 0.003602 | 0.00090276
102 | 0.99431 | -0.1094 | 0.0029318 | 0.00073478
103 | 0.99569 | -0.082772 | 0.00099604 | 0.00024963
104 | 0.99426 | -0.11054 | 0 | 0
105 | 0.99563 | -0.084073 | 0.0021654 | 0.00054269
106 | 0.98303 | -0.32506 | 0.0018505 | 0.00046379
107 | 0.98133 | -0.35817 | 0.003431 | 0.00085989
108 | 0.98524 | -0.28218 | 0 | 0
109 | 0.98098 | -0.36499 | 0 | 0
110 | 0.98501 | -0.28673 | 0.011695 | 0.0029311
111 | 0.9794 | -0.39579 | 0.0019447 | 0.00048739
112 | 0.98089 | -0.36669 | 0.0033013 | 0.00082738
113 | 0.9855 | -0.27721 | 0.011698 | 0.0029317
114 | 0.97901 | -0.40343 | 0.001944 | 0.00048721
115 | 0.9783 | -0.41716 | 0 | 0
116 | 0.99417 | -0.11214 | 0.0016611 | 0.00041632
117 | 0.99421 | -0.11146 | 0.001919 | 0.00048094
118 | 0.99424 | -0.1109 | 0.0021181 | 0.00053086
119 | 0.9955 | -0.086466 | 0.0076712 | 0.0019226
120 | 0.97627 | -0.45717 | 0 | 0
121 | 0.9763 | -0.45641 | 0 | 0
122 | 0.97619 | -0.45874 | 0.0020313 | 0.00050908
123 | 0.97631 | -0.45621 | 0.0013078 | 0.00032777
124 | 0.97617 | -0.45904 | 0.0020313 | 0.00050908
125 | 0.978 | -0.4232 | 0 | 0
126 | 0.97487 | -0.48456 | 0.0020646 | 0.00051745
127 | 0.97474 | -0.48711 | 0 | 0
128 | 0.97458 | -0.49041 | 0.0086499 | 0.0021679
129 | 0.9777 | -0.42891 | 0.0019682 | 0.00049327
130 | 0.97734 | -0.43599 | 0.0019682 | 0.00049327
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12839 | 0.032742 | -0.12824 | -0.032643 | 0.00015817 | 9.8864e-05 | 0.19225 | 0.19226 | 0.19226 | 0.99479 | -0.098864 | 0.99345 | -0.12441 | 13.2043
1 | -0.13216 | -0.033686 | 0.13221 | 0.033714 | 4.3532e-05 | 2.7245e-05 | 0.19789 | 0.19789 | 0.19789 | 0.99479 | -0.098864 | 0.99515 | -0.092042 | 13.5914
2 | 0.11143 | 0.028428 | -0.1114 | -0.02841 | 2.8759e-05 | 1.837e-05 | 0.16709 | 0.16709 | 0.16709 | 0.99345 | -0.12441 | 0.99317 | -0.12976 | 45.9026
3 | 0.016804 | 0.0042147 | -0.016797 | -0.004211 | 6.2989e-06 | 3.6881e-06 | 0.02517 | 0.02517 | 0.02517 | 0.99345 | -0.12441 | 0.99305 | -0.13228 | 6.9148
4 | 0.0033891 | 0.00084902 | -0.0033887 | -0.00084928 | 3.6769e-07 | -2.6069e-07 | 0.0050674 | 0.0050676 | 0.0050676 | 0.99515 | -0.092042 | 0.99503 | -0.09432 | 1.3922
5 | -0.1356 | -0.034563 | 0.13577 | 0.034671 | 0.00017238 | 0.000108 | 0.20296 | 0.20296 | 0.20296 | 0.99515 | -0.092042 | 0.99653 | -0.065739 | 13.9395
6 | 0.1114 | 0.02841 | -0.11116 | -0.028253 | 0.00024647 | 0.00015744 | 0.16709 | 0.16709 | 0.16709 | 0.99317 | -0.12976 | 0.99077 | -0.17569 | 45.9027
7 | 0.011328 | 0.0028402 | -0.011325 | -0.0028387 | 2.9049e-06 | 1.5114e-06 | 0.016974 | 0.016974 | 0.016974 | 0.99305 | -0.13228 | 0.99277 | -0.13766 | 4.6633
8 | 0.0017413 | 0.0004364 | -0.0017413 | -0.00043641 | 1.9747e-09 | -8.823e-09 | 0.002604 | 0.002604 | 0.002604 | 0.99503 | -0.09432 | 0.99503 | -0.094344 | 0.71538
9 | 0.0033581 | 0.00084154 | -0.003358 | -0.00084159 | 7.4727e-08 | -5.543e-08 | 0.0050142 | 0.0050143 | 0.0050143 | 0.99653 | -0.065739 | 0.99651 | -0.066206 | 1.3776
10 | -0.13913 | -0.035512 | 0.13957 | 0.03579 | 0.00044343 | 0.00027808 | 0.20797 | 0.20797 | 0.20797 | 0.99653 | -0.065739 | 1 | 0 | 14.2838
11 | 0.099483 | 0.025326 | -0.099264 | -0.025186 | 0.00021861 | 0.00013958 | 0.14955 | 0.14955 | 0.14955 | 0.99077 | -0.17569 | 0.9884 | -0.22137 | 41.0855
12 | 0.011675 | 0.0029269 | -0.011672 | -0.0029252 | 3.2358e-06 | 1.7096e-06 | 0.017535 | 0.017535 | 0.017535 | 0.99077 | -0.17569 | 0.99047 | -0.18151 | 4.8172
13 | 0.0090377 | 0.0022655 | -0.0090364 | -0.0022649 | 1.2748e-06 | 5.7637e-07 | 0.013546 | 0.013546 | 0.013546 | 0.99277 | -0.13766 | 0.99261 | -0.14062 | 3.7215
14 | 0.036503 | 0.0091608 | -0.03649 | -0.0091525 | 1.3111e-05 | 8.2375e-06 | 0.054482 | 0.054482 | 0.054482 | 0.99705 | -0.055766 | 0.99666 | -0.0633 | 14.9675
15 | -0.23436 | -0.059864 | 0.235 | 0.060267 | 0.0006337 | 0.00040268 | 0.35016 | 0.35016 | 0.35016 | 0.99705 | -0.055766 | 1 | 0 | 24.0497
16 | 0.18633 | 0.047813 | -0.18526 | -0.047139 | 0.0010648 | 0.00067387 | 0.27848 | 0.27848 | 0.27848 | 0.99705 | -0.055766 | 0.99083 | -0.17427 | 19.1263
17 | 0.01153 | 0.0028899 | -0.011528 | -0.0028892 | 1.4615e-06 | 7.6372e-07 | 0.017207 | 0.017207 | 0.017207 | 0.99705 | -0.055766 | 0.99692 | -0.058427 | 4.7273
18 | 0.022723 | 0.0057003 | -0.022718 | -0.0056976 | 4.4301e-06 | 2.7016e-06 | 0.033927 | 0.033927 | 0.033927 | 0.99666 | -0.0633 | 0.99645 | -0.067391 | 9.3206
19 | 0.013767 | 0.0034522 | -0.013764 | -0.0034505 | 3.1225e-06 | 1.7416e-06 | 0.020555 | 0.020555 | 0.020555 | 0.99666 | -0.0633 | 0.99642 | -0.068061 | 5.647
20 | 0.045205 | 0.011399 | -0.045117 | -0.011344 | 8.705e-05 | 5.5041e-05 | 0.06729 | 0.06729 | 0.06729 | 1 | 0 | 0.9979 | -0.040316 | 18.4862
21 | 0.018885 | 0.0047349 | -0.01888 | -0.0047323 | 4.4619e-06 | 2.658e-06 | 0.028101 | 0.028101 | 0.028101 | 1 | 0 | 0.99974 | -0.0049592 | 7.7201
22 | 0.1637 | 0.041731 | -0.16348 | -0.041587 | 0.00022836 | 0.00014408 | 0.2461 | 0.2461 | 0.2461 | 0.99083 | -0.17427 | 0.98932 | -0.20322 | 16.9025
23 | 0.02156 | 0.0054082 | -0.021552 | -0.0054032 | 8.0818e-06 | 4.9077e-06 | 0.03238 | 0.03238 | 0.03238 | 0.99083 | -0.17427 | 0.99043 | -0.18214 | 8.8955
24 | 0.008181 | 0.0020503 | -0.0081801 | -0.0020499 | 8.9451e-07 | 3.6393e-07 | 0.012211 | 0.012211 | 0.012211 | 0.99692 | -0.058427 | 0.9968 | -0.060722 | 3.3547
25 | 0.041833 | 0.010521 | -0.041789 | -0.010493 | 4.4677e-05 | 2.8194e-05 | 0.062393 | 0.062393 | 0.062393 | 0.9979 | -0.040316 | 0.99673 | -0.0627 | 17.1409
26 | 0.015232 | 0.003818 | -0.015231 | -0.0038176 | 7.8219e-07 | 4.474e-07 | 0.022672 | 0.022672 | 0.022672 | 0.99974 | -0.0049592 | 0.99969 | -0.0060371 | 6.2285
27 | 0.002774 | 0.00069506 | -0.0027739 | -0.00069519 | 9.8917e-08 | -1.3708e-07 | 0.0041416 | 0.0041417 | 0.0041417 | 0.99663 | -0.064708 | 0.99659 | -0.065457 | 1.1378
28 | -0.002774 | -0.00069506 | 0.0027742 | 0.00069469 | 2.6529e-07 | -3.6774e-07 | 0.0041416 | 0.0041414 | 0.0041416 | 0.99663 | -0.064708 | 0.99673 | -0.0627 | 1.1378
29 | 0.039014 | 0.0097983 | -0.038992 | -0.009784 | 2.2847e-05 | 1.4388e-05 | 0.058252 | 0.058252 | 0.058252 | 0.99673 | -0.0627 | 0.9961 | -0.07498 | 16.0032
30 | 0.015666 | 0.0039277 | -0.015662 | -0.0039254 | 4.0336e-06 | 2.3494e-06 | 0.023972 | 0.023972 | 0.023972 | 0.97248 | -0.53118 | 0.97221 | -0.53658 | 6.5857
31 | -0.015666 | -0.0039277 | 0.015677 | 0.0039337 | 1.0274e-05 | 5.9832e-06 | 0.023972 | 0.023972 | 0.023972 | 0.97248 | -0.53118 | 0.97318 | -0.51742 | 6.5857
32 | -0.015677 | -0.0039337 | 0.015695 | 0.0039446 | 1.8692e-05 | 1.0884e-05 | 0.023972 | 0.023971 | 0.023972 | 0.97318 | -0.51742 | 0.97445 | -0.49245 | 6.5856
33 | 0.16129 | 0.041038 | -0.16116 | -0.040958 | 0.00012635 | 7.9693e-05 | 0.24281 | 0.24281 | 0.24281 | 0.98932 | -0.20322 | 0.98848 | -0.21948 | 16.6763
34 | 0.019612 | 0.0049171 | -0.019611 | -0.0049166 | 8.7319e-07 | 5.2433e-07 | 0.029465 | 0.029465 | 0.029465 | 0.99043 | -0.18214 | 0.99038 | -0.18307 | 8.0949
35 | 0.0022722 | 0.00056896 | -0.002272 | -0.00056942 | 2.004e-07 | -4.5722e-07 | 0.0034203 | 0.0034205 | 0.0034205 | 0.98848 | -0.21948 | 0.98838 | -0.22134 | 0.93971
36 | 0.15889 | 0.040389 | -0.1586 | -0.040211 | 0.00028333 | 0.00017863 | 0.23939 | 0.23939 | 0.23939 | 0.98848 | -0.21948 | 0.98655 | -0.25658 | 16.4414
37 | 0.1586 | 0.040211 | -0.15846 | -0.040118 | 0.00014706 | 9.2722e-05 | 0.23939 | 0.23939 | 0.23939 | 0.98655 | -0.25658 | 0.98555 | -0.27589 | 16.4415
38 | 0.13625 | 0.034553 | -0.13617 | -0.034499 | 8.7211e-05 | 5.4697e-05 | 0.20586 | 0.20586 | 0.20586 | 0.98555 | -0.27589 | 0.98486 | -0.28921 | 14.139
39 | -0.017031 | -0.0042793 | 0.017032 | 0.0042798 | 7.9868e-07 | 4.7194e-07 | 0.026011 | 0.026011 | 0.026011 | 0.97445 | -0.49245 | 0.9745 | -0.49147 | 7.1458
40 | 0.12186 | 0.030865 | -0.12183 | -0.03085 | 2.3487e-05 | 1.4657e-05 | 0.18444 | 0.18444 | 0.18444 | 0.98374 | -0.31099 | 0.98353 | -0.315 | 12.6675
41 | -0.12186 | -0.030865 | 0.12191 | 0.030899 | 5.4352e-05 | 3.392e-05 | 0.18444 | 0.18444 | 0.18444 | 0.98374 | -0.31099 | 0.98422 | -0.30171 | 12.6675
42 | 0.11278 | 0.028581 | -0.11273 | -0.028551 | 4.8107e-05 | 2.9896e-05 | 0.17074 | 0.17074 | 0.17074 | 0.98353 | -0.315 | 0.98307 | -0.32389 | 11.7266
43 | -0.12191 | -0.030899 | 0.12198 | 0.030944 | 7.3237e-05 | 4.5704e-05 | 0.18444 | 0.18444 | 0.18444 | 0.98422 | -0.30171 | 0.98486 | -0.28921 | 12.6675
44 | -0.087681 | -0.022117 | 0.087875 | 0.022236 | 0.00019436 | 0.00011852 | 0.13339 | 0.13339 | 0.13339 | 0.97847 | -0.41357 | 0.98084 | -0.36738 | 9.1616
45 | 0.087681 | 0.022117 | -0.087512 | -0.022014 | 0.0001688 | 0.00010296 | 0.13339 | 0.13339 | 0.13339 | 0.97847 | -0.41357 | 0.97641 | -0.45387 | 9.1617
46 | -0.10321 | -0.026086 | 0.10343 | 0.026219 | 0.00021572 | 0.00013332 | 0.15666 | 0.15666 | 0.15666 | 0.98084 | -0.36738 | 0.98307 | -0.32389 | 10.7596
47 | 0.015336 | 0.0038505 | -0.015317 | -0.003839 | 1.9833e-05 | 1.1462e-05 | 0.023269 | 0.02327 | 0.02327 | 0.98084 | -0.36738 | 0.97945 | -0.39453 | 6.3928
48 | 0.07584 | 0.019089 | -0.075796 | -0.019063 | 4.3803e-05 | 2.6286e-05 | 0.11561 | 0.11561 | 0.11561 | 0.97641 | -0.45387 | 0.97579 | -0.46596 | 7.9401
49 | 0.018328 | 0.004606 | -0.018324 | -0.0046035 | 4.1062e-06 | 2.4537e-06 | 0.027983 | 0.027983 | 0.027983 | 0.97474 | -0.48677 | 0.9745 | -0.49147 | 7.6878
50 | -0.054048 | -0.013589 | 0.054055 | 0.013594 | 7.6942e-06 | 4.8867e-06 | 0.082524 | 0.082524 | 0.082524 | 0.97474 | -0.48677 | 0.97489 | -0.48379 | 22.6714
51 | 0.03572 | 0.0089831 | -0.035657 | -0.0089438 | 6.2612e-05 | 3.9373e-05 | 0.054541 | 0.054541 | 0.054541 | 0.97474 | -0.48677 | 0.97287 | -0.52354 | 14.9838
52 | -0.059101 | -0.014859 | 0.059129 | 0.014876 | 2.7591e-05 | 1.7207e-05 | 0.090226 | 0.090225 | 0.090226 | 0.97489 | -0.48379 | 0.97538 | -0.47402 | 12.3936
53 | 0.020267 | 0.0050865 | -0.020247 | -0.0050746 | 1.9629e-05 | 1.1887e-05 | 0.031001 | 0.031001 | 0.031001 | 0.97287 | -0.52354 | 0.97184 | -0.54387 | 8.5168
54 | 0.015317 | 0.003839 | -0.015316 | -0.0038385 | 8.9222e-07 | 5.1572e-07 | 0.02327 | 0.02327 | 0.02327 | 0.97945 | -0.39453 | 0.97939 | -0.39575 | 6.3928
55 | 0.0026024 | 0.00065218 | -0.0026024 | -0.00065223 | 2.8945e-08 | -4.748e-08 | 0.0038946 | 0.0038946 | 0.0038946 | 0.99432 | -0.10922 | 0.99431 | -0.10945 | 1.0699
56 | 0.0056417 | 0.0014137 | -0.0056395 | -0.0014133 | 2.2001e-06 | 3.4098e-07 | 0.0084428 | 0.0084432 | 0.0084432 | 0.99432 | -0.10922 | 0.9939 | -0.11741 | 2.3196
57 | -0.0082442 | -0.0020659 | 0.0082469 | 0.002067 | 2.6634e-06 | 1.0991e-06 | 0.012337 | 0.012337 | 0.012337 | 0.99432 | -0.10922 | 0.99467 | -0.10244 | 3.3894
58 | 0.0056395 | 0.0014133 | -0.0056394 | -0.0014133 | 1.1835e-07 | 1.8372e-08 | 0.0084432 | 0.0084432 | 0.0084432 | 0.9939 | -0.11741 | 0.99388 | -0.11785 | 2.3196
59 | 0.010316 | 0.0025857 | -0.010315 | -0.0025849 | 1.5707e-06 | 7.7706e-07 | 0.015433 | 0.015433 | 0.015433 | 0.99467 | -0.10244 | 0.99451 | -0.10563 | 4.2399
60 | -0.018563 | -0.0046526 | 0.018575 | 0.0046597 | 1.1842e-05 | 7.047e-06 | 0.027771 | 0.02777 | 0.027771 | 0.99467 | -0.10244 | 0.99537 | -0.089056 | 7.6293
61 | 0.0038802 | 0.00097241 | -0.0038801 | -0.00097244 | 8.8493e-08 | -3.3977e-08 | 0.0058093 | 0.0058094 | 0.0058094 | 0.99388 | -0.11785 | 0.99385 | -0.11833 | 1.596
62 | 0.015445 | 0.0038727 | -0.015441 | -0.0038709 | 3.1991e-06 | 1.8388e-06 | 0.023073 | 0.023073 | 0.023073 | 0.9961 | -0.07498 | 0.99587 | -0.079328 | 6.3386
63 | 0.023547 | 0.0059112 | -0.023542 | -0.0059081 | 5.079e-06 | 3.1082e-06 | 0.035179 | 0.035179 | 0.035179 | 0.9961 | -0.07498 | 0.99586 | -0.079504 | 9.6646
64 | 0.011676 | 0.002927 | -0.011674 | -0.0029258 | 2.3416e-06 | 1.2397e-06 | 0.017579 | 0.017579 | 0.017579 | 0.9884 | -0.22137 | 0.98818 | -0.22558 | 4.8293
65 | 0.087588 | 0.022259 | -0.087385 | -0.022129 | 0.00020359 | 0.0001299 | 0.13197 | 0.13197 | 0.13197 | 0.9884 | -0.22137 | 0.98589 | -0.26977 | 36.2563
66 | -0.0090358 | -0.0022646 | 0.0090364 | 0.0022649 | 5.8093e-07 | 2.6268e-07 | 0.013546 | 0.013546 | 0.013546 | 0.99255 | -0.14197 | 0.99261 | -0.14062 | 3.7216
67 | 0.0090358 | 0.0022646 | -0.0090342 | -0.0022639 | 1.593e-06 | 7.2039e-07 | 0.013546 | 0.013547 | 0.013547 | 0.99255 | -0.14197 | 0.99235 | -0.14567 | 3.7216
68 | 0.006748 | 0.0016909 | -0.0067437 | -0.0016896 | 4.2401e-06 | 1.2879e-06 | 0.010118 | 0.010119 | 0.010119 | 0.99235 | -0.14567 | 0.99167 | -0.15887 | 2.7799
69 | -0.012545 | -0.0031446 | 0.012552 | 0.0031483 | 6.724e-06 | 3.6959e-06 | 0.019169 | 0.019169 | 0.019169 | 0.97383 | -0.5052 | 0.9744 | -0.49395 | 5.2663
70 | 0.012545 | 0.0031446 | -0.012543 | -0.0031437 | 1.738e-06 | 9.554e-07 | 0.019169 | 0.019169 | 0.019169 | 0.97383 | -0.5052 | 0.97368 | -0.5081 | 5.2663
71 | 0.012546 | 0.0031453 | -0.012543 | -0.0031437 | 2.9163e-06 | 1.6026e-06 | 0.01916 | 0.01916 | 0.01916 | 0.9744 | -0.49395 | 0.97415 | -0.49883 | 5.2638
72 | -0.025098 | -0.0062936 | 0.025112 | 0.0063018 | 1.3325e-05 | 8.2266e-06 | 0.038329 | 0.038329 | 0.038329 | 0.9744 | -0.49395 | 0.97496 | -0.48282 | 10.53
73 | 0.038107 | 0.0095673 | -0.038087 | -0.0095545 | 2.0325e-05 | 1.2808e-05 | 0.058133 | 0.058133 | 0.058133 | 0.97553 | -0.47163 | 0.97496 | -0.48282 | 15.9705
74 | -0.038107 | -0.0095673 | 0.038131 | 0.0095825 | 2.4165e-05 | 1.5227e-05 | 0.058133 | 0.058133 | 0.058133 | 0.97553 | -0.47163 | 0.9762 | -0.45835 | 15.9705
75 | 0.012975 | 0.0032527 | -0.012975 | -0.0032526 | 6.9117e-08 | 3.8374e-08 | 0.019804 | 0.019804 | 0.019804 | 0.97496 | -0.48282 | 0.97496 | -0.48293 | 5.4406
76 | -0.041683 | -0.010473 | 0.041689 | 0.010477 | 6.98e-06 | 4.4096e-06 | 0.063545 | 0.063545 | 0.063545 | 0.9762 | -0.45835 | 0.97638 | -0.45484 | 17.4575
77 | 0.019247 | 0.0048276 | -0.019238 | -0.0048225 | 8.5726e-06 | 5.1262e-06 | 0.028743 | 0.028743 | 0.028743 | 0.99645 | -0.067391 | 0.99597 | -0.076739 | 7.8964
78 | 0.012004 | 0.0030095 | -0.012003 | -0.003009 | 9.805e-07 | 5.2156e-07 | 0.017927 | 0.017927 | 0.017927 | 0.99642 | -0.068061 | 0.99633 | -0.069775 | 4.9251
79 | 0.0031578 | 0.00079118 | -0.0031576 | -0.00079137 | 2.0211e-07 | -1.8679e-07 | 0.0047139 | 0.004714 | 0.004714 | 0.9968 | -0.060722 | 0.99673 | -0.062066 | 1.2951
80 | 0.010371 | 0.0025993 | -0.010369 | -0.0025987 | 1.3414e-06 | 6.617e-07 | 0.015437 | 0.015437 | 0.015437 | 0.99969 | -0.0060371 | 0.99954 | -0.0087523 | 4.2408
81 | 0.0173 | 0.0043375 | -0.017296 | -0.0043347 | 4.7748e-06 | 2.8134e-06 | 0.025994 | 0.025994 | 0.025994 | 0.99038 | -0.18307 | 0.99008 | -0.18887 | 7.1412
82 | 0.072907 | 0.018338 | -0.072898 | -0.018333 | 9.0344e-06 | 5.3927e-06 | 0.1112 | 0.1112 | 0.1112 | 0.97579 | -0.46596 | 0.97566 | -0.46855 | 7.6375
83 | -0.064043 | -0.016107 | 0.06406 | 0.016118 | 1.6727e-05 | 1.0472e-05 | 0.097722 | 0.097722 | 0.097722 | 0.97538 | -0.47402 | 0.97566 | -0.46855 | 13.4234
84 | 0.0097232 | 0.0024371 | -0.0097223 | -0.0024366 | 9.0036e-07 | 4.4202e-07 | 0.014887 | 0.014888 | 0.014888 | 0.97184 | -0.54387 | 0.97174 | -0.54581 | 4.09
85 | 0.0086322 | 0.0021632 | -0.0086306 | -0.0021625 | 1.5502e-06 | 6.7066e-07 | 0.012916 | 0.012916 | 0.012916 | 0.99451 | -0.10563 | 0.99431 | -0.1094 | 3.5483
86 | -0.022529 | -0.0056505 | 0.022539 | 0.0056567 | 1.0263e-05 | 6.2545e-06 | 0.03368 | 0.03368 | 0.03368 | 0.99537 | -0.089056 | 0.99586 | -0.079504 | 9.2529
87 | 0.014438 | 0.0036195 | -0.014437 | -0.0036186 | 1.5342e-06 | 8.6753e-07 | 0.021574 | 0.021574 | 0.021574 | 0.99587 | -0.079328 | 0.99576 | -0.081558 | 5.9269
88 | 0.011702 | 0.0029339 | -0.011698 | -0.0029317 | 4.1518e-06 | 2.2048e-06 | 0.017662 | 0.017663 | 0.017663 | 0.98589 | -0.26977 | 0.9855 | -0.27721 | 4.8523
89 | 0.075683 | 0.019195 | -0.075637 | -0.019166 | 4.5154e-05 | 2.8781e-05 | 0.11431 | 0.11431 | 0.11431 | 0.98589 | -0.26977 | 0.98524 | -0.28218 | 31.404
90 | 0.0047427 | 0.0011881 | -0.0047425 | -0.0011881 | 1.8461e-07 | -7.2623e-09 | 0.0071163 | 0.0071163 | 0.0071163 | 0.99167 | -0.15887 | 0.99163 | -0.15969 | 1.955
91 | 0.010718 | 0.0026868 | -0.010717 | -0.0026864 | 8.3016e-07 | 4.2815e-07 | 0.016358 | 0.016358 | 0.016358 | 0.97496 | -0.48293 | 0.97487 | -0.48456 | 4.494
92 | 0.0053712 | 0.0013458 | -0.0053709 | -0.0013457 | 3.5093e-07 | 4.9934e-08 | 0.0081857 | 0.0081857 | 0.0081857 | 0.97638 | -0.45484 | 0.97631 | -0.45621 | 2.2488
93 | -0.047061 | -0.011823 | 0.047103 | 0.01185 | 4.2368e-05 | 2.684e-05 | 0.071731 | 0.071731 | 0.071731 | 0.97638 | -0.45484 | 0.97734 | -0.43599 | 19.7063
94 | -0.0050746 | -0.0012718 | 0.0050752 | 0.0012718 | 5.5476e-07 | 2.0335e-08 | 0.0075831 | 0.007583 | 0.0075831 | 0.99578 | -0.080376 | 0.9959 | -0.078081 | 2.0833
95 | 0.0058759 | 0.0014722 | -0.0058753 | -0.0014721 | 5.503e-07 | 1.0448e-07 | 0.0087792 | 0.0087793 | 0.0087793 | 0.9959 | -0.078081 | 0.9958 | -0.080047 | 2.4119
96 | -0.010951 | -0.0027441 | 0.010955 | 0.0027463 | 4.3343e-06 | 2.2119e-06 | 0.016362 | 0.016362 | 0.016362 | 0.9959 | -0.078081 | 0.99633 | -0.069775 | 4.4951
97 | 0.0026245 | 0.00065742 | -0.0026243 | -0.00065772 | 1.8525e-07 | -2.9925e-07 | 0.0039217 | 0.0039218 | 0.0039218 | 0.9958 | -0.080047 | 0.99572 | -0.081529 | 1.0774
98 | 0.0047425 | 0.0011881 | -0.004741 | -0.0011882 | 1.5122e-06 | -5.9029e-08 | 0.0071163 | 0.0071167 | 0.0071167 | 0.99163 | -0.15969 | 0.99129 | -0.16638 | 1.9551
99 | 0.015766 | 0.0039523 | -0.015765 | -0.0039519 | 5.9542e-07 | 3.4383e-07 | 0.023556 | 0.023556 | 0.023556 | 0.99597 | -0.076739 | 0.99593 | -0.077532 | 6.4713
100 | 0.013354 | 0.0033476 | -0.013353 | -0.0033469 | 1.1301e-06 | 6.2479e-07 | 0.019953 | 0.019953 | 0.019953 | 0.99593 | -0.077532 | 0.99583 | -0.079308 | 5.4815
101 | -0.0055064 | -0.00138 | 0.0055068 | 0.00138 | 3.5977e-07 | 4.3155e-08 | 0.0081979 | 0.0081979 | 0.0081979 | 0.99947 | -0.010124 | 0.99954 | -0.0087523 | 2.2522
102 | 0.0030434 | 0.00076269 | -0.0030434 | -0.00076275 | 5.512e-08 | -5.8549e-08 | 0.0045311 | 0.0045311 | 0.0045311 | 0.99947 | -0.010124 | 0.99945 | -0.010504 | 1.2448
103 | 0.010867 | 0.0027238 | -0.010865 | -0.002723 | 1.5082e-06 | 7.668e-07 | 0.016237 | 0.016238 | 0.016238 | 0.99583 | -0.079308 | 0.99568 | -0.082221 | 4.4609
104 | 0.0084524 | 0.0021184 | -0.0084524 | -0.0021184 | 1.5499e-08 | 6.5505e-09 | 0.012632 | 0.012632 | 0.012632 | 0.99568 | -0.082221 | 0.99568 | -0.08226 | 3.4703
105 | 0.004795 | 0.0012017 | -0.0047949 | -0.0012017 | 7.2212e-08 | -2.5562e-09 | 0.007166 | 0.007166 | 0.007166 | 0.99568 | -0.08226 | 0.99566 | -0.082576 | 1.9687
106 | 0.010835 | 0.0027158 | -0.010834 | -0.0027155 | 6.2657e-07 | 3.181e-07 | 0.016191 | 0.016191 | 0.016191 | 0.99576 | -0.081558 | 0.99569 | -0.082772 | 4.4481
107 | 0.0056988 | 0.0014277 | -0.0056985 | -0.0014277 | 3.078e-07 | 5.0623e-08 | 0.0085282 | 0.0085283 | 0.0085283 | 0.99431 | -0.1094 | 0.99426 | -0.11054 | 2.3429
108 | 0.009838 | 0.0024659 | -0.0098374 | -0.0024656 | 6.0985e-07 | 2.9246e-07 | 0.014703 | 0.014703 | 0.014703 | 0.99569 | -0.082772 | 0.99563 | -0.084073 | 4.0392
109 | 0.0021182 | 0.00053076 | -0.0021181 | -0.00053086 | 3.604e-08 | -1.0096e-07 | 0.0031701 | 0.0031701 | 0.0031701 | 0.99426 | -0.11054 | 0.99424 | -0.1109 | 0.87091
110 | 0.0035803 | 0.0008969 | -0.0035802 | -0.00089699 | 1.5688e-07 | -8.8557e-08 | 0.0053582 | 0.0053583 | 0.0053583 | 0.99426 | -0.11054 | 0.99421 | -0.11146 | 1.4721
111 | 0.007672 | 0.0019229 | -0.0076712 | -0.0019226 | 8.7453e-07 | 3.2906e-07 | 0.011466 | 0.011466 | 0.011466 | 0.99563 | -0.084073 | 0.9955 | -0.086466 | 3.1501
112 | 0.061958 | 0.015686 | -0.061859 | -0.015624 | 9.8304e-05 | 6.2538e-05 | 0.093842 | 0.093842 | 0.093842 | 0.98303 | -0.32506 | 0.98133 | -0.35817 | 25.7809
113 | -0.063808 | -0.01615 | 0.06394 | 0.016234 | 0.00013163 | 8.3764e-05 | 0.096643 | 0.096643 | 0.096643 | 0.98303 | -0.32506 | 0.98524 | -0.28218 | 26.5504
114 | 0.058428 | 0.014764 | -0.058409 | -0.014752 | 1.9096e-05 | 1.214e-05 | 0.08864 | 0.08864 | 0.08864 | 0.98133 | -0.35817 | 0.98098 | -0.36499 | 24.3516
115 | 0.011698 | 0.0029324 | -0.011695 | -0.0029311 | 2.5349e-06 | 1.3466e-06 | 0.017667 | 0.017667 | 0.017667 | 0.98524 | -0.28218 | 0.98501 | -0.28673 | 4.8537
116 | 0.055108 | 0.013925 | -0.055026 | -0.013873 | 8.1248e-05 | 5.1608e-05 | 0.083632 | 0.083632 | 0.083632 | 0.98098 | -0.36499 | 0.9794 | -0.39579 | 22.9758
117 | 0.0033016 | 0.00082719 | -0.0033013 | -0.00082738 | 2.6816e-07 | -1.8831e-07 | 0.0050079 | 0.0050081 | 0.0050081 | 0.98098 | -0.36499 | 0.98089 | -0.36669 | 1.3758
118 | 0.053082 | 0.013386 | -0.053062 | -0.013373 | 1.9412e-05 | 1.2323e-05 | 0.080677 | 0.080678 | 0.080678 | 0.9794 | -0.39579 | 0.97901 | -0.40343 | 22.1641
119 | 0.051118 | 0.012886 | -0.051085 | -0.012865 | 3.3548e-05 | 2.1284e-05 | 0.077723 | 0.077723 | 0.077723 | 0.97901 | -0.40343 | 0.9783 | -0.41716 | 21.3524
120 | 0.051085 | 0.012865 | -0.05107 | -0.012855 | 1.4749e-05 | 9.3579e-06 | 0.077723 | 0.077723 | 0.077723 | 0.9783 | -0.41716 | 0.978 | -0.4232 | 21.3524
121 | -0.0016611 | -0.00041632 | 0.0016612 | 0.00041605 | 5.4263e-08 | -2.6882e-07 | 0.0024863 | 0.0024862 | 0.0024863 | 0.99417 | -0.11214 | 0.99421 | -0.11146 | 0.68305
122 | -0.0040629 | -0.001018 | 0.004063 | 0.001018 | 1.4747e-07 | -3.3853e-08 | 0.0061925 | 0.0061925 | 0.0061925 | 0.97627 | -0.45717 | 0.9763 | -0.45641 | 1.7012
123 | 0.0040629 | 0.001018 | -0.0040626 | -0.0010181 | 3.0469e-07 | -6.9908e-08 | 0.0061925 | 0.0061926 | 0.0061926 | 0.97627 | -0.45717 | 0.97619 | -0.45874 | 1.7013
124 | -0.004063 | -0.001018 | 0.0040631 | 0.001018 | 3.7721e-08 | -8.6612e-09 | 0.0061925 | 0.0061924 | 0.0061925 | 0.9763 | -0.45641 | 0.97631 | -0.45621 | 1.7012
125 | 0.0020313 | 0.000509 | -0.0020313 | -0.00050908 | 2.8854e-08 | -8.1869e-08 | 0.0030963 | 0.0030963 | 0.0030963 | 0.97619 | -0.45874 | 0.97617 | -0.45904 | 0.85064
126 | 0.05107 | 0.012855 | -0.051056 | -0.012847 | 1.3935e-05 | 8.8412e-06 | 0.077723 | 0.077723 | 0.077723 | 0.978 | -0.4232 | 0.9777 | -0.42891 | 21.3524
127 | 0.0086523 | 0.0021689 | -0.0086512 | -0.0021685 | 1.0532e-06 | 4.7329e-07 | 0.013207 | 0.013207 | 0.013207 | 0.97487 | -0.48456 | 0.97474 | -0.48711 | 3.6282
128 | 0.0086512 | 0.0021685 | -0.0086499 | -0.0021679 | 1.3592e-06 | 6.1092e-07 | 0.013207 | 0.013207 | 0.013207 | 0.97474 | -0.48711 | 0.97458 | -0.49041 | 3.6283
129 | 0.049088 | 0.012353 | -0.049071 | -0.012343 | 1.6617e-05 | 1.0535e-05 | 0.074727 | 0.074728 | 0.074728 | 0.9777 | -0.42891 | 0.97734 | -0.43599 | 20.5295

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4403 | 0.11219

## res_load
| p_mw | q_mvar
0 | 0.0037685 | 0.00094448
1 | 0.0054695 | 0.0013708
2 | 0.0016474 | 0.00041288
3 | 0.0022871 | 0.00057321
4 | 0.0033473 | 0.00083892
5 | 0.0032841 | 0.00082308
6 | 0.0036479 | 0.00091424
7 | 0.003358 | 0.00084159
8 | 0.0027739 | 0.00069519
9 | 0.015662 | 0.0039254
10 | 0.0021902 | 0.0005489
11 | 0.0019397 | 0.00048613
12 | 0.002272 | 0.00056942
13 | 0.022204 | 0.0055648
14 | 0.0013355 | 0.00033471
15 | 0.0090554 | 0.0022695
16 | 0.011672 | 0.0029253
17 | 0.0012919 | 0.00032379
18 | 0.0050457 | 0.0012646
19 | 0.015391 | 0.0038572
20 | 0.015316 | 0.0038385
21 | 0.0093023 | 0.0023314
22 | 0.0026024 | 0.00065223
23 | 0.0017592 | 0.00044091
24 | 0.0017413 | 0.00043641
25 | 0.011672 | 0.0029252
26 | 0.0022862 | 0.00057299
27 | 0.012543 | 0.0031437
28 | 0.003551 | 0.00088997
29 | 0.012543 | 0.0031437
30 | 0.0034714 | 0.00087002
31 | 0.0017595 | 0.00044096
32 | 0.0050223 | 0.0012587
33 | 0.0048608 | 0.0012182
34 | 0.0023107 | 0.00057911
35 | 0.014181 | 0.0035542
36 | 0.0028893 | 0.00072412
37 | 0.0049143 | 0.0012316
38 | 0.010524 | 0.0026376
39 | 0.0097223 | 0.0024366
40 | 0.0016827 | 0.00042173
41 | 0.0039534 | 0.00099081
42 | 0.0038801 | 0.00097244
43 | 0.0010031 | 0.00025141
44 | 0.0010031 | 0.00025139
45 | 0.011674 | 0.0029258
46 | 0.002001 | 0.00050151
47 | 0.0022576 | 0.00056581
48 | 0.0050746 | 0.0012718
49 | 0.0032508 | 0.00081473
50 | 0.0010481 | 0.00026268
51 | 0.0026243 | 0.00065772
52 | 0.004741 | 0.0011882
53 | 0.0031576 | 0.00079137
54 | 0.017296 | 0.0043347
55 | 0.0034722 | 0.00087021
56 | 0.0024114 | 0.00060436
57 | 0.002463 | 0.00061728
58 | 0.0048625 | 0.0012187
59 | 0.0030434 | 0.00076275
60 | 0.0024863 | 0.00062314
61 | 0.0024126 | 0.00060467
62 | 0.0036574 | 0.00091664
63 | 0.0047949 | 0.0012017
64 | 0.0088384 | 0.0022151
65 | 0.003602 | 0.00090276
66 | 0.0029318 | 0.00073478
67 | 0.00099604 | 0.00024963
68 | 0.0021654 | 0.00054269
69 | 0.0018505 | 0.00046379
70 | 0.003431 | 0.00085989
71 | 0.011695 | 0.0029311
72 | 0.0019447 | 0.00048739
73 | 0.0033013 | 0.00082738
74 | 0.011698 | 0.0029317
75 | 0.001944 | 0.00048721
76 | 0.0016611 | 0.00041632
77 | 0.001919 | 0.00048094
78 | 0.0021181 | 0.00053086
79 | 0.0076712 | 0.0019226
80 | 0.0020313 | 0.00050908
81 | 0.0013078 | 0.00032777
82 | 0.0020313 | 0.00050908
83 | 0.0020646 | 0.00051745
84 | 0.0086499 | 0.0021679
85 | 0.0019682 | 0.00049327
86 | 0.0019682 | 0.00049327

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1