## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1063-9_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1063-9_0_5_node_86 | 0.4 | n |  | TRUE
2 | bus_LV_1063-9_0_5_node_83 | 0.4 | n |  | TRUE
3 | bus_LV_1063-9_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1063-9_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1063-9_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1063-9_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1063-9_0_5_node_92 | 0.4 | n |  | TRUE
8 | bus_LV_1063-9_0_5_node_91 | 0.4 | n |  | TRUE
9 | bus_LV_1063-9_0_5_node_68 | 0.4 | n |  | TRUE
10 | bus_LV_1063-9_0_5_node_66 | 0.4 | n |  | TRUE
11 | bus_LV_1063-9_0_5_node_122 | 0.4 | n |  | TRUE
12 | bus_LV_1063-9_0_5_node_90 | 0.4 | n |  | TRUE
13 | bus_LV_1063-9_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1063-9_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1063-9_0_5_node_84 | 0.4 | n |  | TRUE
16 | bus_LV_1063-9_0_5_node_82 | 0.4 | n |  | TRUE
17 | bus_LV_1063-9_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1063-9_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1063-9_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1063-9_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1063-9_0_5_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1063-9_0_5_node_88 | 0.4 | n |  | TRUE
23 | bus_LV_1063-9_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1063-9_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1063-9_0_5_node_144 | 0.4 | n |  | TRUE
26 | bus_LV_1063-9_0_5_node_77 | 0.4 | n |  | TRUE
27 | bus_LV_1063-9_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1063-9_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1063-9_0_5_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1063-9_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1063-9_0_5_node_142 | 0.4 | n |  | TRUE
32 | bus_LV_1063-9_0_5_node_136 | 0.4 | n |  | TRUE
33 | bus_LV_1063-9_0_5_node_147 | 0.4 | n |  | TRUE
34 | bus_LV_1063-9_0_5_node_138 | 0.4 | n |  | TRUE
35 | bus_LV_1063-9_0_5_node_134 | 0.4 | n |  | TRUE
36 | bus_LV_1063-9_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1063-9_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1063-9_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1063-9_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1063-9_0_5_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1063-9_0_5_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1063-9_0_5_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_1063-9_0_5_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_1063-9_0_5_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_1063-9_0_5_node_51 | 0.4 | n |  | TRUE
46 | bus_LV_1063-9_0_5_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_1063-9_0_5_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_1063-9_0_5_node_79 | 0.4 | n |  | TRUE
49 | bus_LV_1063-9_0_5_node_60 | 0.4 | n |  | TRUE
50 | bus_LV_1063-9_0_5_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1063-9_0_5_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_1063-9_0_5_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_1063-9_0_5_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_1063-9_0_5_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_1063-9_0_5_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_1063-9_0_5_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_1063-9_0_5_node_93 | 0.4 | n |  | TRUE
58 | bus_LV_1063-9_0_5_node_124 | 0.4 | n |  | TRUE
59 | bus_LV_1063-9_0_5_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_1063-9_0_5_node_108 | 0.4 | n |  | TRUE
61 | bus_LV_1063-9_0_5_node_123 | 0.4 | n |  | TRUE
62 | bus_LV_1063-9_0_5_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_1063-9_0_5_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_1063-9_0_5_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_1063-9_0_5_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_1063-9_0_5_node_35 | 0.4 | n |  | TRUE
67 | bus_LV_1063-9_0_5_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_1063-9_0_5_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_1063-9_0_5_node_133 | 0.4 | n |  | TRUE
70 | bus_LV_1063-9_0_5_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_1063-9_0_5_node_114 | 0.4 | n |  | TRUE
72 | bus_LV_1063-9_0_5_node_102 | 0.4 | n |  | TRUE
73 | bus_LV_1063-9_0_5_node_38 | 0.4 | n |  | TRUE
74 | bus_LV_1063-9_0_5_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_1063-9_0_5_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_1063-9_0_5_node_41 | 0.4 | n |  | TRUE
77 | bus_LV_1063-9_0_5_node_42 | 0.4 | n |  | TRUE
78 | bus_LV_1063-9_0_5_node_127 | 0.4 | n |  | TRUE
79 | bus_LV_1063-9_0_5_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_1063-9_0_5_node_69 | 0.4 | n |  | TRUE
81 | bus_LV_1063-9_0_5_node_126 | 0.4 | n |  | TRUE
82 | bus_LV_1063-9_0_5_node_106 | 0.4 | n |  | TRUE
83 | bus_LV_1063-9_0_5_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_1063-9_0_5_node_103 | 0.4 | n |  | TRUE
85 | bus_LV_1063-9_0_5_node_149 | 0.4 | n |  | TRUE
86 | bus_LV_1063-9_0_5_node_98 | 0.4 | n |  | TRUE
87 | bus_LV_1063-9_0_5_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_1063-9_0_5_node_45 | 0.4 | n |  | TRUE
89 | bus_LV_1063-9_0_5_node_132 | 0.4 | n |  | TRUE
90 | bus_LV_1063-9_0_5_node_150 | 0.4 | n |  | TRUE
91 | bus_LV_1063-9_0_5_node_146 | 0.4 | n |  | TRUE
92 | bus_LV_1063-9_0_5_node_129 | 0.4 | n |  | TRUE
93 | bus_LV_1063-9_0_5_node_56 | 0.4 | n |  | TRUE
94 | bus_LV_1063-9_0_5_node_53 | 0.4 | n |  | TRUE
95 | bus_LV_1063-9_0_5_node_54 | 0.4 | n |  | TRUE
96 | bus_LV_1063-9_0_5_node_55 | 0.4 | n |  | TRUE
97 | bus_LV_1063-9_0_5_node_57 | 0.4 | n |  | TRUE
98 | bus_LV_1063-9_0_5_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_1063-9_0_5_node_59 | 0.4 | n |  | TRUE
100 | bus_LV_1063-9_0_5_node_61 | 0.4 | n |  | TRUE
101 | bus_LV_1063-9_0_5_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_1063-9_0_5_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_1063-9_0_5_node_63 | 0.4 | n |  | TRUE
104 | bus_LV_1063-9_0_5_node_64 | 0.4 | n |  | TRUE
105 | bus_LV_1063-9_0_5_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_1063-9_0_5_node_111 | 0.4 | n |  | TRUE
107 | bus_LV_1063-9_0_5_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_1063-9_0_5_node_109 | 0.4 | n |  | TRUE
109 | bus_LV_1063-9_0_5_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_1063-9_0_5_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_1063-9_0_5_node_101 | 0.4 | n |  | TRUE
112 | bus_LV_1063-9_0_5_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_1063-9_0_5_node_99 | 0.4 | n |  | TRUE
114 | bus_LV_1063-9_0_5_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_1063-9_0_5_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_1063-9_0_5_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_1063-9_0_5_node_148 | 0.4 | n |  | TRUE
118 | bus_LV_1063-9_0_5_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_1063-9_0_5_node_74 | 0.4 | n |  | TRUE
120 | bus_LV_1063-9_0_5_node_75 | 0.4 | n |  | TRUE
121 | bus_LV_1063-9_0_5_node_76 | 0.4 | n |  | TRUE
122 | bus_LV_1063-9_0_5_node_87 | 0.4 | n |  | TRUE
123 | bus_LV_1063-9_0_5_node_85 | 0.4 | n |  | TRUE
124 | bus_LV_1063-9_0_5_node_125 | 0.4 | n |  | TRUE
125 | bus_LV_1063-9_0_5_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_1063-9_0_5_node_95 | 0.4 | n |  | TRUE
127 | bus_LV_1063-9_0_5_node_97 | 0.4 | n |  | TRUE
128 | bus_LV_1063-9_0_5_node_135 | 0.4 | n |  | TRUE
129 | bus_LV_1063-9_0_5_node_140 | 0.4 | n |  | TRUE
130 | bus_LV_1063-9_0_5_node_137 | 0.4 | n |  | TRUE
131 | bus_LV_1063-9_0_5_node_139 | 0.4 | n |  | TRUE
132 | bus_LV_1063-9_0_5_node_105 | 0.4 | n |  | TRUE
133 | bus_LV_1063-9_0_5_node_145 | 0.4 | n |  | TRUE
134 | bus_LV_1063-9_0_5_node_115 | 0.4 | n |  | TRUE
135 | bus_LV_1063-9_0_5_node_116 | 0.4 | n |  | TRUE
136 | bus_LV_1063-9_0_5_node_117 | 0.4 | n |  | TRUE
137 | bus_LV_1063-9_0_5_node_119 | 0.4 | n |  | TRUE
138 | bus_LV_1063-9_0_5_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_1063-9_0_5_node_121 | 0.4 | n |  | TRUE
140 | bus_LV_1063-9_0_5_node_128 | 0.4 | n |  | TRUE
141 | bus_LV_1063-9_0_5_node_130 | 0.4 | n |  | TRUE
142 | bus_LV_1063-9_0_5_node_131 | 0.4 | n |  | TRUE
143 | bus_MV_211_2_node_147 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1063-9_0_5_load_0 | 0 | 0.0011061 | 0.00027722 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1063-9_0_5_load_86 | 1 | 0.0030797 | 0.00077183 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1063-9_0_5_load_2 | 3 | 0.0059035 | 0.0014796 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1063-9_0_5_load_5 | 6 | 0.01128 | 0.0028271 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1063-9_0_5_load_92 | 7 | 0.016022 | 0.0040155 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1063-9_0_5_load_91 | 8 | 0.013536 | 0.0033925 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1063-9_0_5_load_68 | 9 | 0.0030841 | 0.00077295 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1063-9_0_5_load_66 | 10 | 0.0013172 | 0.00033012 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1063-9_0_5_load_122 | 11 | 0.0066853 | 0.0016755 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1063-9_0_5_load_8 | 13 | 0.0012929 | 0.00032404 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1063-9_0_5_load_82 | 16 | 0.0027295 | 0.00068408 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1063-9_0_5_load_11 | 17 | 0.005179 | 0.001298 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1063-9_0_5_load_13 | 19 | 0.0047493 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1063-9_0_5_load_16 | 23 | 0.0033364 | 0.00083619 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1063-9_0_5_load_144 | 25 | 0.0034944 | 0.00087577 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1063-9_0_5_load_15 | 27 | 0.0040074 | 0.0010044 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1063-9_0_5_load_18 | 29 | 0.0094877 | 0.0023778 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1063-9_0_5_load_142 | 31 | 0.015513 | 0.003888 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1063-9_0_5_load_147 | 33 | 0.0050221 | 0.0012587 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1063-9_0_5_load_138 | 34 | 0.0016949 | 0.00042478 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1063-9_0_5_load_134 | 35 | 0.0078906 | 0.0019776 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1063-9_0_5_load_22 | 36 | 0.0043817 | 0.0010982 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1063-9_0_5_load_23 | 37 | 0.0035323 | 0.00088528 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1063-9_0_5_load_24 | 38 | 0.0033451 | 0.00083836 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1063-9_0_5_load_25 | 39 | 0.0034962 | 0.00087622 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1063-9_0_5_load_48 | 40 | 0.0022945 | 0.00057507 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1063-9_0_5_load_26 | 41 | 0.0045203 | 0.0011329 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1063-9_0_5_load_47 | 42 | 0.0095743 | 0.0023996 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1063-9_0_5_load_50 | 44 | 0.0039377 | 0.00098688 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1063-9_0_5_load_51 | 45 | 0.00099727 | 0.00024994 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1063-9_0_5_load_52 | 46 | 0.0025987 | 0.0006513 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1063-9_0_5_load_67 | 47 | 0.0027581 | 0.00069125 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1063-9_0_5_load_58 | 51 | 0.0045203 | 0.0011329 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1063-9_0_5_load_27 | 52 | 0.0096621 | 0.0024215 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1063-9_0_5_load_28 | 53 | 0.0071263 | 0.001786 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1063-9_0_5_load_31 | 56 | 0.0071263 | 0.001786 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1063-9_0_5_load_124 | 58 | 0.0035407 | 0.00088739 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1063-9_0_5_load_37 | 59 | 0.018359 | 0.0046012 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1063-9_0_5_load_108 | 60 | 0.014162 | 0.0035493 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1063-9_0_5_load_123 | 61 | 0.0036453 | 0.00091359 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1063-9_0_5_load_33 | 63 | 0.0081619 | 0.0020456 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1063-9_0_5_load_46 | 67 | 0.0035354 | 0.00088604 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1063-9_0_5_load_43 | 68 | 0.0023851 | 0.00059777 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1063-9_0_5_load_133 | 69 | 0.004075 | 0.0010213 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1063-9_0_5_load_44 | 70 | 0.0022784 | 0.00057102 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1063-9_0_5_load_114 | 71 | 0.0020526 | 0.00051443 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1063-9_0_5_load_38 | 73 | 0.0024904 | 0.00062414 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1063-9_0_5_load_39 | 74 | 0.0055248 | 0.0013846 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1063-9_0_5_load_40 | 75 | 0.0015724 | 0.00039407 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1063-9_0_5_load_41 | 76 | 0.0045538 | 0.0011413 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1063-9_0_5_load_127 | 78 | 0.0032093 | 0.00080433 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1063-9_0_5_load_69 | 80 | 0.0026735 | 0.00067004 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1063-9_0_5_load_126 | 81 | 0.0023731 | 0.00059476 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1063-9_0_5_load_106 | 82 | 0.0038599 | 0.00096738 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1063-9_0_5_load_103 | 84 | 0.0038586 | 0.00096705 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1063-9_0_5_load_149 | 85 | 0.0075661 | 0.0018963 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1063-9_0_5_load_70 | 87 | 0.0031833 | 0.00079781 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1063-9_0_5_load_150 | 90 | 0.0069576 | 0.0017437 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1063-9_0_5_load_146 | 91 | 0.0053822 | 0.0013489 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1063-9_0_5_load_53 | 94 | 0.0010757 | 0.00026959 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1063-9_0_5_load_54 | 95 | 0.0021314 | 0.00053418 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1063-9_0_5_load_55 | 96 | 0.0010876 | 0.00027259 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1063-9_0_5_load_57 | 97 | 0.0024658 | 0.000618 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1063-9_0_5_load_81 | 98 | 0.0011793 | 0.00029557 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1063-9_0_5_load_59 | 99 | 0.002572 | 0.0006446 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1063-9_0_5_load_61 | 100 | 0.017548 | 0.004398 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1063-9_0_5_load_71 | 101 | 0.0026394 | 0.00066149 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1063-9_0_5_load_62 | 102 | 0.0044836 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1063-9_0_5_load_64 | 104 | 0.0038328 | 0.00096058 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1063-9_0_5_load_65 | 105 | 0.0046938 | 0.0011764 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1063-9_0_5_load_104 | 109 | 0.002848 | 0.00071378 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1063-9_0_5_load_94 | 112 | 0.0050474 | 0.001265 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1063-9_0_5_load_113 | 114 | 0.0060002 | 0.0015038 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1063-9_0_5_load_110 | 116 | 0.010221 | 0.0025617 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1063-9_0_5_load_148 | 117 | 0.0050712 | 0.001271 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1063-9_0_5_load_107 | 118 | 0.006146 | 0.0015403 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1063-9_0_5_load_74 | 119 | 0.0027246 | 0.00068286 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1063-9_0_5_load_75 | 120 | 0.0053206 | 0.0013335 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1063-9_0_5_load_76 | 121 | 0.0097273 | 0.0024379 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1063-9_0_5_load_87 | 122 | 0.011661 | 0.0029226 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1063-9_0_5_load_85 | 123 | 0.0018631 | 0.00046693 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1063-9_0_5_load_125 | 124 | 0.0028382 | 0.00071133 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1063-9_0_5_load_118 | 125 | 0.0025212 | 0.00063186 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1063-9_0_5_load_95 | 126 | 0.0053764 | 0.0013474 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1063-9_0_5_load_140 | 129 | 0.0016088 | 0.0004032 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1063-9_0_5_load_137 | 130 | 0.0033029 | 0.00082778 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1063-9_0_5_load_139 | 131 | 0.0016577 | 0.00041545 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1063-9_0_5_load_105 | 132 | 0.0010519 | 0.00026364 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1063-9_0_5_load_145 | 133 | 0.0034131 | 0.00085541 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1063-9_0_5_load_115 | 134 | 0.0017211 | 0.00043135 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1063-9_0_5_load_119 | 137 | 0.0017125 | 0.00042918 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1063-9_0_5_load_120 | 138 | 0.002864 | 0.00071778 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1063-9_0_5_load_121 | 139 | 0.0037858 | 0.00094882 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1063-9_0_5_load_128 | 140 | 0.003195 | 0.00080073 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1063-9_0_5_load_130 | 141 | 0.0035791 | 0.000897 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1063-9_0_5_load_131 | 142 | 0.0068506 | 0.0017169 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1063-9_0_5_line_0 |  | 0 | 1 | 0.15155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1063-9_0_5_line_1 |  | 1 | 2 | 0.0067236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1063-9_0_5_line_2 |  | 2 | 98 | 0.057517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1063-9_0_5_line_3 |  | 3 | 4 | 0.048903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1063-9_0_5_line_4 |  | 4 | 5 | 0.030394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1063-9_0_5_line_5 |  | 4 | 6 | 0.077217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1063-9_0_5_line_6 |  | 5 | 9 | 0.0054124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1063-9_0_5_line_7 |  | 7 | 8 | 0.032716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1063-9_0_5_line_8 |  | 8 | 57 | 0.013406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1063-9_0_5_line_9 |  | 9 | 10 | 0.018835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1063-9_0_5_line_10 |  | 10 | 47 | 0.0018778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1063-9_0_5_line_11 |  | 11 | 12 | 0.0091401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1063-9_0_5_line_12 |  | 12 | 20 | 0.018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1063-9_0_5_line_13 |  | 13 | 14 | 0.0099175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1063-9_0_5_line_14 |  | 14 | 15 | 0.22905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1063-9_0_5_line_15 |  | 15 | 16 | 0.07583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1063-9_0_5_line_16 |  | 16 | 98 | 0.10201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1063-9_0_5_line_17 |  | 17 | 18 | 0.034573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1063-9_0_5_line_18 |  | 18 | 19 | 0.020969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1063-9_0_5_line_19 |  | 18 | 20 | 0.012014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1063-9_0_5_line_20 |  | 19 | 21 | 0.051306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1063-9_0_5_line_21 |  | 20 | 22 | 0.010557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1063-9_0_5_line_22 |  | 20 | 23 | 0.023882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1063-9_0_5_line_23 |  | 21 | 24 | 0.014044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1063-9_0_5_line_24 |  | 22 | 25 | 0.037043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1063-9_0_5_line_25 |  | 22 | 26 | 0.004439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1063-9_0_5_line_26 |  | 23 | 27 | 0.0017903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1063-9_0_5_line_27 |  | 24 | 30 | 0.018999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1063-9_0_5_line_28 |  | 24 | 31 | 0.026732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1063-9_0_5_line_29 |  | 26 | 120 | 0.016899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1063-9_0_5_line_30 |  | 27 | 28 | 0.013426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1063-9_0_5_line_31 |  | 28 | 29 | 0.010006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1063-9_0_5_line_32 |  | 30 | 32 | 0.01217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1063-9_0_5_line_33 |  | 30 | 33 | 0.023549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1063-9_0_5_line_34 |  | 32 | 34 | 0.023032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1063-9_0_5_line_35 |  | 32 | 35 | 0.047189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1063-9_0_5_line_36 |  | 35 | 128 | 0.011062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1063-9_0_5_line_37 |  | 36 | 37 | 0.0039154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1063-9_0_5_line_38 |  | 36 | 38 | 0.0033341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1063-9_0_5_line_39 |  | 37 | 39 | 0.0020805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1063-9_0_5_line_40 |  | 38 | 40 | 0.038804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1063-9_0_5_line_41 |  | 39 | 41 | 0.033932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1063-9_0_5_line_42 |  | 40 | 44 | 0.026112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1063-9_0_5_line_43 |  | 40 | 42 | 0.0093403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1063-9_0_5_line_44 |  | 41 | 49 | 0.033318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1063-9_0_5_line_45 |  | 42 | 43 | 0.035811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1063-9_0_5_line_46 |  | 43 | 45 | 0.0064196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1063-9_0_5_line_47 |  | 43 | 46 | 0.018848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1063-9_0_5_line_48 |  | 44 | 47 | 0.020412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1063-9_0_5_line_49 |  | 45 | 48 | 0.030423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1063-9_0_5_line_50 |  | 48 | 93 | 0.030384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1063-9_0_5_line_51 |  | 49 | 50 | 0.010163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_1063-9_0_5_line_52 |  | 49 | 51 | 0.0078559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1063-9_0_5_line_53 |  | 50 | 60 | 0.021886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_1063-9_0_5_line_54 |  | 50 | 54 | 0.033412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1063-9_0_5_line_55 |  | 51 | 99 | 0.0091199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1063-9_0_5_line_56 |  | 52 | 53 | 0.01485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1063-9_0_5_line_57 |  | 52 | 54 | 0.0046605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1063-9_0_5_line_58 |  | 53 | 55 | 0.015726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1063-9_0_5_line_59 |  | 54 | 56 | 0.013453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1063-9_0_5_line_60 |  | 55 | 57 | 0.002209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1063-9_0_5_line_61 |  | 55 | 58 | 0.002377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1063-9_0_5_line_62 |  | 56 | 59 | 0.0018258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1063-9_0_5_line_63 |  | 58 | 61 | 0.0083509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1063-9_0_5_line_64 |  | 60 | 62 | 0.030689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_1063-9_0_5_line_65 |  | 61 | 122 | 0.02771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1063-9_0_5_line_66 |  | 62 | 108 | 0.004437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1063-9_0_5_line_67 |  | 62 | 121 | 0.033558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1063-9_0_5_line_68 |  | 63 | 64 | 0.02116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1063-9_0_5_line_69 |  | 64 | 65 | 0.017394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1063-9_0_5_line_70 |  | 65 | 66 | 0.004994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1063-9_0_5_line_71 |  | 66 | 67 | 0.0064285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1063-9_0_5_line_72 |  | 66 | 68 | 0.048581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1063-9_0_5_line_73 |  | 67 | 69 | 0.019234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1063-9_0_5_line_74 |  | 68 | 70 | 0.063627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1063-9_0_5_line_75 |  | 70 | 88 | 0.029476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1063-9_0_5_line_76 |  | 71 | 72 | 0.064748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1063-9_0_5_line_77 |  | 72 | 88 | 0.00337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1063-9_0_5_line_78 |  | 73 | 74 | 0.032947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1063-9_0_5_line_79 |  | 73 | 75 | 0.025649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1063-9_0_5_line_80 |  | 74 | 76 | 0.02049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1063-9_0_5_line_81 |  | 75 | 77 | 0.014326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1063-9_0_5_line_82 |  | 76 | 78 | 0.00015742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1063-9_0_5_line_83 |  | 77 | 79 | 0.015105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1063-9_0_5_line_84 |  | 77 | 80 | 0.005026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1063-9_0_5_line_85 |  | 78 | 81 | 0.044662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1063-9_0_5_line_86 |  | 79 | 82 | 0.015929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1063-9_0_5_line_87 |  | 79 | 83 | 0.026899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1063-9_0_5_line_88 |  | 79 | 84 | 0.052415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1063-9_0_5_line_89 |  | 80 | 87 | 0.025392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1063-9_0_5_line_90 |  | 81 | 137 | 0.030084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1063-9_0_5_line_91 |  | 83 | 85 | 0.011051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1063-9_0_5_line_92 |  | 83 | 86 | 0.040115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1063-9_0_5_line_93 |  | 84 | 109 | 0.00049029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1063-9_0_5_line_94 |  | 86 | 90 | 0.038702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1063-9_0_5_line_95 |  | 86 | 88 | 0.037563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1063-9_0_5_line_96 |  | 87 | 101 | 0.029882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1063-9_0_5_line_97 |  | 88 | 89 | 0.006461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1063-9_0_5_line_98 |  | 89 | 91 | 0.01273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1063-9_0_5_line_99 |  | 89 | 92 | 0.02192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1063-9_0_5_line_100 |  | 92 | 142 | 0.017897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1063-9_0_5_line_101 |  | 92 | 140 | 0.0068788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1063-9_0_5_line_102 |  | 93 | 95 | 0.018441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1063-9_0_5_line_103 |  | 94 | 95 | 0.0012372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1063-9_0_5_line_104 |  | 94 | 96 | 0.022445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1063-9_0_5_line_105 |  | 96 | 97 | 0.0031517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1063-9_0_5_line_106 |  | 97 | 98 | 0.07417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1063-9_0_5_line_107 |  | 99 | 100 | 0.0019695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1063-9_0_5_line_108 |  | 100 | 101 | 0.006837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1063-9_0_5_line_109 |  | 102 | 103 | 0.015958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1063-9_0_5_line_110 |  | 103 | 104 | 0.007132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1063-9_0_5_line_111 |  | 103 | 105 | 0.014551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1063-9_0_5_line_112 |  | 105 | 106 | 0.034746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1063-9_0_5_line_113 |  | 106 | 107 | 0.023243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1063-9_0_5_line_114 |  | 106 | 108 | 0.026012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1063-9_0_5_line_115 |  | 107 | 133 | 0.036332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1063-9_0_5_line_116 |  | 108 | 116 | 0.01563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1063-9_0_5_line_117 |  | 109 | 132 | 0.00010066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1063-9_0_5_line_118 |  | 110 | 111 | 0.032495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1063-9_0_5_line_119 |  | 110 | 112 | 0.017834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1063-9_0_5_line_120 |  | 111 | 118 | 0.014241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1063-9_0_5_line_121 |  | 111 | 115 | 0.036446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1063-9_0_5_line_122 |  | 113 | 114 | 0.007963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1063-9_0_5_line_123 |  | 113 | 115 | 0.012839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1063-9_0_5_line_124 |  | 113 | 116 | 0.013542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1063-9_0_5_line_125 |  | 115 | 117 | 0.016425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1063-9_0_5_line_126 |  | 119 | 120 | 0.033546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1063-9_0_5_line_127 |  | 119 | 121 | 0.034139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1063-9_0_5_line_128 |  | 123 | 124 | 0.025568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1063-9_0_5_line_129 |  | 124 | 125 | 0.034147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1063-9_0_5_line_130 |  | 125 | 135 | 0.014399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1063-9_0_5_line_131 |  | 126 | 127 | 0.0458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1063-9_0_5_line_132 |  | 127 | 128 | 0.047462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1063-9_0_5_line_133 |  | 127 | 129 | 0.02573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1063-9_0_5_line_134 |  | 128 | 130 | 0.02943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1063-9_0_5_line_135 |  | 129 | 131 | 0.017797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1063-9_0_5_line_136 |  | 134 | 135 | 0.02288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1063-9_0_5_line_137 |  | 134 | 136 | 0.029315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1063-9_0_5_line_138 |  | 135 | 137 | 0.065357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1063-9_0_5_line_139 |  | 136 | 138 | 0.04004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1063-9_0_5_line_140 |  | 136 | 139 | 0.011807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1063-9_0_5_line_141 |  | 140 | 141 | 0.0074615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1063-9_0_5_trafo_108 | 0.63 MVA 20/0.4 kV | 143 | 60 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2670423.8035 | 1211680.0448 | 2670343.9957 | 1211808.8737
1 | 2670422.1327 | 1211673.5321 | 2670423.8035 | 1211680.0448
2 | 2670422.1327 | 1211673.5321 | 2670426.3809 | 1211676.7064 | 2670466.3856 | 1211699.4485 | 2670471.773 | 1211702.5101
3 | 2670595.6928 | 1211515.284 | 2670606.4519 | 1211530.7766 | 2670629.2828 | 1211550.3016
4 | 2670595.6928 | 1211515.284 | 2670588.872 | 1211520.7957 | 2670579.978 | 1211524.9264 | 2670568.585 | 1211528.316
5 | 2670595.6928 | 1211515.284 | 2670620.8491 | 1211488.665 | 2670627.9399 | 1211482.1671 | 2670636.1635 | 1211476.9167 | 2670655.6397 | 1211468.4989
6 | 2670568.585 | 1211528.316 | 2670563.2887 | 1211529.431
7 | 2670516.3843 | 1211454.2009 | 2670519.7902 | 1211453.2922 | 2670539.6349 | 1211449.1352 | 2670546.9505 | 1211446.7647 | 2670548.0479 | 1211446.2193
8 | 2670503.431 | 1211457.6571 | 2670516.3843 | 1211454.2009
9 | 2670544.858 | 1211533.3122 | 2670557.5847 | 1211530.6318 | 2670563.2887 | 1211529.431
10 | 2670544.858 | 1211533.3122 | 2670543.0205 | 1211533.6992
11 | 2670565.0809 | 1211375.5568 | 2670573.9936 | 1211373.5307
12 | 2670565.0809 | 1211375.5568 | 2670559.4212 | 1211376.7017 | 2670556.8063 | 1211376.7708 | 2670555.3721 | 1211376.5982 | 2670554.2065 | 1211375.5615 | 2670553.5059 | 1211373.7632 | 2670552.5533 | 1211373.9854 | 2670548.0268 | 1211375.0548
13 | 2670772.429 | 1211971.1965 | 2670780.3223 | 1211977.2009
14 | 2670610.3646 | 1211809.3416 | 2670772.429 | 1211971.1965
15 | 2670610.3646 | 1211809.3416 | 2670607.7262 | 1211808.8434 | 2670605.7806 | 1211806.9526 | 2670593.7277 | 1211787.8202 | 2670563.4585 | 1211758.6105 | 2670558.6382 | 1211755.4672
16 | 2670471.773 | 1211702.5101 | 2670482.2894 | 1211708.4865 | 2670523.88 | 1211737.8074 | 2670534.9652 | 1211743.6976 | 2670554.9151 | 1211753.0393 | 2670558.6382 | 1211755.4672
17 | 2670545.1022 | 1211363.4018 | 2670577.2042 | 1211350.565
18 | 2670545.1022 | 1211363.4018 | 2670542.2149 | 1211350.5152 | 2670539.4759 | 1211343.2513
19 | 2670548.0268 | 1211375.0548 | 2670545.1022 | 1211363.4018
20 | 2670513.7988 | 1211299.9811 | 2670513.5767 | 1211303.3361 | 2670515.9722 | 1211308.3342 | 2670529.3156 | 1211324.4687 | 2670536.77 | 1211336.0751 | 2670539.4759 | 1211343.2513
21 | 2670548.0268 | 1211375.0548 | 2670549.9139 | 1211382.5485 | 2670550.6034 | 1211385.2917
22 | 2670548.0268 | 1211375.0548 | 2670543.9881 | 1211375.9965 | 2670543.1194 | 1211376.1975 | 2670543.4541 | 1211373.5998 | 2670542.9886 | 1211369.9143 | 2670539.9695 | 1211357.775
23 | 2670507.3409 | 1211291.4995 | 2670507.1837 | 1211292.5872 | 2670506.4455 | 1211297.8151 | 2670513.7988 | 1211299.9811
24 | 2670550.6034 | 1211385.2917 | 2670514.5729 | 1211393.8921
25 | 2670551.1135 | 1211389.7005 | 2670550.6034 | 1211385.2917
26 | 2670539.5374 | 1211356.0377 | 2670539.9695 | 1211357.775
27 | 2670494.407 | 1211294.0705 | 2670495.813 | 1211294.6986 | 2670498.8498 | 1211295.5906 | 2670506.4455 | 1211297.8151 | 2670507.1837 | 1211292.5872 | 2670507.3409 | 1211291.4995
28 | 2670507.3409 | 1211291.4995 | 2670508.4524 | 1211283.6188 | 2670527.0223 | 1211286.3744
29 | 2670551.1135 | 1211389.7005 | 2670547.8204 | 1211389.9283 | 2670534.6029 | 1211393.1229
30 | 2670535.3088 | 1211343.318 | 2670538.3822 | 1211351.3927 | 2670539.5374 | 1211356.0377
31 | 2670535.3088 | 1211343.318 | 2670530.8048 | 1211341.8416 | 2670526.4247 | 1211338.8768
32 | 2670494.407 | 1211294.0705 | 2670485.5779 | 1211290.1082 | 2670483.4199 | 1211288.8041
33 | 2670477.9947 | 1211310.6092 | 2670484.4592 | 1211306.3162 | 2670487.6572 | 1211303.2076 | 2670494.407 | 1211294.0705
34 | 2670483.4199 | 1211288.8041 | 2670480.2173 | 1211277.5148 | 2670478.1067 | 1211266.4162
35 | 2670483.4199 | 1211288.8041 | 2670475.9651 | 1211284.3021 | 2670470.6071 | 1211280.4809 | 2670465.0532 | 1211284.8847 | 2670457.2723 | 1211288.0393 | 2670449.1906 | 1211290.2786 | 2670441.2292 | 1211291.3189
36 | 2670430.1798 | 1211291.3548 | 2670430.7342 | 1211291.3836 | 2670439.9052 | 1211291.4919 | 2670441.2292 | 1211291.3189
37 | 2670471.2635 | 1211535.0213 | 2670470.8027 | 1211531.1331
38 | 2670471.6559 | 1211538.3322 | 2670471.2635 | 1211535.0213
39 | 2670470.8027 | 1211531.1331 | 2670470.5578 | 1211529.0671
40 | 2670471.6559 | 1211538.3322 | 2670505.9171 | 1211556.5499
41 | 2670470.5578 | 1211529.0671 | 2670467.1851 | 1211500.6114 | 2670464.303 | 1211496.1903
42 | 2670523.1343 | 1211538.1756 | 2670517.1895 | 1211540.8384 | 2670510.6991 | 1211547.3435 | 2670507.483 | 1211552.6311 | 2670505.9171 | 1211556.5499
43 | 2670504.0143 | 1211565.6062 | 2670503.9095 | 1211565.0188 | 2670504.9538 | 1211558.9607 | 2670505.9171 | 1211556.5499
44 | 2670435.9121 | 1211481.5858 | 2670448.8183 | 1211483.8952 | 2670461.0351 | 1211491.1773 | 2670464.303 | 1211496.1903
45 | 2670525.9083 | 1211591.3619 | 2670517.9304 | 1211587.4319 | 2670512.8518 | 1211583.7918 | 2670507.6026 | 1211577.2256 | 2670505.1424 | 1211571.9266 | 2670504.0143 | 1211565.6062
46 | 2670525.9083 | 1211591.3619 | 2670527.9259 | 1211597.4563
47 | 2670525.9083 | 1211591.3619 | 2670539.0284 | 1211590.9835 | 2670544.6818 | 1211590.1002
48 | 2670523.1343 | 1211538.1756 | 2670524.3477 | 1211537.6321 | 2670543.0205 | 1211533.6992
49 | 2670547.7369 | 1211620.516 | 2670540.8359 | 1211611.6288 | 2670527.9259 | 1211597.4563
50 | 2670556.1906 | 1211649.1005 | 2670556.7871 | 1211644.2823 | 2670552.202 | 1211629.1186 | 2670547.7369 | 1211620.516
51 | 2670436.0777 | 1211471.4259 | 2670435.9121 | 1211481.5858
52 | 2670435.9121 | 1211481.5858 | 2670433.0195 | 1211486.5103 | 2670431.2282 | 1211487.6897
53 | 2670436.0777 | 1211471.4259 | 2670436.469 | 1211449.5438
54 | 2670468.7472 | 1211464.2404 | 2670444.593 | 1211470.4035 | 2670436.0777 | 1211471.4259
55 | 2670431.2282 | 1211487.6897 | 2670428.9221 | 1211489.2081 | 2670422.568 | 1211489.4525
56 | 2670473.2625 | 1211463.0865 | 2670487.6498 | 1211459.4098
57 | 2670468.7472 | 1211464.2404 | 2670473.2625 | 1211463.0865
58 | 2670502.8864 | 1211455.516 | 2670487.6498 | 1211459.4098
59 | 2670468.7472 | 1211464.2404 | 2670465.9431 | 1211451.0825
60 | 2670503.431 | 1211457.6571 | 2670502.8864 | 1211455.516
61 | 2670502.8864 | 1211455.516 | 2670505.1895 | 1211454.9276
62 | 2670465.5626 | 1211449.2968 | 2670465.9431 | 1211451.0825
63 | 2670505.1895 | 1211454.9276 | 2670513.2804 | 1211452.8603
64 | 2670437.0177 | 1211418.8597 | 2670436.469 | 1211449.5438
65 | 2670540.1278 | 1211446.0007 | 2670513.2804 | 1211452.8603
66 | 2670437.0177 | 1211418.8597 | 2670437.0929 | 1211414.4244
67 | 2670437.0177 | 1211418.8597 | 2670469.6298 | 1211410.947
68 | 2670119.2221 | 1211460.3649 | 2670122.8035 | 1211459.5287 | 2670128.7623 | 1211458.1423 | 2670138.7784 | 1211454.858 | 2670139.5304 | 1211454.5217
69 | 2670119.2221 | 1211460.3649 | 2670119.6655 | 1211462.0823 | 2670120.6542 | 1211465.8852 | 2670131.8785 | 1211462.6151
70 | 2670133.9909 | 1211467.1427 | 2670131.8785 | 1211462.6151
71 | 2670133.9909 | 1211467.1427 | 2670136.7113 | 1211472.9672
72 | 2670133.9909 | 1211467.1427 | 2670146.9954 | 1211461.7589 | 2670172.6175 | 1211448.3518 | 2670177.7539 | 1211446.1495
73 | 2670136.7113 | 1211472.9672 | 2670151.5497 | 1211485.2045
74 | 2670177.7539 | 1211446.1495 | 2670182.2332 | 1211444.2289 | 2670192.8525 | 1211441.3632 | 2670212.5089 | 1211439.6267 | 2670225.958 | 1211441.0192 | 2670240.2623 | 1211443.3946
75 | 2670269.3397 | 1211448.2233 | 2670240.2623 | 1211443.3946
76 | 2670269.668 | 1211444.8695 | 2670222.5803 | 1211436.1764 | 2670209.9686 | 1211435.2941 | 2670205.7525 | 1211435.5116
77 | 2670269.3397 | 1211448.2233 | 2670269.668 | 1211444.8695
78 | 2670385.5139 | 1211516.0666 | 2670411.8885 | 1211535.8121
79 | 2670385.5139 | 1211516.0666 | 2670364.9813 | 1211500.6947
80 | 2670411.8885 | 1211535.8121 | 2670425.1541 | 1211545.7434 | 2670426.9466 | 1211549.2277
81 | 2670353.5134 | 1211492.1092 | 2670364.9813 | 1211500.6947
82 | 2670426.9466 | 1211549.2277 | 2670427.0186 | 1211549.3677 | 2670427.0186 | 1211549.3677
83 | 2670341.6707 | 1211485.3209 | 2670342.5743 | 1211484.0863 | 2670346.9705 | 1211487.6181 | 2670353.5134 | 1211492.1092
84 | 2670353.5134 | 1211492.1092 | 2670358.5357 | 1211491.916
85 | 2670386.964 | 1211546.8905 | 2670420.3199 | 1211555.5035 | 2670423.6568 | 1211554.7758 | 2670426.4028 | 1211552.6069 | 2670427.0186 | 1211549.3677
86 | 2670341.6707 | 1211485.3209 | 2670339.7394 | 1211487.9887 | 2670336.6995 | 1211488.6644 | 2670327.2044 | 1211489.377
87 | 2670327.8203 | 1211464.4779 | 2670328.8806 | 1211469.2934 | 2670330.9315 | 1211472.5863 | 2670333.6091 | 1211476.865 | 2670342.5743 | 1211484.0863 | 2670341.6707 | 1211485.3209
88 | 2670341.6707 | 1211485.3209 | 2670344.1016 | 1211487.3175 | 2670340.8707 | 1211491.9378 | 2670340.1787 | 1211511.3084 | 2670315.9568 | 1211510.1762
89 | 2670358.5357 | 1211491.916 | 2670383.9085 | 1211490.9398
90 | 2670357.8355 | 1211539.369 | 2670386.964 | 1211546.8905
91 | 2670327.8203 | 1211464.4779 | 2670338.8908 | 1211463.9414
92 | 2670306.831 | 1211449.7214 | 2670311.5969 | 1211448.966 | 2670321.9829 | 1211446.5535 | 2670326.4645 | 1211444.7719 | 2670326.8932 | 1211450.3026 | 2670326.9799 | 1211456.4853 | 2670327.0776 | 1211461.0893 | 2670327.8203 | 1211464.4779
93 | 2670315.467 | 1211510.1533 | 2670315.9568 | 1211510.1762
94 | 2670322.845 | 1211472.0351 | 2670323.1291 | 1211465.3454 | 2670323.2251 | 1211463.0006 | 2670323.318 | 1211460.9227 | 2670323.4133 | 1211458.6446 | 2670323.1669 | 1211453.116 | 2670307.919 | 1211454.1147 | 2670306.831 | 1211449.7214
95 | 2670269.3397 | 1211448.2233 | 2670276.3937 | 1211449.3404 | 2670293.1877 | 1211450.6168 | 2670303.8848 | 1211450.1758 | 2670306.831 | 1211449.7214
96 | 2670383.9085 | 1211490.9398 | 2670413.768 | 1211489.7911
97 | 2670269.3397 | 1211448.2233 | 2670268.7168 | 1211454.6533
98 | 2670268.7168 | 1211454.6533 | 2670270.9675 | 1211455.825 | 2670273.1927 | 1211458.5195 | 2670276.8729 | 1211464.133
99 | 2670268.7168 | 1211454.6533 | 2670268.0939 | 1211476.5596
100 | 2670250.2259 | 1211474.8593 | 2670268.0939 | 1211476.5596
101 | 2670268.0939 | 1211476.5596 | 2670272.4859 | 1211481.8539
102 | 2670556.1906 | 1211649.1005 | 2670549.7 | 1211649.2016 | 2670538.0781 | 1211646.423
103 | 2670536.8748 | 1211646.1353 | 2670538.0781 | 1211646.423
104 | 2670536.8748 | 1211646.1353 | 2670515.0451 | 1211640.9163
105 | 2670511.9798 | 1211640.1834 | 2670515.0451 | 1211640.9163
106 | 2670471.773 | 1211702.5101 | 2670511.9798 | 1211640.1834
107 | 2670420.5999 | 1211489.5282 | 2670422.568 | 1211489.4525
108 | 2670420.5999 | 1211489.5282 | 2670413.768 | 1211489.7911
109 | 2670422.0082 | 1211375.8556 | 2670418.458 | 1211376.6142 | 2670414.5205 | 1211371.5646 | 2670410.0988 | 1211367.6211
110 | 2670422.0082 | 1211375.8556 | 2670421.0527 | 1211374.399 | 2670420.6526 | 1211369.0243
111 | 2670422.0082 | 1211375.8556 | 2670422.71 | 1211376.9201 | 2670431.6265 | 1211386.7568
112 | 2670457.3439 | 1211404.8242 | 2670449.6549 | 1211406.6457 | 2670431.6265 | 1211386.7568
113 | 2670457.3439 | 1211404.8242 | 2670458.3392 | 1211408.705 | 2670464.213 | 1211406.7954 | 2670468.0806 | 1211405.5403 | 2670476.7492 | 1211403.1412
114 | 2670457.3439 | 1211404.8242 | 2670458.3392 | 1211408.705 | 2670456.0812 | 1211409.4344 | 2670437.0929 | 1211414.4244
115 | 2670472.7232 | 1211368.9278 | 2670469.3995 | 1211376.2487 | 2670468.8076 | 1211378.7433 | 2670469.282 | 1211382.3289 | 2670471.6573 | 1211389.6726 | 2670476.7492 | 1211403.1412
116 | 2670437.0929 | 1211414.4244 | 2670423.3088 | 1211417.5859 | 2670421.8323 | 1211417.7693
117 | 2670315.3665 | 1211510.1486 | 2670315.467 | 1211510.1533
118 | 2670346.5713 | 1211425.4746 | 2670346.5279 | 1211426.5748 | 2670346.1895 | 1211428.85 | 2670345.3153 | 1211434.6767 | 2670356.0225 | 1211432.0902 | 2670364.0929 | 1211430.1397 | 2670364.8916 | 1211433.9403
119 | 2670346.5713 | 1211425.4746 | 2670347.1412 | 1211411.9506 | 2670348.2843 | 1211407.8071
120 | 2670364.8916 | 1211433.9403 | 2670365.8194 | 1211438.3874 | 2670375.4499 | 1211437.2437
121 | 2670364.8916 | 1211433.9403 | 2670397.3186 | 1211426.0623 | 2670400.4195 | 1211425.3763
122 | 2670408.4565 | 1211419.8232 | 2670406.4502 | 1211412.1169
123 | 2670400.4195 | 1211425.3763 | 2670399.6433 | 1211421.6092 | 2670408.4565 | 1211419.8232
124 | 2670408.4565 | 1211419.8232 | 2670413.4992 | 1211418.8043 | 2670421.8323 | 1211417.7693
125 | 2670400.4195 | 1211425.3763 | 2670400.7285 | 1211426.8809 | 2670400.5072 | 1211441.7653
126 | 2670501.9956 | 1211401.0039 | 2670534.6029 | 1211393.1229
127 | 2670501.9956 | 1211401.0039 | 2670485.2833 | 1211405.0432 | 2670482.0248 | 1211407.484 | 2670474.246 | 1211409.8269 | 2670469.6298 | 1211410.947
128 | 2670347.9411 | 1211594.5462 | 2670355.4743 | 1211601.5674 | 2670366.0831 | 1211611.81 | 2670366.4227 | 1211612.2087
129 | 2670322.2328 | 1211572.121 | 2670325.5403 | 1211574.6866 | 2670332.0838 | 1211579.7669 | 2670347.9411 | 1211594.5462
130 | 2670310.6792 | 1211563.5378 | 2670314.9305 | 1211566.4564 | 2670322.2328 | 1211572.121
131 | 2670384.0239 | 1211280.8815 | 2670388.8831 | 1211294.7697 | 2670394.6032 | 1211319.4192 | 2670395.9451 | 1211325.0436
132 | 2670384.0239 | 1211280.8815 | 2670396.9629 | 1211285.6037 | 2670411.1915 | 1211289.2294 | 2670422.1746 | 1211290.9823 | 2670430.1798 | 1211291.3548
133 | 2670384.0239 | 1211280.8815 | 2670382.3676 | 1211271.8452 | 2670381.465 | 1211262.0395 | 2670380.9063 | 1211257.2188 | 2670380.3037 | 1211255.4773
134 | 2670430.1798 | 1211291.3548 | 2670430.0298 | 1211286.0386 | 2670430.4313 | 1211282.2855 | 2670432.9626 | 1211270.6414 | 2670434.7923 | 1211262.4245
135 | 2670364.128 | 1211248.2821 | 2670366.4017 | 1211249.9321 | 2670374.9515 | 1211253.7464 | 2670380.3037 | 1211255.4773
136 | 2670310.6792 | 1211563.5378 | 2670288.9418 | 1211556.396
137 | 2670261.6467 | 1211545.8492 | 2670272.7782 | 1211551.0836 | 2670282.0737 | 1211554.1394 | 2670288.9418 | 1211556.396
138 | 2670310.6792 | 1211563.5378 | 2670320.307 | 1211540.9816 | 2670324.5524 | 1211536.0286 | 2670329.4856 | 1211533.9743 | 2670334.5078 | 1211534.0336 | 2670344.9706 | 1211536.0471 | 2670357.8355 | 1211539.369
139 | 2670261.6467 | 1211545.8492 | 2670258.8331 | 1211550.5301 | 2670257.0574 | 1211552.2547 | 2670254.3041 | 1211553.7566 | 2670248.4571 | 1211556.634 | 2670242.501 | 1211559.0876 | 2670240.2936 | 1211560.696 | 2670231.321 | 1211570.4822
140 | 2670261.6467 | 1211545.8492 | 2670251.1054 | 1211540.5318
141 | 2670277.2499 | 1211487.5966 | 2670272.4859 | 1211481.8539

## bus_geodata
| x | y | coords
0 | 2670343.9957 | 1211808.8737
1 | 2670423.8035 | 1211680.0448
2 | 2670422.1327 | 1211673.5321
3 | 2670629.2828 | 1211550.3016
4 | 2670595.6928 | 1211515.284
5 | 2670568.585 | 1211528.316
6 | 2670655.6397 | 1211468.4989
7 | 2670548.0479 | 1211446.2193
8 | 2670516.3843 | 1211454.2009
9 | 2670563.2887 | 1211529.431
10 | 2670544.858 | 1211533.3122
11 | 2670573.9936 | 1211373.5307
12 | 2670565.0809 | 1211375.5568
13 | 2670780.3223 | 1211977.2009
14 | 2670772.429 | 1211971.1965
15 | 2670610.3646 | 1211809.3416
16 | 2670558.6382 | 1211755.4672
17 | 2670577.2042 | 1211350.565
18 | 2670545.1022 | 1211363.4018
19 | 2670539.4759 | 1211343.2513
20 | 2670548.0268 | 1211375.0548
21 | 2670513.7988 | 1211299.9811
22 | 2670550.6034 | 1211385.2917
23 | 2670539.9695 | 1211357.775
24 | 2670507.3409 | 1211291.4995
25 | 2670514.5729 | 1211393.8921
26 | 2670551.1135 | 1211389.7005
27 | 2670539.5374 | 1211356.0377
28 | 2670535.3088 | 1211343.318
29 | 2670526.4247 | 1211338.8768
30 | 2670494.407 | 1211294.0705
31 | 2670527.0223 | 1211286.3744
32 | 2670483.4199 | 1211288.8041
33 | 2670477.9947 | 1211310.6092
34 | 2670478.1067 | 1211266.4162
35 | 2670441.2292 | 1211291.3189
36 | 2670471.2635 | 1211535.0213
37 | 2670470.8027 | 1211531.1331
38 | 2670471.6559 | 1211538.3322
39 | 2670470.5578 | 1211529.0671
40 | 2670505.9171 | 1211556.5499
41 | 2670464.303 | 1211496.1903
42 | 2670504.0143 | 1211565.6062
43 | 2670525.9083 | 1211591.3619
44 | 2670523.1343 | 1211538.1756
45 | 2670527.9259 | 1211597.4563
46 | 2670544.6818 | 1211590.1002
47 | 2670543.0205 | 1211533.6992
48 | 2670547.7369 | 1211620.516
49 | 2670435.9121 | 1211481.5858
50 | 2670436.0777 | 1211471.4259
51 | 2670431.2282 | 1211487.6897
52 | 2670473.2625 | 1211463.0865
53 | 2670487.6498 | 1211459.4098
54 | 2670468.7472 | 1211464.2404
55 | 2670502.8864 | 1211455.516
56 | 2670465.9431 | 1211451.0825
57 | 2670503.431 | 1211457.6571
58 | 2670505.1895 | 1211454.9276
59 | 2670465.5626 | 1211449.2968
60 | 2670436.469 | 1211449.5438
61 | 2670513.2804 | 1211452.8603
62 | 2670437.0177 | 1211418.8597
63 | 2670139.5304 | 1211454.5217
64 | 2670119.2221 | 1211460.3649
65 | 2670131.8785 | 1211462.6151
66 | 2670133.9909 | 1211467.1427
67 | 2670136.7113 | 1211472.9672
68 | 2670177.7539 | 1211446.1495
69 | 2670151.5497 | 1211485.2045
70 | 2670240.2623 | 1211443.3946
71 | 2670205.7525 | 1211435.5116
72 | 2670269.668 | 1211444.8695
73 | 2670385.5139 | 1211516.0666
74 | 2670411.8885 | 1211535.8121
75 | 2670364.9813 | 1211500.6947
76 | 2670426.9466 | 1211549.2277
77 | 2670353.5134 | 1211492.1092
78 | 2670427.0186 | 1211549.3677
79 | 2670341.6707 | 1211485.3209
80 | 2670358.5357 | 1211491.916
81 | 2670386.964 | 1211546.8905
82 | 2670327.2044 | 1211489.377
83 | 2670327.8203 | 1211464.4779
84 | 2670315.9568 | 1211510.1762
85 | 2670338.8908 | 1211463.9414
86 | 2670306.831 | 1211449.7214
87 | 2670383.9085 | 1211490.9398
88 | 2670269.3397 | 1211448.2233
89 | 2670268.7168 | 1211454.6533
90 | 2670322.845 | 1211472.0351
91 | 2670276.8729 | 1211464.133
92 | 2670268.0939 | 1211476.5596
93 | 2670556.1906 | 1211649.1005
94 | 2670536.8748 | 1211646.1353
95 | 2670538.0781 | 1211646.423
96 | 2670515.0451 | 1211640.9163
97 | 2670511.9798 | 1211640.1834
98 | 2670471.773 | 1211702.5101
99 | 2670422.568 | 1211489.4525
100 | 2670420.5999 | 1211489.5282
101 | 2670413.768 | 1211489.7911
102 | 2670410.0988 | 1211367.6211
103 | 2670422.0082 | 1211375.8556
104 | 2670420.6526 | 1211369.0243
105 | 2670431.6265 | 1211386.7568
106 | 2670457.3439 | 1211404.8242
107 | 2670476.7492 | 1211403.1412
108 | 2670437.0929 | 1211414.4244
109 | 2670315.467 | 1211510.1533
110 | 2670346.5713 | 1211425.4746
111 | 2670364.8916 | 1211433.9403
112 | 2670348.2843 | 1211407.8071
113 | 2670408.4565 | 1211419.8232
114 | 2670406.4502 | 1211412.1169
115 | 2670400.4195 | 1211425.3763
116 | 2670421.8323 | 1211417.7693
117 | 2670400.5072 | 1211441.7653
118 | 2670375.4499 | 1211437.2437
119 | 2670501.9956 | 1211401.0039
120 | 2670534.6029 | 1211393.1229
121 | 2670469.6298 | 1211410.947
122 | 2670540.1278 | 1211446.0007
123 | 2670366.4227 | 1211612.2087
124 | 2670347.9411 | 1211594.5462
125 | 2670322.2328 | 1211572.121
126 | 2670395.9451 | 1211325.0436
127 | 2670384.0239 | 1211280.8815
128 | 2670430.1798 | 1211291.3548
129 | 2670380.3037 | 1211255.4773
130 | 2670434.7923 | 1211262.4245
131 | 2670364.128 | 1211248.2821
132 | 2670315.3665 | 1211510.1486
133 | 2670472.7232 | 1211368.9278
134 | 2670288.9418 | 1211556.396
135 | 2670310.6792 | 1211563.5378
136 | 2670261.6467 | 1211545.8492
137 | 2670357.8355 | 1211539.369
138 | 2670231.321 | 1211570.4822
139 | 2670251.1054 | 1211540.5318
140 | 2670272.4859 | 1211481.8539
141 | 2670277.2499 | 1211487.5966
142 | 2670250.2259 | 1211474.8593
143 | 2670436.0777 | 1211471.4259

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98594 | -0.27093 | 0.0011061 | 0.00027722
1 | 0.98609 | -0.26792 | 0.0030797 | 0.00077183
2 | 0.98612 | -0.26742 | 0 | 0
3 | 0.98712 | -0.24778 | 0.0059035 | 0.0014796
4 | 0.98739 | -0.24262 | 0 | 0
5 | 0.98787 | -0.23328 | 0 | 0
6 | 0.98659 | -0.2582 | 0.01128 | 0.0028271
7 | 0.99255 | -0.14313 | 0.016022 | 0.0040155
8 | 0.99303 | -0.13386 | 0.013536 | 0.0033925
9 | 0.98795 | -0.23162 | 0.0030841 | 0.00077295
10 | 0.9883 | -0.2248 | 0.0013172 | 0.00033012
11 | 0.98716 | -0.24644 | 0.0066853 | 0.0016755
12 | 0.98721 | -0.24535 | 0 | 0
13 | 0.98559 | -0.2778 | 0.0012929 | 0.00032404
14 | 0.9856 | -0.27757 | 0 | 0
15 | 0.98587 | -0.27224 | 0 | 0
16 | 0.98596 | -0.27047 | 0.0027295 | 0.00068408
17 | 0.98659 | -0.25747 | 0.005179 | 0.001298
18 | 0.98675 | -0.25426 | 0 | 0
19 | 0.98585 | -0.27186 | 0.0047493 | 0.0011903
20 | 0.98733 | -0.24309 | 0 | 0
21 | 0.98385 | -0.31065 | 0 | 0
22 | 0.98806 | -0.22884 | 0 | 0
23 | 0.98696 | -0.25028 | 0.0033364 | 0.00083619
24 | 0.98331 | -0.3213 | 0 | 0
25 | 0.98794 | -0.23115 | 0.0034944 | 0.00087577
26 | 0.98839 | -0.22258 | 0 | 0
27 | 0.98694 | -0.25071 | 0.0040074 | 0.0010044
28 | 0.98682 | -0.25299 | 0 | 0
29 | 0.98673 | -0.25469 | 0.0094877 | 0.0023778
30 | 0.98284 | -0.3304 | 0 | 0
31 | 0.98293 | -0.32878 | 0.015513 | 0.003888
32 | 0.9826 | -0.33513 | 0 | 0
33 | 0.98273 | -0.33253 | 0.0050221 | 0.0012587
34 | 0.98256 | -0.33584 | 0.0016949 | 0.00042478
35 | 0.98174 | -0.35205 | 0.0078906 | 0.0019776
36 | 0.9918 | -0.15701 | 0.0043817 | 0.0010982
37 | 0.99205 | -0.15232 | 0.0035323 | 0.00088528
38 | 0.99161 | -0.16075 | 0.0033451 | 0.00083836
39 | 0.99218 | -0.14969 | 0.0034962 | 0.00087622
40 | 0.98948 | -0.20206 | 0.0022945 | 0.00057507
41 | 0.99451 | -0.10493 | 0.0045203 | 0.0011329
42 | 0.98922 | -0.20694 | 0.0095743 | 0.0023996
43 | 0.98857 | -0.21956 | 0 | 0
44 | 0.9888 | -0.21522 | 0.0039377 | 0.00098688
45 | 0.98847 | -0.22152 | 0.00099727 | 0.00024994
46 | 0.98853 | -0.22043 | 0.0025987 | 0.0006513
47 | 0.98834 | -0.22408 | 0.0027581 | 0.00069125
48 | 0.98802 | -0.23031 | 0 | 0
49 | 0.99693 | -0.058532 | 0 | 0
50 | 0.99794 | -0.03921 | 0 | 0
51 | 0.99593 | -0.077541 | 0.0045203 | 0.0011329
52 | 0.9949 | -0.097734 | 0.0096621 | 0.0024215
53 | 0.99415 | -0.11227 | 0.0071263 | 0.001786
54 | 0.99518 | -0.092385 | 0 | 0
55 | 0.99345 | -0.1257 | 0 | 0
56 | 0.99486 | -0.098421 | 0.0071263 | 0.001786
57 | 0.99339 | -0.12686 | 0 | 0
58 | 0.99341 | -0.12649 | 0.0035407 | 0.00088739
59 | 0.99483 | -0.099012 | 0.018359 | 0.0046012
60 | 1 | 0 | -0.45957 | -0.1165
61 | 0.99329 | -0.12875 | 0.0036453 | 0.00091359
62 | 0.99795 | -0.039053 | 0 | 0
63 | 0.97958 | -0.39405 | 0.0081619 | 0.0020456
64 | 0.97974 | -0.39091 | 0 | 0
65 | 0.97987 | -0.38833 | 0 | 0
66 | 0.97991 | -0.38759 | 0 | 0
67 | 0.97986 | -0.38848 | 0.0035354 | 0.00088604
68 | 0.98061 | -0.37369 | 0.0023851 | 0.00059777
69 | 0.97979 | -0.3899 | 0.004075 | 0.0010213
70 | 0.98168 | -0.35277 | 0.0022784 | 0.00057102
71 | 0.98211 | -0.3444 | 0.0020526 | 0.00051443
72 | 0.98223 | -0.342 | 0 | 0
73 | 0.98649 | -0.25927 | 0.0024904 | 0.00062414
74 | 0.98548 | -0.27875 | 0.0055248 | 0.0013846
75 | 0.98732 | -0.24299 | 0.0015724 | 0.00039407
76 | 0.98497 | -0.28885 | 0.0045538 | 0.0011413
77 | 0.98781 | -0.23351 | 0 | 0
78 | 0.98496 | -0.28892 | 0.0032093 | 0.00080433
79 | 0.98687 | -0.25178 | 0 | 0
80 | 0.9883 | -0.22411 | 0.0026735 | 0.00067004
81 | 0.98415 | -0.30473 | 0.0023731 | 0.00059476
82 | 0.98681 | -0.25288 | 0.0038599 | 0.00096738
83 | 0.98548 | -0.27879 | 0 | 0
84 | 0.9865 | -0.25906 | 0.0038586 | 0.00096705
85 | 0.9854 | -0.28029 | 0.0075661 | 0.0018963
86 | 0.98368 | -0.31375 | 0 | 0
87 | 0.99081 | -0.17559 | 0.0031833 | 0.00079781
88 | 0.98224 | -0.34188 | 0 | 0
89 | 0.98213 | -0.3441 | 0 | 0
90 | 0.98343 | -0.3186 | 0.0069576 | 0.0017437
91 | 0.98206 | -0.34533 | 0.0053822 | 0.0013489
92 | 0.98185 | -0.34949 | 0 | 0
93 | 0.98757 | -0.23908 | 0 | 0
94 | 0.98728 | -0.24473 | 0.0010757 | 0.00026959
95 | 0.9873 | -0.24441 | 0.0021314 | 0.00053418
96 | 0.98702 | -0.24993 | 0.0010876 | 0.00027259
97 | 0.98698 | -0.2506 | 0.0024658 | 0.000618
98 | 0.98634 | -0.26309 | 0.0011793 | 0.00029557
99 | 0.99481 | -0.09893 | 0.002572 | 0.0006446
100 | 0.99457 | -0.10347 | 0.017548 | 0.004398
101 | 0.99386 | -0.11711 | 0.0026394 | 0.00066149
102 | 0.99678 | -0.06164 | 0.0044836 | 0.0011237
103 | 0.99684 | -0.060385 | 0 | 0
104 | 0.99682 | -0.060864 | 0.0038328 | 0.00096058
105 | 0.99695 | -0.058262 | 0.0046938 | 0.0011764
106 | 0.99736 | -0.050337 | 0 | 0
107 | 0.99729 | -0.051728 | 0 | 0
108 | 0.99775 | -0.042853 | 0 | 0
109 | 0.98649 | -0.2591 | 0.002848 | 0.00071378
110 | 0.99631 | -0.070738 | 0 | 0
111 | 0.99646 | -0.067857 | 0 | 0
112 | 0.99622 | -0.072318 | 0.0050474 | 0.001265
113 | 0.99702 | -0.057034 | 0 | 0
114 | 0.99697 | -0.057872 | 0.0060002 | 0.0015038
115 | 0.99683 | -0.060697 | 0 | 0
116 | 0.99729 | -0.051748 | 0.010221 | 0.0025617
117 | 0.99675 | -0.062158 | 0.0050712 | 0.001271
118 | 0.99638 | -0.069394 | 0.006146 | 0.0015403
119 | 0.99222 | -0.14856 | 0.0027246 | 0.00068286
120 | 0.98962 | -0.19878 | 0.0053206 | 0.0013335
121 | 0.99496 | -0.096076 | 0.0097273 | 0.0024379
122 | 0.993 | -0.13446 | 0.011661 | 0.0029226
123 | 0.98244 | -0.33813 | 0.0018631 | 0.00046693
124 | 0.98249 | -0.33727 | 0.0028382 | 0.00071133
125 | 0.98263 | -0.33437 | 0.0025212 | 0.00063186
126 | 0.98101 | -0.36633 | 0.0053764 | 0.0013474
127 | 0.98123 | -0.36187 | 0 | 0
128 | 0.98161 | -0.35444 | 0 | 0
129 | 0.98116 | -0.36339 | 0.0016088 | 0.0004032
130 | 0.98152 | -0.3562 | 0.0033029 | 0.00082778
131 | 0.98113 | -0.36392 | 0.0016577 | 0.00041545
132 | 0.98649 | -0.2591 | 0.0010519 | 0.00026364
133 | 0.99718 | -0.053902 | 0.0034131 | 0.00085541
134 | 0.98255 | -0.33595 | 0.0017211 | 0.00043135
135 | 0.98273 | -0.33249 | 0 | 0
136 | 0.98237 | -0.33947 | 0 | 0
137 | 0.98367 | -0.31411 | 0.0017125 | 0.00042918
138 | 0.98227 | -0.34154 | 0.002864 | 0.00071778
139 | 0.98233 | -0.34028 | 0.0037858 | 0.00094882
140 | 0.98181 | -0.35034 | 0.003195 | 0.00080073
141 | 0.98178 | -0.35082 | 0.0035791 | 0.000897
142 | 0.98174 | -0.35171 | 0.0068506 | 0.0017169
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0011061 | -0.00027722 | 0.0011063 | 0.00027539 | 1.5832e-07 | -1.8316e-06 | 0.0016694 | 0.0016687 | 0.0016694 | 0.98594 | -0.27093 | 0.98609 | -0.26792 | 0.45863
1 | -0.0041859 | -0.0010472 | 0.0041861 | 0.0010472 | 1.0058e-07 | -2.1404e-08 | 0.0063159 | 0.0063159 | 0.0063159 | 0.98609 | -0.26792 | 0.98612 | -0.26742 | 1.7351
2 | -0.0041861 | -0.0010472 | 0.0041869 | 0.001047 | 8.6036e-07 | -1.8331e-07 | 0.0063159 | 0.0063156 | 0.0063159 | 0.98612 | -0.26742 | 0.98634 | -0.26309 | 1.7351
3 | -0.0059035 | -0.0014796 | 0.0059049 | 0.0014799 | 1.4523e-06 | 3.0413e-07 | 0.0088991 | 0.0088988 | 0.0088991 | 0.98712 | -0.24778 | 0.98739 | -0.24262 | 2.4448
4 | -0.017194 | -0.0043114 | 0.017201 | 0.0043159 | 7.6529e-06 | 4.5089e-06 | 0.025912 | 0.025912 | 0.025912 | 0.98739 | -0.24262 | 0.98787 | -0.23328 | 7.1187
5 | 0.011289 | 0.0028315 | -0.01128 | -0.0028271 | 8.3817e-06 | 4.3775e-06 | 0.017013 | 0.017014 | 0.017014 | 0.98739 | -0.24262 | 0.98659 | -0.2582 | 4.6741
6 | -0.017201 | -0.0043159 | 0.017203 | 0.0043167 | 1.3628e-06 | 8.0288e-07 | 0.025912 | 0.025912 | 0.025912 | 0.98787 | -0.23328 | 0.98795 | -0.23162 | 7.1187
7 | -0.016022 | -0.0040155 | 0.016029 | 0.0040196 | 7.0785e-06 | 4.1072e-06 | 0.02402 | 0.02402 | 0.02402 | 0.99255 | -0.14313 | 0.99303 | -0.13386 | 6.599
8 | -0.029566 | -0.0074121 | 0.029575 | 0.0074183 | 9.8679e-06 | 6.1419e-06 | 0.044304 | 0.044304 | 0.044304 | 0.99303 | -0.13386 | 0.99339 | -0.12686 | 12.1713
9 | -0.020287 | -0.0050896 | 0.020293 | 0.0050936 | 6.5951e-06 | 3.9796e-06 | 0.030557 | 0.030557 | 0.030557 | 0.98795 | -0.23162 | 0.9883 | -0.2248 | 8.3948
10 | -0.021611 | -0.0054237 | 0.021611 | 0.0054242 | 7.4562e-07 | 4.5313e-07 | 0.03254 | 0.03254 | 0.03254 | 0.9883 | -0.2248 | 0.98834 | -0.22408 | 8.9396
11 | -0.0066853 | -0.0016755 | 0.0066857 | 0.0016756 | 3.4807e-07 | 1.0591e-07 | 0.010077 | 0.010077 | 0.010077 | 0.98716 | -0.24644 | 0.98721 | -0.24535 | 2.7685
12 | -0.0066857 | -0.0016756 | 0.0066864 | 0.0016758 | 7.1997e-07 | 2.1902e-07 | 0.010077 | 0.010077 | 0.010077 | 0.98721 | -0.24535 | 0.98733 | -0.24309 | 2.7685
13 | -0.0012929 | -0.00032404 | 0.0012929 | 0.00032392 | 1.4171e-08 | -1.1732e-07 | 0.001952 | 0.001952 | 0.001952 | 0.98559 | -0.2778 | 0.9856 | -0.27757 | 0.53627
14 | -0.0012929 | -0.00032392 | 0.0012933 | 0.00032121 | 3.2709e-07 | -2.7105e-06 | 0.001952 | 0.0019509 | 0.001952 | 0.9856 | -0.27757 | 0.98587 | -0.27224 | 0.53625
15 | -0.0012933 | -0.00032121 | 0.0012934 | 0.00032031 | 1.0821e-07 | -8.9776e-07 | 0.0019509 | 0.0019506 | 0.0019509 | 0.98587 | -0.27224 | 0.98596 | -0.27047 | 0.53597
16 | -0.0040229 | -0.0010044 | 0.0040243 | 0.001004 | 1.4093e-06 | -3.9952e-07 | 0.0060699 | 0.0060695 | 0.0060699 | 0.98596 | -0.27047 | 0.98634 | -0.26309 | 1.6676
17 | -0.005179 | -0.001298 | 0.0051798 | 0.001298 | 7.9105e-07 | 6.4702e-08 | 0.0078112 | 0.0078111 | 0.0078112 | 0.98659 | -0.25747 | 0.98675 | -0.25426 | 2.1459
18 | 0.047 | 0.011845 | -0.04696 | -0.01182 | 3.9527e-05 | 2.503e-05 | 0.070899 | 0.070899 | 0.070899 | 0.98675 | -0.25426 | 0.98585 | -0.27186 | 19.4777
19 | -0.052179 | -0.013144 | 0.052207 | 0.013161 | 2.7911e-05 | 1.771e-05 | 0.07871 | 0.07871 | 0.07871 | 0.98675 | -0.25426 | 0.98733 | -0.24309 | 21.6236
20 | 0.042211 | 0.01063 | -0.042133 | -0.010581 | 7.8143e-05 | 4.9359e-05 | 0.06373 | 0.063731 | 0.063731 | 0.98585 | -0.27186 | 0.98385 | -0.31065 | 17.5084
21 | -0.075733 | -0.01906 | 0.075785 | 0.019093 | 5.16e-05 | 3.2889e-05 | 0.11417 | 0.11417 | 0.11417 | 0.98733 | -0.24309 | 0.98806 | -0.22884 | 31.3645
22 | 0.016839 | 0.0042228 | -0.016834 | -0.0042194 | 5.7686e-06 | 3.3866e-06 | 0.02538 | 0.02538 | 0.02538 | 0.98733 | -0.24309 | 0.98696 | -0.25028 | 6.9725
23 | 0.042133 | 0.010581 | -0.042111 | -0.010567 | 2.1391e-05 | 1.3512e-05 | 0.063731 | 0.063731 | 0.063731 | 0.98385 | -0.31065 | 0.98331 | -0.3213 | 17.5084
24 | 0.0034948 | 0.00087554 | -0.0034944 | -0.00087577 | 3.8478e-07 | -2.2813e-07 | 0.005263 | 0.0052631 | 0.0052631 | 0.98806 | -0.22884 | 0.98794 | -0.23115 | 1.4459
25 | -0.079279 | -0.019968 | 0.079303 | 0.019983 | 2.3743e-05 | 1.5139e-05 | 0.11943 | 0.11943 | 0.11943 | 0.98806 | -0.22884 | 0.98839 | -0.22258 | 32.8103
26 | 0.013497 | 0.0033832 | -0.013497 | -0.003383 | 2.7801e-07 | 1.5505e-07 | 0.02035 | 0.02035 | 0.02035 | 0.98696 | -0.25028 | 0.98694 | -0.25071 | 5.5905
27 | 0.026592 | 0.0066761 | -0.026581 | -0.0066689 | 1.154e-05 | 7.1445e-06 | 0.040246 | 0.040246 | 0.040246 | 0.98331 | -0.3213 | 0.98284 | -0.3304 | 11.0566
28 | 0.015519 | 0.0038912 | -0.015513 | -0.003888 | 5.529e-06 | 3.1996e-06 | 0.023485 | 0.023485 | 0.023485 | 0.98331 | -0.3213 | 0.98293 | -0.32878 | 6.4519
29 | -0.079303 | -0.019983 | 0.079394 | 0.020041 | 9.039e-05 | 5.7632e-05 | 0.11943 | 0.11943 | 0.11943 | 0.98839 | -0.22258 | 0.98962 | -0.19878 | 32.8103
30 | 0.0094895 | 0.0023787 | -0.0094884 | -0.0023782 | 1.0307e-06 | 4.8808e-07 | 0.014308 | 0.014308 | 0.014308 | 0.98694 | -0.25071 | 0.98682 | -0.25299 | 3.9307
31 | 0.0094884 | 0.0023782 | -0.0094877 | -0.0023778 | 7.6811e-07 | 3.6377e-07 | 0.014308 | 0.014308 | 0.014308 | 0.98682 | -0.25299 | 0.98673 | -0.25469 | 3.9307
32 | 0.021558 | 0.0054103 | -0.021553 | -0.0054073 | 4.8626e-06 | 2.9579e-06 | 0.032642 | 0.032642 | 0.032642 | 0.98284 | -0.3304 | 0.9826 | -0.33513 | 8.9675
33 | 0.0050226 | 0.0012587 | -0.0050221 | -0.0012587 | 5.1064e-07 | 2.8409e-08 | 0.0076042 | 0.0076043 | 0.0076043 | 0.98284 | -0.3304 | 0.98273 | -0.33253 | 2.0891
34 | 0.0016949 | 0.00042452 | -0.0016949 | -0.00042478 | 5.6902e-08 | -2.5531e-07 | 0.0025667 | 0.0025668 | 0.0025668 | 0.9826 | -0.33513 | 0.98256 | -0.33584 | 0.70516
35 | 0.019858 | 0.0049828 | -0.019842 | -0.0049731 | 1.6006e-05 | 9.6468e-06 | 0.030075 | 0.030075 | 0.030075 | 0.9826 | -0.33513 | 0.98174 | -0.35205 | 8.2624
36 | 0.011952 | 0.0029955 | -0.01195 | -0.0029948 | 1.3613e-06 | 7.314e-07 | 0.018115 | 0.018115 | 0.018115 | 0.98174 | -0.35205 | 0.98161 | -0.35444 | 4.9768
37 | -0.067855 | -0.017083 | 0.067871 | 0.017092 | 1.5226e-05 | 9.6938e-06 | 0.10183 | 0.10183 | 0.10183 | 0.9918 | -0.15701 | 0.99205 | -0.15232 | 27.9757
38 | 0.063474 | 0.015985 | -0.063462 | -0.015977 | 1.1345e-05 | 7.2179e-06 | 0.095258 | 0.095258 | 0.095258 | 0.9918 | -0.15701 | 0.99161 | -0.16075 | 26.1696
39 | -0.071403 | -0.017978 | 0.071412 | 0.017983 | 8.9539e-06 | 5.7036e-06 | 0.10713 | 0.10713 | 0.10713 | 0.99205 | -0.15232 | 0.99218 | -0.14969 | 29.4312
40 | 0.060117 | 0.015139 | -0.059999 | -0.015064 | 0.00011849 | 7.5334e-05 | 0.090238 | 0.090238 | 0.090238 | 0.99161 | -0.16075 | 0.98948 | -0.20206 | 24.7907
41 | -0.074908 | -0.01886 | 0.075069 | 0.018962 | 0.00016068 | 0.0001024 | 0.11237 | 0.11237 | 0.11237 | 0.99218 | -0.14969 | 0.99451 | -0.10493 | 30.8717
42 | 0.028335 | 0.0071197 | -0.028318 | -0.0071087 | 1.7785e-05 | 1.1048e-05 | 0.042618 | 0.042618 | 0.042618 | 0.98948 | -0.20206 | 0.9888 | -0.21522 | 11.7084
43 | 0.029369 | 0.0073689 | -0.029362 | -0.0073646 | 6.8333e-06 | 4.2533e-06 | 0.044169 | 0.044169 | 0.044169 | 0.98948 | -0.20206 | 0.98922 | -0.20694 | 12.1344
44 | -0.079589 | -0.020095 | 0.079766 | 0.020208 | 0.00017733 | 0.00011306 | 0.11914 | 0.11914 | 0.11914 | 0.99451 | -0.10493 | 0.99693 | -0.058532 | 32.7297
45 | 0.019788 | 0.0049651 | -0.019776 | -0.0049579 | 1.1899e-05 | 7.1562e-06 | 0.029767 | 0.029767 | 0.029767 | 0.98922 | -0.20694 | 0.98857 | -0.21956 | 8.1779
46 | 0.017177 | 0.0043068 | -0.017175 | -0.0043059 | 1.6094e-06 | 9.4769e-07 | 0.025856 | 0.025856 | 0.025856 | 0.98857 | -0.21956 | 0.98847 | -0.22152 | 7.1032
47 | 0.0025988 | 0.00065113 | -0.0025987 | -0.0006513 | 1.0815e-07 | -1.7242e-07 | 0.0039117 | 0.0039118 | 0.0039118 | 0.98857 | -0.21956 | 0.98853 | -0.22043 | 1.0747
48 | 0.02438 | 0.0061218 | -0.02437 | -0.0061154 | 1.0306e-05 | 6.334e-06 | 0.036693 | 0.036693 | 0.036693 | 0.9888 | -0.21522 | 0.98834 | -0.22408 | 10.0804
49 | 0.016178 | 0.0040559 | -0.016171 | -0.004052 | 6.7669e-06 | 3.941e-06 | 0.024354 | 0.024355 | 0.024355 | 0.98847 | -0.22152 | 0.98802 | -0.23031 | 6.6908
50 | 0.016171 | 0.004052 | -0.016165 | -0.004048 | 6.7583e-06 | 3.9364e-06 | 0.024355 | 0.024355 | 0.024355 | 0.98802 | -0.23031 | 0.98757 | -0.23908 | 6.6909
51 | -0.219 | -0.055649 | 0.21921 | 0.055779 | 0.00020395 | 0.00013027 | 0.32716 | 0.32716 | 0.32716 | 0.99693 | -0.058532 | 0.99794 | -0.03921 | 44.939
52 | 0.13924 | 0.035441 | -0.13911 | -0.03536 | 0.00012748 | 8.1484e-05 | 0.20802 | 0.20802 | 0.20802 | 0.99693 | -0.058532 | 0.99593 | -0.077541 | 57.1484
53 | -0.31024 | -0.078727 | 0.31082 | 0.079101 | 0.00058628 | 0.00037436 | 0.46293 | 0.46293 | 0.46293 | 0.99794 | -0.03921 | 1 | 0 | 42.3933
54 | 0.091029 | 0.022948 | -0.090798 | -0.0228 | 0.00023099 | 0.0001474 | 0.13578 | 0.13578 | 0.13578 | 0.99794 | -0.03921 | 0.99518 | -0.092385 | 37.3019
55 | 0.13459 | 0.034227 | -0.13445 | -0.034138 | 0.00013854 | 8.8545e-05 | 0.20127 | 0.20127 | 0.20127 | 0.99593 | -0.077541 | 0.99481 | -0.09893 | 55.293
56 | 0.055626 | 0.013976 | -0.055587 | -0.013952 | 3.8556e-05 | 2.4483e-05 | 0.083209 | 0.083209 | 0.083209 | 0.9949 | -0.097734 | 0.99415 | -0.11227 | 22.8596
57 | -0.065288 | -0.016398 | 0.065305 | 0.016408 | 1.6668e-05 | 1.0607e-05 | 0.09766 | 0.09766 | 0.09766 | 0.9949 | -0.097734 | 0.99518 | -0.092385 | 26.8297
58 | 0.048461 | 0.012166 | -0.04843 | -0.012146 | 3.1035e-05 | 1.9658e-05 | 0.072543 | 0.072543 | 0.072543 | 0.99415 | -0.11227 | 0.99345 | -0.1257 | 19.9293
59 | 0.025493 | 0.006392 | -0.025486 | -0.0063875 | 7.3307e-06 | 4.5169e-06 | 0.038119 | 0.038119 | 0.038119 | 0.99518 | -0.092385 | 0.99486 | -0.098421 | 10.4723
60 | 0.029577 | 0.0074193 | -0.029575 | -0.0074183 | 1.6259e-06 | 1.012e-06 | 0.044304 | 0.044304 | 0.044304 | 0.99345 | -0.1257 | 0.99339 | -0.12686 | 12.1713
61 | 0.018853 | 0.0047267 | -0.018852 | -0.0047262 | 7.1083e-07 | 4.2416e-07 | 0.028239 | 0.028239 | 0.028239 | 0.99345 | -0.1257 | 0.99341 | -0.12649 | 7.758
62 | 0.018359 | 0.0046015 | -0.018359 | -0.0046012 | 5.1629e-07 | 3.0672e-07 | 0.02746 | 0.02746 | 0.02746 | 0.99486 | -0.098421 | 0.99483 | -0.099012 | 7.544
63 | 0.015312 | 0.0038389 | -0.01531 | -0.0038379 | 1.6473e-06 | 9.4619e-07 | 0.022936 | 0.022936 | 0.022936 | 0.99341 | -0.12649 | 0.99329 | -0.12875 | 6.301
64 | 0.1471 | 0.037399 | -0.14682 | -0.037224 | 0.00027615 | 0.00017593 | 0.21907 | 0.21907 | 0.21907 | 1 | 0 | 0.99795 | -0.039053 | 30.0919
65 | 0.011665 | 0.0029243 | -0.011661 | -0.0029226 | 3.1731e-06 | 1.6722e-06 | 0.017475 | 0.017475 | 0.017475 | 0.99329 | -0.12875 | 0.993 | -0.13446 | 4.8008
66 | 0.048959 | 0.012285 | -0.04895 | -0.01228 | 8.8684e-06 | 5.6178e-06 | 0.073007 | 0.073007 | 0.073007 | 0.99795 | -0.039053 | 0.99775 | -0.042853 | 20.0568
67 | 0.09786 | 0.024938 | -0.097592 | -0.024767 | 0.00026848 | 0.00017139 | 0.14606 | 0.14606 | 0.14606 | 0.99795 | -0.039053 | 0.99496 | -0.096076 | 40.1272
68 | -0.0081619 | -0.0020456 | 0.0081631 | 0.0020461 | 1.2197e-06 | 5.1421e-07 | 0.012398 | 0.012398 | 0.012398 | 0.97958 | -0.39405 | 0.97974 | -0.39091 | 3.4061
69 | -0.0081631 | -0.0020461 | 0.0081641 | 0.0020465 | 1.0026e-06 | 4.2261e-07 | 0.012398 | 0.012398 | 0.012398 | 0.97974 | -0.39091 | 0.97987 | -0.38833 | 3.4061
70 | -0.0081641 | -0.0020465 | 0.0081644 | 0.0020466 | 2.8786e-07 | 1.2132e-07 | 0.012398 | 0.012398 | 0.012398 | 0.97987 | -0.38833 | 0.97991 | -0.38759 | 3.4061
71 | 0.007611 | 0.0019074 | -0.0076106 | -0.0019073 | 3.2201e-07 | 1.2511e-07 | 0.011557 | 0.011557 | 0.011557 | 0.97991 | -0.38759 | 0.97986 | -0.38848 | 3.1751
72 | -0.015775 | -0.003954 | 0.015786 | 0.0039601 | 1.0455e-05 | 6.0785e-06 | 0.023955 | 0.023955 | 0.023955 | 0.97991 | -0.38759 | 0.98061 | -0.37369 | 6.5812
73 | 0.0040753 | 0.0010212 | -0.004075 | -0.0010213 | 2.7624e-07 | -6.5455e-08 | 0.0061887 | 0.0061888 | 0.0061888 | 0.97986 | -0.38848 | 0.97979 | -0.3899 | 1.7002
74 | -0.018171 | -0.0045579 | 0.018189 | 0.0045687 | 1.8142e-05 | 1.0807e-05 | 0.027575 | 0.027574 | 0.027575 | 0.98061 | -0.37369 | 0.98168 | -0.35277 | 7.5754
75 | -0.020467 | -0.0051397 | 0.020478 | 0.0051461 | 1.0641e-05 | 6.4375e-06 | 0.031028 | 0.031028 | 0.031028 | 0.98168 | -0.35277 | 0.98224 | -0.34188 | 8.5241
76 | -0.0020526 | -0.00051443 | 0.0020528 | 0.00051376 | 2.3481e-07 | -6.6915e-07 | 0.0031099 | 0.0031096 | 0.0031099 | 0.98211 | -0.3444 | 0.98223 | -0.342 | 0.85438
77 | -0.0020528 | -0.00051376 | 0.0020528 | 0.00051373 | 1.222e-08 | -3.4834e-08 | 0.0031096 | 0.0031096 | 0.0031096 | 0.98223 | -0.342 | 0.98224 | -0.34188 | 0.8543
78 | 0.033051 | 0.0083117 | -0.033021 | -0.0082925 | 3.0721e-05 | 1.9241e-05 | 0.049865 | 0.049865 | 0.049865 | 0.98649 | -0.25927 | 0.98548 | -0.27875 | 13.6992
79 | -0.035542 | -0.0089359 | 0.035569 | 0.0089532 | 2.7656e-05 | 1.7372e-05 | 0.053621 | 0.053621 | 0.053621 | 0.98649 | -0.25927 | 0.98732 | -0.24299 | 14.7312
80 | 0.027496 | 0.0069078 | -0.027483 | -0.0068996 | 1.3248e-05 | 8.2177e-06 | 0.041523 | 0.041523 | 0.041523 | 0.98548 | -0.27875 | 0.98497 | -0.28885 | 11.4075
81 | -0.037142 | -0.0093473 | 0.037159 | 0.0093579 | 1.6842e-05 | 1.0595e-05 | 0.055991 | 0.055991 | 0.055991 | 0.98732 | -0.24299 | 0.98781 | -0.23351 | 15.3822
82 | 0.022929 | 0.0057583 | -0.022929 | -0.0057583 | 7.0848e-08 | 4.3339e-08 | 0.034644 | 0.034644 | 0.034644 | 0.98497 | -0.28885 | 0.98496 | -0.28892 | 9.5175
83 | 0.067961 | 0.017151 | -0.067902 | -0.017113 | 5.9415e-05 | 3.7833e-05 | 0.10242 | 0.10242 | 0.10242 | 0.98781 | -0.23351 | 0.98687 | -0.25178 | 28.1366
84 | -0.10512 | -0.026509 | 0.10517 | 0.026539 | 4.7295e-05 | 3.0204e-05 | 0.15841 | 0.15841 | 0.15841 | 0.98781 | -0.23351 | 0.9883 | -0.22411 | 43.5187
85 | 0.01972 | 0.004954 | -0.019705 | -0.004945 | 1.4868e-05 | 8.9478e-06 | 0.029795 | 0.029795 | 0.029795 | 0.98496 | -0.28892 | 0.98415 | -0.30473 | 8.1856
86 | 0.0038601 | 0.00096731 | -0.0038599 | -0.00096738 | 2.0236e-07 | -7.4009e-08 | 0.0058203 | 0.0058203 | 0.0058203 | 0.98687 | -0.25178 | 0.98681 | -0.25288 | 1.599
87 | 0.05628 | 0.014201 | -0.056208 | -0.014154 | 7.2699e-05 | 4.6184e-05 | 0.084894 | 0.084894 | 0.084894 | 0.98687 | -0.25178 | 0.98548 | -0.27879 | 23.3226
88 | 0.0077612 | 0.0019455 | -0.0077585 | -0.0019445 | 2.6919e-06 | 1.0534e-06 | 0.011703 | 0.011703 | 0.011703 | 0.98687 | -0.25178 | 0.9865 | -0.25906 | 3.2151
89 | -0.10784 | -0.027209 | 0.10809 | 0.02737 | 0.00025123 | 0.00016046 | 0.16243 | 0.16243 | 0.16243 | 0.9883 | -0.22411 | 0.99081 | -0.17559 | 44.6245
90 | 0.017332 | 0.0043502 | -0.017324 | -0.0043457 | 7.7484e-06 | 4.5769e-06 | 0.026207 | 0.026207 | 0.026207 | 0.98415 | -0.30473 | 0.98367 | -0.31411 | 7.1998
91 | 0.0075667 | 0.0018965 | -0.0075661 | -0.0018963 | 5.4097e-07 | 2.0543e-07 | 0.011425 | 0.011425 | 0.011425 | 0.98548 | -0.27879 | 0.9854 | -0.28029 | 3.1388
92 | 0.048641 | 0.012258 | -0.04856 | -0.012206 | 8.1199e-05 | 5.1457e-05 | 0.073469 | 0.073469 | 0.073469 | 0.98548 | -0.27879 | 0.98368 | -0.31375 | 20.1839
93 | 0.0039 | 0.00097742 | -0.0039 | -0.00097742 | 6.3625e-09 | -2.1877e-09 | 0.0058826 | 0.0058826 | 0.0058826 | 0.9865 | -0.25906 | 0.98649 | -0.2591 | 1.6161
94 | 0.0069592 | 0.0017443 | -0.0069576 | -0.0017437 | 1.6084e-06 | 5.382e-07 | 0.010527 | 0.010527 | 0.010527 | 0.98368 | -0.31375 | 0.98343 | -0.3186 | 2.8921
95 | 0.0416 | 0.010462 | -0.041545 | -0.010427 | 5.5805e-05 | 3.5239e-05 | 0.062942 | 0.062942 | 0.062942 | 0.98368 | -0.31375 | 0.98224 | -0.34188 | 17.2918
96 | -0.11127 | -0.028168 | 0.11159 | 0.028368 | 0.00031331 | 0.00020013 | 0.16721 | 0.16721 | 0.16721 | 0.99081 | -0.17559 | 0.99386 | -0.11711 | 45.9379
97 | 0.019014 | 0.0047671 | -0.019012 | -0.0047658 | 2.0103e-06 | 1.2048e-06 | 0.028805 | 0.028805 | 0.028805 | 0.98224 | -0.34188 | 0.98213 | -0.3441 | 7.9134
98 | 0.0053825 | 0.001349 | -0.0053822 | -0.0013489 | 3.1748e-07 | 4.2105e-08 | 0.008155 | 0.0081551 | 0.0081551 | 0.98213 | -0.3441 | 0.98206 | -0.34533 | 2.2404
99 | 0.013629 | 0.0034169 | -0.013626 | -0.0034149 | 3.5052e-06 | 1.966e-06 | 0.02065 | 0.02065 | 0.02065 | 0.98213 | -0.3441 | 0.98185 | -0.34949 | 5.6731
100 | 0.0068513 | 0.0017172 | -0.0068506 | -0.0017169 | 7.2358e-07 | 2.3677e-07 | 0.010383 | 0.010383 | 0.010383 | 0.98185 | -0.34949 | 0.98174 | -0.35171 | 2.8526
101 | 0.0067744 | 0.0016978 | -0.0067741 | -0.0016977 | 2.719e-07 | 8.702e-08 | 0.010267 | 0.010267 | 0.010267 | 0.98185 | -0.34949 | 0.98181 | -0.35034 | 2.8205
102 | 0.016165 | 0.004048 | -0.01616 | -0.0040456 | 4.1018e-06 | 2.3893e-06 | 0.024355 | 0.024355 | 0.024355 | 0.98757 | -0.23908 | 0.9873 | -0.24441 | 6.6909
103 | -0.014029 | -0.0035113 | 0.014029 | 0.0035115 | 2.0738e-07 | 1.169e-07 | 0.021142 | 0.021142 | 0.021142 | 0.98728 | -0.24473 | 0.9873 | -0.24441 | 5.8084
104 | 0.012953 | 0.0032418 | -0.01295 | -0.00324 | 3.2075e-06 | 1.7658e-06 | 0.019521 | 0.019521 | 0.019521 | 0.98728 | -0.24473 | 0.98702 | -0.24993 | 5.363
105 | 0.011862 | 0.0029674 | -0.011862 | -0.0029672 | 3.7791e-07 | 2.0158e-07 | 0.017882 | 0.017882 | 0.017882 | 0.98702 | -0.24993 | 0.98698 | -0.2506 | 4.9125
106 | 0.0093961 | 0.0023492 | -0.0093905 | -0.0023466 | 5.5801e-06 | 2.624e-06 | 0.014164 | 0.014164 | 0.014164 | 0.98698 | -0.2506 | 0.98634 | -0.26309 | 3.8913
107 | 0.13188 | 0.033494 | -0.13185 | -0.033475 | 2.8785e-05 | 1.8397e-05 | 0.19742 | 0.19742 | 0.19742 | 0.99481 | -0.09893 | 0.99457 | -0.10347 | 54.2361
108 | 0.1143 | 0.029077 | -0.11423 | -0.029029 | 7.5115e-05 | 4.7985e-05 | 0.17117 | 0.17117 | 0.17117 | 0.99457 | -0.10347 | 0.99386 | -0.11711 | 47.0235
109 | -0.0044836 | -0.0011237 | 0.0044839 | 0.0011237 | 2.6809e-07 | -3.6449e-08 | 0.0066932 | 0.0066932 | 0.0066932 | 0.99678 | -0.06164 | 0.99684 | -0.060385 | 1.8388
110 | 0.0038328 | 0.00096054 | -0.0038328 | -0.00096058 | 8.7548e-08 | -3.6944e-08 | 0.0057214 | 0.0057214 | 0.0057214 | 0.99684 | -0.060385 | 0.99682 | -0.060864 | 1.5718
111 | -0.0083167 | -0.0020842 | 0.0083176 | 0.0020846 | 8.41e-07 | 3.4852e-07 | 0.012415 | 0.012414 | 0.012415 | 0.99684 | -0.060385 | 0.99695 | -0.058262 | 3.4106
112 | -0.013011 | -0.0032609 | 0.013016 | 0.0032636 | 4.9141e-06 | 2.6917e-06 | 0.01942 | 0.01942 | 0.01942 | 0.99695 | -0.058262 | 0.99736 | -0.050337 | 5.3352
113 | 0.0034137 | 0.000855 | -0.0034135 | -0.00085516 | 2.2608e-07 | -1.5862e-07 | 0.0050929 | 0.005093 | 0.005093 | 0.99736 | -0.050337 | 0.99729 | -0.051728 | 1.3992
114 | -0.01643 | -0.0041186 | 0.016436 | 0.004122 | 5.8614e-06 | 3.4117e-06 | 0.024513 | 0.024513 | 0.024513 | 0.99736 | -0.050337 | 0.99775 | -0.042853 | 6.7343
115 | 0.0034135 | 0.00085516 | -0.0034131 | -0.00085541 | 3.5341e-07 | -2.4783e-07 | 0.005093 | 0.0050932 | 0.0050932 | 0.99729 | -0.051728 | 0.99718 | -0.053902 | 1.3992
116 | 0.032514 | 0.0081576 | -0.0325 | -0.008149 | 1.3783e-05 | 8.6174e-06 | 0.048494 | 0.048494 | 0.048494 | 0.99775 | -0.042853 | 0.99729 | -0.051748 | 13.3225
117 | 0.0010519 | 0.00026364 | -0.0010519 | -0.00026364 | 9.6402e-11 | -1.224e-09 | 0.0015867 | 0.0015867 | 0.0015867 | 0.98649 | -0.2591 | 0.98649 | -0.2591 | 0.43592
118 | -0.0050478 | -0.001265 | 0.0050485 | 0.001265 | 6.9258e-07 | 2.0023e-08 | 0.0075391 | 0.0075389 | 0.0075391 | 0.99631 | -0.070738 | 0.99646 | -0.067857 | 2.0712
119 | 0.0050478 | 0.001265 | -0.0050474 | -0.001265 | 3.8012e-07 | 1.1051e-08 | 0.0075391 | 0.0075391 | 0.0075391 | 0.99631 | -0.070738 | 0.99622 | -0.072318 | 2.0712
120 | 0.0061465 | 0.0015404 | -0.006146 | -0.0015403 | 4.4991e-07 | 1.0245e-07 | 0.0091786 | 0.0091786 | 0.0091786 | 0.99646 | -0.067857 | 0.99638 | -0.069394 | 2.5216
121 | -0.011195 | -0.0028055 | 0.011199 | 0.0028074 | 3.8196e-06 | 1.9696e-06 | 0.016717 | 0.016717 | 0.016717 | 0.99646 | -0.067857 | 0.99683 | -0.060697 | 4.5927
122 | 0.0060004 | 0.0015038 | -0.0060002 | -0.0015038 | 2.3949e-07 | 4.943e-08 | 0.0089554 | 0.0089555 | 0.0089555 | 0.99702 | -0.057034 | 0.99697 | -0.057872 | 2.4603
123 | 0.016273 | 0.0040801 | -0.01627 | -0.0040784 | 2.84e-06 | 1.6502e-06 | 0.024288 | 0.024288 | 0.024288 | 0.99702 | -0.057034 | 0.99683 | -0.060697 | 6.6725
124 | -0.022274 | -0.0055839 | 0.022279 | 0.0055873 | 5.6119e-06 | 3.4149e-06 | 0.033243 | 0.033243 | 0.033243 | 0.99702 | -0.057034 | 0.99729 | -0.051748 | 9.1327
125 | 0.0050715 | 0.001271 | -0.0050712 | -0.001271 | 3.5301e-07 | 1.1825e-08 | 0.0075705 | 0.0075706 | 0.0075706 | 0.99683 | -0.060697 | 0.99675 | -0.062158 | 2.0798
126 | 0.084918 | 0.021505 | -0.084714 | -0.021375 | 0.00020427 | 0.0001303 | 0.12743 | 0.12743 | 0.12743 | 0.99222 | -0.14856 | 0.98962 | -0.19878 | 35.0082
127 | -0.087643 | -0.022188 | 0.087865 | 0.022329 | 0.00022143 | 0.00014127 | 0.13152 | 0.13152 | 0.13152 | 0.99222 | -0.14856 | 0.99496 | -0.096076 | 36.1307
128 | -0.0018631 | -0.00046693 | 0.0018631 | 0.00046665 | 7.6343e-08 | -2.7491e-07 | 0.0028218 | 0.0028217 | 0.0028218 | 0.98244 | -0.33813 | 0.98249 | -0.33727 | 0.77522
129 | -0.0047014 | -0.001178 | 0.004702 | 0.001178 | 6.4919e-07 | -1.701e-08 | 0.0071203 | 0.0071202 | 0.0071203 | 0.98249 | -0.33727 | 0.98263 | -0.33437 | 1.9561
130 | -0.0072232 | -0.0018098 | 0.0072238 | 0.0018101 | 6.4599e-07 | 2.3102e-07 | 0.010938 | 0.010938 | 0.010938 | 0.98263 | -0.33437 | 0.98273 | -0.33249 | 3.0049
131 | -0.0053764 | -0.0013474 | 0.0053775 | 0.0013476 | 1.1422e-06 | 1.526e-07 | 0.008155 | 0.0081548 | 0.008155 | 0.98101 | -0.36633 | 0.98123 | -0.36187 | 2.2404
132 | -0.0086442 | -0.0021659 | 0.0086473 | 0.0021672 | 3.0583e-06 | 1.3576e-06 | 0.013109 | 0.013108 | 0.013109 | 0.98123 | -0.36187 | 0.98161 | -0.35444 | 3.6012
133 | 0.0032667 | 0.00081828 | -0.0032665 | -0.00081845 | 2.3678e-07 | -1.7344e-07 | 0.0049538 | 0.0049539 | 0.0049539 | 0.98123 | -0.36187 | 0.98116 | -0.36339 | 1.361
134 | 0.0033031 | 0.00082758 | -0.0033029 | -0.00082778 | 2.767e-07 | -1.9491e-07 | 0.0050071 | 0.0050072 | 0.0050072 | 0.98161 | -0.35444 | 0.98152 | -0.3562 | 1.3756
135 | 0.0016577 | 0.00041525 | -0.0016577 | -0.00041545 | 4.2179e-08 | -1.9776e-07 | 0.002514 | 0.0025141 | 0.0025141 | 0.98116 | -0.36339 | 0.98113 | -0.36392 | 0.69067
136 | -0.0083725 | -0.0020979 | 0.0083738 | 0.0020985 | 1.3794e-06 | 5.9297e-07 | 0.012679 | 0.012679 | 0.012679 | 0.98255 | -0.33595 | 0.98273 | -0.33249 | 3.4834
137 | 0.0066514 | 0.0016666 | -0.0066502 | -0.0016662 | 1.1154e-06 | 3.4265e-07 | 0.010073 | 0.010073 | 0.010073 | 0.98255 | -0.33595 | 0.98237 | -0.33947 | 2.7673
138 | -0.015598 | -0.0039086 | 0.015611 | 0.0039165 | 1.367e-05 | 7.9201e-06 | 0.023617 | 0.023617 | 0.023617 | 0.98273 | -0.33249 | 0.98367 | -0.31411 | 6.4883
139 | 0.0028643 | 0.00071745 | -0.002864 | -0.00071778 | 2.8262e-07 | -3.2601e-07 | 0.0043384 | 0.0043386 | 0.0043386 | 0.98237 | -0.33947 | 0.98227 | -0.34154 | 1.1919
140 | 0.003786 | 0.00094876 | -0.0037858 | -0.00094882 | 1.456e-07 | -5.6289e-08 | 0.0057347 | 0.0057347 | 0.0057347 | 0.98237 | -0.33947 | 0.98233 | -0.34028 | 1.5755
141 | 0.0035791 | 0.00089696 | -0.0035791 | -0.000897 | 8.2333e-08 | -4.1665e-08 | 0.0054245 | 0.0054245 | 0.0054245 | 0.98181 | -0.35034 | 0.98178 | -0.35082 | 1.4903

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47373 | 0.12005

## res_load
| p_mw | q_mvar
0 | 0.0011061 | 0.00027722
1 | 0.0030797 | 0.00077183
2 | 0.0059035 | 0.0014796
3 | 0.01128 | 0.0028271
4 | 0.016022 | 0.0040155
5 | 0.013536 | 0.0033925
6 | 0.0030841 | 0.00077295
7 | 0.0013172 | 0.00033012
8 | 0.0066853 | 0.0016755
9 | 0.0012929 | 0.00032404
10 | 0.0027295 | 0.00068408
11 | 0.005179 | 0.001298
12 | 0.0047493 | 0.0011903
13 | 0.0033364 | 0.00083619
14 | 0.0034944 | 0.00087577
15 | 0.0040074 | 0.0010044
16 | 0.0094877 | 0.0023778
17 | 0.015513 | 0.003888
18 | 0.0050221 | 0.0012587
19 | 0.0016949 | 0.00042478
20 | 0.0078906 | 0.0019776
21 | 0.0043817 | 0.0010982
22 | 0.0035323 | 0.00088528
23 | 0.0033451 | 0.00083836
24 | 0.0034962 | 0.00087622
25 | 0.0022945 | 0.00057507
26 | 0.0045203 | 0.0011329
27 | 0.0095743 | 0.0023996
28 | 0.0039377 | 0.00098688
29 | 0.00099727 | 0.00024994
30 | 0.0025987 | 0.0006513
31 | 0.0027581 | 0.00069125
32 | 0.0045203 | 0.0011329
33 | 0.0096621 | 0.0024215
34 | 0.0071263 | 0.001786
35 | 0.0071263 | 0.001786
36 | 0.0035407 | 0.00088739
37 | 0.018359 | 0.0046012
38 | 0.014162 | 0.0035493
39 | 0.0036453 | 0.00091359
40 | 0.0081619 | 0.0020456
41 | 0.0035354 | 0.00088604
42 | 0.0023851 | 0.00059777
43 | 0.004075 | 0.0010213
44 | 0.0022784 | 0.00057102
45 | 0.0020526 | 0.00051443
46 | 0.0024904 | 0.00062414
47 | 0.0055248 | 0.0013846
48 | 0.0015724 | 0.00039407
49 | 0.0045538 | 0.0011413
50 | 0.0032093 | 0.00080433
51 | 0.0026735 | 0.00067004
52 | 0.0023731 | 0.00059476
53 | 0.0038599 | 0.00096738
54 | 0.0038586 | 0.00096705
55 | 0.0075661 | 0.0018963
56 | 0.0031833 | 0.00079781
57 | 0.0069576 | 0.0017437
58 | 0.0053822 | 0.0013489
59 | 0.0010757 | 0.00026959
60 | 0.0021314 | 0.00053418
61 | 0.0010876 | 0.00027259
62 | 0.0024658 | 0.000618
63 | 0.0011793 | 0.00029557
64 | 0.002572 | 0.0006446
65 | 0.017548 | 0.004398
66 | 0.0026394 | 0.00066149
67 | 0.0044836 | 0.0011237
68 | 0.0038328 | 0.00096058
69 | 0.0046938 | 0.0011764
70 | 0.002848 | 0.00071378
71 | 0.0050474 | 0.001265
72 | 0.0060002 | 0.0015038
73 | 0.010221 | 0.0025617
74 | 0.0050712 | 0.001271
75 | 0.006146 | 0.0015403
76 | 0.0027246 | 0.00068286
77 | 0.0053206 | 0.0013335
78 | 0.0097273 | 0.0024379
79 | 0.011661 | 0.0029226
80 | 0.0018631 | 0.00046693
81 | 0.0028382 | 0.00071133
82 | 0.0025212 | 0.00063186
83 | 0.0053764 | 0.0013474
84 | 0.0016088 | 0.0004032
85 | 0.0033029 | 0.00082778
86 | 0.0016577 | 0.00041545
87 | 0.0010519 | 0.00026364
88 | 0.0034131 | 0.00085541
89 | 0.0017211 | 0.00043135
90 | 0.0017125 | 0.00042918
91 | 0.002864 | 0.00071778
92 | 0.0037858 | 0.00094882
93 | 0.003195 | 0.00080073
94 | 0.0035791 | 0.000897
95 | 0.0068506 | 0.0017169

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1