## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1201-16_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1201-16_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1201-16_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1201-16_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1201-16_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1201-16_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1201-16_0_6_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1201-16_0_6_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1201-16_0_6_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1201-16_0_6_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_1201-16_0_6_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1201-16_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1201-16_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1201-16_0_6_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_1201-16_0_6_node_47 | 0.4 | n |  | TRUE
15 | bus_LV_1201-16_0_6_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_1201-16_0_6_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1201-16_0_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1201-16_0_6_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1201-16_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1201-16_0_6_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1201-16_0_6_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1201-16_0_6_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_1201-16_0_6_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1201-16_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1201-16_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1201-16_0_6_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1201-16_0_6_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_1201-16_0_6_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1201-16_0_6_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_1201-16_0_6_node_41 | 0.4 | n |  | TRUE
31 | bus_LV_1201-16_0_6_node_46 | 0.4 | n |  | TRUE
32 | bus_LV_1201-16_0_6_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_1201-16_0_6_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1201-16_0_6_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_1201-16_0_6_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_1201-16_0_6_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1201-16_0_6_node_44 | 0.4 | n |  | TRUE
38 | bus_LV_1201-16_0_6_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1201-16_0_6_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_1201-16_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1201-16_0_6_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_1201-16_0_6_node_45 | 0.4 | n |  | TRUE
43 | bus_MV_14_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1201-16_0_6_load_0 | 0 | 0.0087084 | 0.0021825 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1201-16_0_6_load_4 | 3 | 0.010106 | 0.0025329 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1201-16_0_6_load_5 | 4 | 0.011392 | 0.0028551 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1201-16_0_6_load_26 | 7 | 0.017803 | 0.0044619 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1201-16_0_6_load_25 | 8 | 0.009377 | 0.0023501 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1201-16_0_6_load_33 | 9 | 0.02063 | 0.0051703 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1201-16_0_6_load_27 | 10 | 0.0095137 | 0.0023844 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1201-16_0_6_load_28 | 13 | 0.062058 | 0.015553 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1201-16_0_6_load_47 | 14 | 0.015353 | 0.0038478 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1201-16_0_6_load_11 | 17 | 0.028762 | 0.0072083 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1201-16_0_6_load_9 | 18 | 0.024437 | 0.0061244 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1201-16_0_6_load_24 | 20 | 0.0046189 | 0.0011576 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1201-16_0_6_load_40 | 22 | 0.011018 | 0.0027615 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1201-16_0_6_load_37 | 23 | 0.042449 | 0.010639 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1201-16_0_6_load_29 | 26 | 0.035222 | 0.0088275 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1201-16_0_6_load_48 | 27 | 0.0092864 | 0.0023274 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1201-16_0_6_load_41 | 30 | 0.014302 | 0.0035845 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1201-16_0_6_load_46 | 31 | 0.0035725 | 0.00089535 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1201-16_0_6_load_42 | 32 | 0.064123 | 0.016071 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1201-16_0_6_load_34 | 33 | 0.06414 | 0.016075 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1201-16_0_6_load_35 | 34 | 0.011932 | 0.0029905 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1201-16_0_6_load_39 | 35 | 0.0099567 | 0.0024954 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1201-16_0_6_load_44 | 37 | 0.018979 | 0.0047565 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1201-16_0_6_load_30 | 39 | 0.0093573 | 0.0023452 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1201-16_0_6_load_31 | 40 | 0.0089718 | 0.0022485 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1201-16_0_6_load_43 | 41 | 0.061843 | 0.015499 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1201-16_0_6_load_45 | 42 | 0.02278 | 0.0057091 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1201-16_0_6_line_0 |  | 0 | 1 | 0.011959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1201-16_0_6_line_1 |  | 0 | 2 | 0.020641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1201-16_0_6_line_2 |  | 1 | 3 | 0.010486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1201-16_0_6_line_3 |  | 2 | 4 | 0.010125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1201-16_0_6_line_4 |  | 2 | 5 | 0.046893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1201-16_0_6_line_5 |  | 3 | 9 | 0.0034784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1201-16_0_6_line_6 |  | 4 | 10 | 0.023974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1201-16_0_6_line_7 |  | 5 | 14 | 0.055864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1201-16_0_6_line_8 |  | 6 | 7 | 0.0022593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1201-16_0_6_line_9 |  | 6 | 8 | 0.015345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1201-16_0_6_line_10 |  | 8 | 15 | 0.013639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1201-16_0_6_line_11 |  | 9 | 16 | 0.018437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1201-16_0_6_line_12 |  | 10 | 13 | 0.007624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1201-16_0_6_line_13 |  | 11 | 12 | 0.045117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1201-16_0_6_line_14 |  | 11 | 13 | 0.021884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1201-16_0_6_line_15 |  | 12 | 17 | 0.018775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1201-16_0_6_line_16 |  | 12 | 18 | 0.0088895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1201-16_0_6_line_17 |  | 15 | 16 | 0.022579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1201-16_0_6_line_18 |  | 17 | 19 | 0.025469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1201-16_0_6_line_19 |  | 19 | 20 | 0.0018435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1201-16_0_6_line_20 |  | 20 | 31 | 0.0019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1201-16_0_6_line_21 |  | 21 | 22 | 0.0087367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1201-16_0_6_line_22 |  | 21 | 23 | 0.018471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1201-16_0_6_line_23 |  | 22 | 37 | 0.017304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1201-16_0_6_line_24 |  | 23 | 29 | 0.011257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1201-16_0_6_line_25 |  | 24 | 25 | 0.03463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1201-16_0_6_line_26 |  | 24 | 26 | 0.018549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1201-16_0_6_line_27 |  | 25 | 27 | 0.016243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1201-16_0_6_line_28 |  | 26 | 39 | 0.006296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1201-16_0_6_line_29 |  | 27 | 38 | 0.013593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1201-16_0_6_line_30 |  | 28 | 29 | 0.032577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1201-16_0_6_line_31 |  | 28 | 30 | 0.027482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1201-16_0_6_line_32 |  | 29 | 35 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_1201-16_0_6_line_33 |  | 30 | 32 | 0.042766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1201-16_0_6_line_34 |  | 31 | 40 | 0.013114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1201-16_0_6_line_35 |  | 33 | 34 | 0.0052024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1201-16_0_6_line_36 |  | 34 | 36 | 0.025307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1201-16_0_6_line_37 |  | 35 | 36 | 0.018635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1201-16_0_6_line_38 |  | 36 | 38 | 0.007265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1201-16_0_6_line_39 |  | 37 | 41 | 0.0042267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1201-16_0_6_line_40 |  | 39 | 40 | 0.003036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1201-16_0_6_line_41 |  | 41 | 42 | 0.0072846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1201-16_0_6_trafo_30 | 0.63 MVA 20/0.4 kV | 43 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2691885.6952 | 1193050.2053 | 2691892.8638 | 1193059.7778
1 | 2691905.2366 | 1193076.2999 | 2691892.8638 | 1193059.7778
2 | 2691885.6952 | 1193050.2053 | 2691878.7293 | 1193042.3675
3 | 2691905.2366 | 1193076.2999 | 2691911.8385 | 1193069.8416 | 2691912.444 | 1193069.1901
4 | 2691905.2366 | 1193076.2999 | 2691917.3876 | 1193095.1765 | 2691899.9418 | 1193112.2973
5 | 2691878.7293 | 1193042.3675 | 2691876.4186 | 1193039.7675
6 | 2691912.444 | 1193069.1901 | 2691928.7636 | 1193051.6286
7 | 2691899.9418 | 1193112.2973 | 2691895.502 | 1193105.0578 | 2691886.7299 | 1193091.0252 | 2691871.2102 | 1193070.1068 | 2691867.6541 | 1193066.9185
8 | 2691904.701 | 1193030.7958 | 2691906.7045 | 1193031.8401
9 | 2691904.701 | 1193030.7958 | 2691892.7173 | 1193021.2117
10 | 2691884.1499 | 1193010.8674 | 2691888.2162 | 1193017.6119 | 2691892.7173 | 1193021.2117
11 | 2691866.2663 | 1193024.7128 | 2691868.7144 | 1193031.099 | 2691876.4186 | 1193039.7675
12 | 2691933.9534 | 1193046.0438 | 2691928.7636 | 1193051.6286
13 | 2691951.6228 | 1193059.0236 | 2691959.836 | 1193053.3795 | 2691965.6338 | 1193038.2367 | 2691981.0808 | 1193027.1892
14 | 2691951.6228 | 1193059.0236 | 2691933.9534 | 1193046.0438
15 | 2691981.0808 | 1193027.1892 | 2691969.5625 | 1193012.3623
16 | 2691981.0808 | 1193027.1892 | 2691986.6459 | 1193034.1212
17 | 2691884.1499 | 1193010.8674 | 2691866.2663 | 1193024.7128
18 | 2691953.9378 | 1192992.2496 | 2691969.5625 | 1193012.3623
19 | 2691953.9378 | 1192992.2496 | 2691952.7711 | 1192990.8223
20 | 2691952.7711 | 1192990.8223 | 2691951.5181 | 1192989.2896
21 | 2692006.5565 | 1192881.098 | 2691999.0695 | 1192876.5952
22 | 2692006.5565 | 1192881.098 | 2691990.1826 | 1192889.6472
23 | 2691984.2404 | 1192867.6768 | 2691999.0695 | 1192876.5952
24 | 2691980.204 | 1192894.8573 | 2691990.1826 | 1192889.6472
25 | 2691926.2115 | 1192957.0565 | 2691938.5609 | 1192950.1418 | 2691942.477 | 1192945.8325 | 2691933.2755 | 1192934.4283
26 | 2691926.2115 | 1192957.0565 | 2691935.0592 | 1192969.1558 | 2691937.3121 | 1192971.9117
27 | 2691944.4751 | 1192922.9708 | 2691940.1961 | 1192928.5753 | 2691937.8546 | 1192931.6191 | 2691933.2755 | 1192934.4283
28 | 2691941.2969 | 1192976.7862 | 2691937.3121 | 1192971.9117
29 | 2691955.7548 | 1192930.6046 | 2691944.4751 | 1192922.9708
30 | 2691954.1441 | 1192875.2109 | 2691980.204 | 1192894.8573
31 | 2691954.1441 | 1192875.2109 | 2691952.1147 | 1192880.2718 | 2691954.2817 | 1192884.6079 | 2691961.4797 | 1192890.9559 | 2691967.38 | 1192895.7215
32 | 2691968.3597 | 1192908.0727 | 2691980.204 | 1192894.8573
33 | 2691967.38 | 1192895.7215 | 2692000.6491 | 1192922.5926
34 | 2691943.2184 | 1192979.1368 | 2691951.5181 | 1192989.2896
35 | 2691980.1833 | 1192940.247 | 2691984.3044 | 1192943.4221
36 | 2691960.136 | 1192924.8015 | 2691980.1833 | 1192940.247
37 | 2691968.3597 | 1192908.0727 | 2691960.136 | 1192924.8015
38 | 2691955.7548 | 1192930.6046 | 2691960.136 | 1192924.8015
39 | 2691980.6183 | 1192865.4985 | 2691984.2404 | 1192867.6768
40 | 2691943.2184 | 1192979.1368 | 2691941.2969 | 1192976.7862
41 | 2691980.6183 | 1192865.4985 | 2691974.3757 | 1192861.7441

## bus_geodata
| x | y | coords
0 | 2691892.8638 | 1193059.7778
1 | 2691885.6952 | 1193050.2053
2 | 2691905.2366 | 1193076.2999
3 | 2691878.7293 | 1193042.3675
4 | 2691912.444 | 1193069.1901
5 | 2691899.9418 | 1193112.2973
6 | 2691904.701 | 1193030.7958
7 | 2691906.7044 | 1193031.8401
8 | 2691892.7173 | 1193021.2117
9 | 2691876.4186 | 1193039.7675
10 | 2691928.7636 | 1193051.6286
11 | 2691951.6228 | 1193059.0236
12 | 2691981.0808 | 1193027.1892
13 | 2691933.9534 | 1193046.0438
14 | 2691867.6541 | 1193066.9185
15 | 2691884.1499 | 1193010.8674
16 | 2691866.2663 | 1193024.7128
17 | 2691969.5625 | 1193012.3623
18 | 2691986.6459 | 1193034.1212
19 | 2691953.9378 | 1192992.2496
20 | 2691952.7711 | 1192990.8223
21 | 2692006.5565 | 1192881.098
22 | 2691999.0695 | 1192876.5952
23 | 2691990.1826 | 1192889.6472
24 | 2691926.2115 | 1192957.0565
25 | 2691933.2755 | 1192934.4283
26 | 2691937.3121 | 1192971.9117
27 | 2691944.4751 | 1192922.9708
28 | 2691954.1441 | 1192875.2109
29 | 2691980.204 | 1192894.8573
30 | 2691967.38 | 1192895.7215
31 | 2691951.5181 | 1192989.2896
32 | 2692000.6491 | 1192922.5926
33 | 2691984.3044 | 1192943.4221
34 | 2691980.1833 | 1192940.247
35 | 2691968.3597 | 1192908.0727
36 | 2691960.136 | 1192924.8015
37 | 2691984.2404 | 1192867.6768
38 | 2691955.7548 | 1192930.6046
39 | 2691941.2969 | 1192976.7862
40 | 2691943.2184 | 1192979.1368
41 | 2691980.6183 | 1192865.4985
42 | 2691974.3757 | 1192861.7441
43 | 2691953.9378 | 1192992.2496

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98709 | -0.24826 | 0.0087084 | 0.0021825
1 | 0.98646 | -0.26066 | 0 | 0
2 | 0.98836 | -0.22369 | 0 | 0
3 | 0.9859 | -0.27154 | 0.010106 | 0.0025329
4 | 0.98912 | -0.20889 | 0.011392 | 0.0028551
5 | 0.9877 | -0.23655 | 0 | 0
6 | 0.98412 | -0.30612 | 0 | 0
7 | 0.98409 | -0.30685 | 0.017803 | 0.0044619
8 | 0.98438 | -0.30121 | 0.009377 | 0.0023501
9 | 0.98574 | -0.27452 | 0.02063 | 0.0051703
10 | 0.99118 | -0.16909 | 0.0095137 | 0.0023844
11 | 0.99356 | -0.12327 | 0 | 0
12 | 0.99584 | -0.079565 | 0 | 0
13 | 0.9919 | -0.15519 | 0.062058 | 0.015553
14 | 0.98691 | -0.25188 | 0.015353 | 0.0038478
15 | 0.98472 | -0.29454 | 0 | 0
16 | 0.98528 | -0.28352 | 0 | 0
17 | 0.99692 | -0.058756 | 0.028762 | 0.0072083
18 | 0.99564 | -0.083384 | 0.024437 | 0.0061244
19 | 0.99862 | -0.026331 | 0 | 0
20 | 0.99874 | -0.023988 | 0.0046189 | 0.0011576
21 | 0.98406 | -0.30592 | 0 | 0
22 | 0.98313 | -0.32396 | 0.011018 | 0.0027615
23 | 0.98601 | -0.26789 | 0.042449 | 0.010639
24 | 0.9974 | -0.049168 | 0 | 0
25 | 0.99388 | -0.11631 | 0 | 0
26 | 0.99929 | -0.013399 | 0.035222 | 0.0088275
27 | 0.99223 | -0.14797 | 0.0092864 | 0.0023274
28 | 0.98447 | -0.29789 | 0 | 0
29 | 0.98683 | -0.25206 | 0 | 0
30 | 0.98247 | -0.33673 | 0.014302 | 0.0035845
31 | 0.99888 | -0.02142 | 0.0035725 | 0.00089535
32 | 0.97993 | -0.38638 | 0.064123 | 0.016071
33 | 0.98809 | -0.22787 | 0.06414 | 0.016075
34 | 0.9884 | -0.22191 | 0.011932 | 0.0029905
35 | 0.98876 | -0.21477 | 0.0099567 | 0.0024954
36 | 0.99017 | -0.18763 | 0 | 0
37 | 0.98148 | -0.35635 | 0.018979 | 0.0047565
38 | 0.99088 | -0.1738 | 0 | 0
39 | 1 | 0 | -0.60993 | -0.15514
40 | 0.99978 | -0.0041517 | 0.0089718 | 0.0022485
41 | 0.98114 | -0.36282 | 0.061843 | 0.015499
42 | 0.98099 | -0.36583 | 0.02278 | 0.0057091
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.058027 | 0.014585 | -0.057993 | -0.014563 | 3.4327e-05 | 2.1817e-05 | 0.087489 | 0.087489 | 0.087489 | 0.98709 | -0.24826 | 0.98646 | -0.26066 | 24.0354
1 | -0.066735 | -0.016767 | 0.066814 | 0.016817 | 7.8363e-05 | 4.9888e-05 | 0.10062 | 0.10062 | 0.10062 | 0.98709 | -0.24826 | 0.98836 | -0.22369 | 27.6419
2 | 0.057993 | 0.014563 | -0.057963 | -0.014544 | 3.0099e-05 | 1.9129e-05 | 0.087489 | 0.087489 | 0.087489 | 0.98646 | -0.26066 | 0.9859 | -0.27154 | 24.0354
3 | -0.082187 | -0.020677 | 0.082246 | 0.020714 | 5.8159e-05 | 3.7092e-05 | 0.12376 | 0.12376 | 0.12376 | 0.98836 | -0.22369 | 0.98912 | -0.20889 | 34.0013
4 | 0.015374 | 0.0038597 | -0.015364 | -0.0038543 | 9.4226e-06 | 5.4299e-06 | 0.023148 | 0.023148 | 0.023148 | 0.98836 | -0.22369 | 0.9877 | -0.23655 | 6.3594
5 | 0.047856 | 0.012011 | -0.047849 | -0.012007 | 6.8064e-06 | 4.3117e-06 | 0.072235 | 0.072235 | 0.072235 | 0.9859 | -0.27154 | 0.98574 | -0.27452 | 19.8449
6 | -0.093637 | -0.023569 | 0.093816 | 0.023683 | 0.00017848 | 0.00011392 | 0.1409 | 0.1409 | 0.1409 | 0.98912 | -0.20889 | 0.99118 | -0.16909 | 38.7094
7 | 0.015364 | 0.0038543 | -0.015353 | -0.0038478 | 1.1226e-05 | 6.47e-06 | 0.023148 | 0.023149 | 0.023149 | 0.9877 | -0.23655 | 0.98691 | -0.25188 | 6.3595
8 | 0.017804 | 0.0044623 | -0.017803 | -0.0044619 | 6.1399e-07 | 3.6425e-07 | 0.02692 | 0.02692 | 0.02692 | 0.98412 | -0.30612 | 0.98409 | -0.30685 | 7.3956
9 | -0.017804 | -0.0044623 | 0.017808 | 0.0044648 | 4.1701e-06 | 2.4738e-06 | 0.02692 | 0.02692 | 0.02692 | 0.98412 | -0.30612 | 0.98438 | -0.30121 | 7.3956
10 | -0.027185 | -0.0068149 | 0.027194 | 0.0068202 | 8.6374e-06 | 5.3545e-06 | 0.041095 | 0.041095 | 0.041095 | 0.98438 | -0.30121 | 0.98472 | -0.29454 | 11.2897
11 | 0.02722 | 0.0068363 | -0.027208 | -0.0068291 | 1.1676e-05 | 7.2374e-06 | 0.041094 | 0.041094 | 0.041094 | 0.98574 | -0.27452 | 0.98528 | -0.28352 | 11.2897
12 | -0.10333 | -0.026067 | 0.1034 | 0.026111 | 6.8851e-05 | 4.3966e-05 | 0.15518 | 0.15518 | 0.15518 | 0.99118 | -0.16909 | 0.9919 | -0.15519 | 42.6331
13 | -0.16571 | -0.041826 | 0.16606 | 0.042046 | 0.00034764 | 0.00022074 | 0.24828 | 0.24828 | 0.24828 | 0.99356 | -0.12327 | 0.99584 | -0.079565 | 22.7363
14 | 0.16571 | 0.041826 | -0.16546 | -0.041664 | 0.00025294 | 0.00016131 | 0.24828 | 0.24828 | 0.24828 | 0.99356 | -0.12327 | 0.9919 | -0.15519 | 34.1045
15 | -0.1905 | -0.048174 | 0.19069 | 0.048295 | 0.00019036 | 0.0001211 | 0.2848 | 0.2848 | 0.2848 | 0.99584 | -0.079565 | 0.99692 | -0.058756 | 26.0808
16 | 0.024441 | 0.0061272 | -0.024437 | -0.0061244 | 4.4464e-06 | 2.7301e-06 | 0.036522 | 0.036522 | 0.036522 | 0.99584 | -0.079565 | 0.99564 | -0.083384 | 10.0334
17 | -0.027194 | -0.0068202 | 0.027208 | 0.0068291 | 1.4299e-05 | 8.8639e-06 | 0.041095 | 0.041094 | 0.041095 | 0.98472 | -0.29454 | 0.98528 | -0.28352 | 11.2897
18 | -0.21945 | -0.055503 | 0.21979 | 0.055721 | 0.00034194 | 0.00021784 | 0.32773 | 0.32773 | 0.32773 | 0.99692 | -0.058756 | 0.99862 | -0.026331 | 30.012
19 | -0.21979 | -0.055721 | 0.21982 | 0.055737 | 2.4751e-05 | 1.5768e-05 | 0.32773 | 0.32773 | 0.32773 | 0.99862 | -0.026331 | 0.99874 | -0.023988 | 30.012
20 | -0.22444 | -0.056894 | 0.22446 | 0.056912 | 2.7708e-05 | 1.7655e-05 | 0.33461 | 0.33461 | 0.33461 | 0.99874 | -0.023988 | 0.99888 | -0.02142 | 30.6422
21 | 0.11491 | 0.02891 | -0.11481 | -0.028847 | 9.8958e-05 | 6.3223e-05 | 0.17379 | 0.17379 | 0.17379 | 0.98406 | -0.30592 | 0.98313 | -0.32396 | 47.7458
22 | -0.11491 | -0.02891 | 0.11512 | 0.029044 | 0.00020922 | 0.00013367 | 0.17379 | 0.17379 | 0.17379 | 0.98406 | -0.30592 | 0.98601 | -0.26789 | 47.7458
23 | 0.10379 | 0.026086 | -0.10363 | -0.025983 | 0.00016019 | 0.0001023 | 0.15712 | 0.15712 | 0.15712 | 0.98313 | -0.32396 | 0.98148 | -0.35635 | 43.1643
24 | -0.15757 | -0.039683 | 0.15769 | 0.039759 | 0.00011941 | 7.6136e-05 | 0.23786 | 0.23785 | 0.23786 | 0.98601 | -0.26789 | 0.98683 | -0.25206 | 32.6724
25 | 0.33499 | 0.08558 | -0.33391 | -0.084888 | 0.0010837 | 0.00069222 | 0.50035 | 0.50035 | 0.50035 | 0.9974 | -0.049168 | 0.99388 | -0.11631 | 45.8197
26 | -0.33499 | -0.08558 | 0.33557 | 0.085951 | 0.00058046 | 0.00037077 | 0.50035 | 0.50035 | 0.50035 | 0.9974 | -0.049168 | 0.99929 | -0.013399 | 45.8196
27 | 0.33391 | 0.084888 | -0.3334 | -0.084564 | 0.00050831 | 0.00032469 | 0.50035 | 0.50035 | 0.50035 | 0.99388 | -0.11631 | 0.99223 | -0.14797 | 45.8197
28 | -0.3708 | -0.094779 | 0.37104 | 0.094932 | 0.0002405 | 0.00015367 | 0.5528 | 0.5528 | 0.5528 | 0.99929 | -0.013399 | 1 | 0 | 50.6225
29 | 0.32412 | 0.082236 | -0.32371 | -0.081979 | 0.00040203 | 0.00025677 | 0.48642 | 0.48642 | 0.48642 | 0.99223 | -0.14797 | 0.99088 | -0.1738 | 44.5444
30 | -0.078724 | -0.019845 | 0.078897 | 0.019956 | 0.00017309 | 0.00011036 | 0.11903 | 0.11903 | 0.11903 | 0.98447 | -0.29789 | 0.98683 | -0.25206 | 32.701
31 | 0.078724 | 0.019845 | -0.078578 | -0.019752 | 0.00014602 | 9.3102e-05 | 0.11903 | 0.11903 | 0.11903 | 0.98447 | -0.29789 | 0.98247 | -0.33673 | 32.701
32 | -0.23658 | -0.059714 | 0.23701 | 0.059985 | 0.00042332 | 0.00027047 | 0.35689 | 0.35689 | 0.35689 | 0.98683 | -0.25206 | 0.98876 | -0.21477 | 49.0228
33 | 0.064275 | 0.016168 | -0.064123 | -0.016071 | 0.00015205 | 9.677e-05 | 0.09737 | 0.09737 | 0.09737 | 0.98247 | -0.33673 | 0.97993 | -0.38638 | 26.75
34 | -0.22804 | -0.057807 | 0.22823 | 0.057928 | 0.00018942 | 0.00012071 | 0.33993 | 0.33993 | 0.33993 | 0.99888 | -0.02142 | 0.99978 | -0.0041517 | 31.1295
35 | -0.06414 | -0.016075 | 0.064158 | 0.016087 | 1.8202e-05 | 1.1582e-05 | 0.096591 | 0.096591 | 0.096591 | 0.98809 | -0.22787 | 0.9884 | -0.22191 | 26.536
36 | -0.07609 | -0.019077 | 0.076215 | 0.019156 | 0.00012454 | 7.938e-05 | 0.11455 | 0.11455 | 0.11455 | 0.9884 | -0.22191 | 0.99017 | -0.18763 | 31.4711
37 | -0.24696 | -0.06248 | 0.24728 | 0.062686 | 0.00032212 | 0.00020544 | 0.37187 | 0.37187 | 0.37187 | 0.98876 | -0.21477 | 0.99017 | -0.18763 | 34.0541
38 | -0.3235 | -0.081842 | 0.32371 | 0.081979 | 0.00021487 | 0.00013724 | 0.48642 | 0.48642 | 0.48642 | 0.99017 | -0.18763 | 0.99088 | -0.1738 | 44.5444
39 | 0.084652 | 0.021227 | -0.084626 | -0.02121 | 2.6109e-05 | 1.6656e-05 | 0.12834 | 0.12834 | 0.12834 | 0.98148 | -0.35635 | 0.98114 | -0.36282 | 35.2595
40 | 0.23724 | 0.060207 | -0.2372 | -0.060177 | 4.7366e-05 | 3.0195e-05 | 0.35329 | 0.35329 | 0.35329 | 1 | 0 | 0.99978 | -0.0041517 | 32.3523
41 | 0.022783 | 0.0057111 | -0.02278 | -0.0057091 | 3.2614e-06 | 1.9953e-06 | 0.034553 | 0.034553 | 0.034553 | 0.98114 | -0.36282 | 0.98099 | -0.36583 | 9.4926

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61929 | 0.15748

## res_load
| p_mw | q_mvar
0 | 0.0087084 | 0.0021825
1 | 0.010106 | 0.0025329
2 | 0.011392 | 0.0028551
3 | 0.017803 | 0.0044619
4 | 0.009377 | 0.0023501
5 | 0.02063 | 0.0051703
6 | 0.0095137 | 0.0023844
7 | 0.062058 | 0.015553
8 | 0.015353 | 0.0038478
9 | 0.028762 | 0.0072083
10 | 0.024437 | 0.0061244
11 | 0.0046189 | 0.0011576
12 | 0.011018 | 0.0027615
13 | 0.042449 | 0.010639
14 | 0.035222 | 0.0088275
15 | 0.0092864 | 0.0023274
16 | 0.014302 | 0.0035845
17 | 0.0035725 | 0.00089535
18 | 0.064123 | 0.016071
19 | 0.06414 | 0.016075
20 | 0.011932 | 0.0029905
21 | 0.0099567 | 0.0024954
22 | 0.018979 | 0.0047565
23 | 0.0093573 | 0.0023452
24 | 0.0089718 | 0.0022485
25 | 0.061843 | 0.015499
26 | 0.02278 | 0.0057091

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1