## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1201-21_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1201-21_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1201-21_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1201-21_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1201-21_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1201-21_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1201-21_0_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1201-21_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1201-21_0_5_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_1201-21_0_5_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_1201-21_0_5_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1201-21_0_5_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1201-21_0_5_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_1201-21_0_5_node_37 | 0.4 | n |  | TRUE
14 | bus_LV_1201-21_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1201-21_0_5_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1201-21_0_5_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_1201-21_0_5_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_1201-21_0_5_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_1201-21_0_5_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1201-21_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1201-21_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1201-21_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1201-21_0_5_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_1201-21_0_5_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_1201-21_0_5_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_1201-21_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1201-21_0_5_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1201-21_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1201-21_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1201-21_0_5_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_1201-21_0_5_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1201-21_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1201-21_0_5_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1201-21_0_5_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1201-21_0_5_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1201-21_0_5_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_1201-21_0_5_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_1201-21_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1201-21_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1201-21_0_5_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_1201-21_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_1201-21_0_5_node_34 | 0.4 | n |  | TRUE
43 | bus_MV_14_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1201-21_0_5_load_0 | 0 | 0.029929 | 0.0075008 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1201-21_0_5_load_4 | 4 | 0.0071519 | 0.0017924 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1201-21_0_5_load_14 | 6 | 0.00099247 | 0.00024874 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1201-21_0_5_load_13 | 7 | 0.00054774 | 0.00013728 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1201-21_0_5_load_31 | 8 | 0.0067377 | 0.0016886 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1201-21_0_5_load_21 | 9 | 0.074812 | 0.01875 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1201-21_0_5_load_20 | 10 | 0.0071978 | 0.0018039 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1201-21_0_5_load_6 | 11 | 0.052215 | 0.013086 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1201-21_0_5_load_38 | 12 | 0.011575 | 0.0029009 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1201-21_0_5_load_37 | 13 | 0.00083285 | 0.00020873 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1201-21_0_5_load_12 | 14 | 0.0050445 | 0.0012643 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1201-21_0_5_load_29 | 15 | 0.0066575 | 0.0016685 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1201-21_0_5_load_39 | 16 | 0.00088496 | 0.00022179 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1201-21_0_5_load_7 | 18 | 0.0053771 | 0.0013476 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1201-21_0_5_load_8 | 19 | 0.0036332 | 0.00091056 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1201-21_0_5_load_9 | 20 | 0.0043387 | 0.0010874 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1201-21_0_5_load_10 | 21 | 0.0036322 | 0.00091031 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1201-21_0_5_load_11 | 22 | 0.0040736 | 0.0010209 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1201-21_0_5_load_45 | 24 | 0.0063893 | 0.0016013 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1201-21_0_5_load_35 | 25 | 0.013976 | 0.0035026 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1201-21_0_5_load_15 | 26 | 0.0092151 | 0.0023095 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1201-21_0_5_load_16 | 27 | 0.04321 | 0.01083 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1201-21_0_5_load_40 | 30 | 0.0001158 | 2.9021e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1201-21_0_5_load_22 | 32 | 0.0086233 | 0.0021612 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1201-21_0_5_load_23 | 33 | 0.00052815 | 0.00013237 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1201-21_0_5_load_24 | 34 | 0.00045329 | 0.0001136 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1201-21_0_5_load_41 | 35 | 0.080429 | 0.020158 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1201-21_0_5_load_42 | 36 | 0.016027 | 0.0040167 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1201-21_0_5_load_26 | 37 | 0.0065954 | 0.001653 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1201-21_0_5_load_27 | 38 | 0.0081635 | 0.002046 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1201-21_0_5_load_28 | 39 | 0.0079377 | 0.0019894 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1201-21_0_5_load_32 | 41 | 0.014768 | 0.0037012 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1201-21_0_5_load_34 | 42 | 0.014161 | 0.0035491 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1201-21_0_5_line_0 |  | 0 | 1 | 0.023786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1201-21_0_5_line_1 |  | 0 | 2 | 0.022918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1201-21_0_5_line_2 |  | 1 | 3 | 0.040956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1201-21_0_5_line_3 |  | 1 | 4 | 0.022222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1201-21_0_5_line_4 |  | 2 | 5 | 0.031923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1201-21_0_5_line_5 |  | 3 | 6 | 0.029659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1201-21_0_5_line_6 |  | 3 | 7 | 0.052446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1201-21_0_5_line_7 |  | 4 | 8 | 0.018246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1201-21_0_5_line_8 |  | 5 | 9 | 0.018308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1201-21_0_5_line_9 |  | 5 | 10 | 0.037199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1201-21_0_5_line_10 |  | 6 | 13 | 0.0094398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1201-21_0_5_line_11 |  | 7 | 14 | 0.0051823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1201-21_0_5_line_12 |  | 8 | 15 | 0.017773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1201-21_0_5_line_13 |  | 9 | 16 | 0.042922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1201-21_0_5_line_14 |  | 11 | 12 | 0.031345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1201-21_0_5_line_15 |  | 12 | 17 | 0.034552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1201-21_0_5_line_16 |  | 13 | 25 | 0.025915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1201-21_0_5_line_17 |  | 14 | 21 | 0.016383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1201-21_0_5_line_18 |  | 15 | 38 | 0.027836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1201-21_0_5_line_19 |  | 16 | 31 | 0.04684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1201-21_0_5_line_20 |  | 17 | 40 | 0.059597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1201-21_0_5_line_21 |  | 18 | 19 | 0.0055437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1201-21_0_5_line_22 |  | 18 | 20 | 0.0057654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1201-21_0_5_line_23 |  | 19 | 21 | 0.017023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1201-21_0_5_line_24 |  | 20 | 22 | 0.0067055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1201-21_0_5_line_25 |  | 22 | 23 | 0.058074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1201-21_0_5_line_26 |  | 23 | 24 | 0.04122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1201-21_0_5_line_27 |  | 25 | 42 | 0.033869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1201-21_0_5_line_28 |  | 26 | 27 | 0.00067905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1201-21_0_5_line_29 |  | 26 | 28 | 0.064261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1201-21_0_5_line_30 |  | 28 | 29 | 0.045416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1201-21_0_5_line_31 |  | 29 | 30 | 0.073844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1201-21_0_5_line_32 |  | 30 | 31 | 0.04567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1201-21_0_5_line_33 |  | 31 | 34 | 0.038809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1201-21_0_5_line_34 |  | 32 | 33 | 0.022105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1201-21_0_5_line_35 |  | 32 | 34 | 0.0024801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1201-21_0_5_line_36 |  | 33 | 35 | 0.16598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1201-21_0_5_line_37 |  | 35 | 36 | 0.016344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1201-21_0_5_line_38 |  | 37 | 38 | 0.018618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1201-21_0_5_line_39 |  | 37 | 39 | 0.019093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1201-21_0_5_line_40 |  | 39 | 40 | 0.016724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1201-21_0_5_line_41 |  | 40 | 41 | 0.019442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1201-21_0_5_trafo_5 | 0.63 MVA 20/0.4 kV | 43 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2692311.845 | 1192756.2413 | 2692291.0166 | 1192744.7533
1 | 2692270.9491 | 1192733.685 | 2692291.0166 | 1192744.7533
2 | 2692311.845 | 1192756.2413 | 2692348.5747 | 1192774.5754
3 | 2692311.845 | 1192756.2413 | 2692296.1352 | 1192771.9576
4 | 2692288.9442 | 1192707.29 | 2692270.9491 | 1192733.685
5 | 2692348.5747 | 1192774.5754 | 2692327.1223 | 1192795.0552
6 | 2692348.5747 | 1192774.5754 | 2692354.3184 | 1192776.354 | 2692363.5203 | 1192777.8192 | 2692380.9011 | 1192775.4193 | 2692394.0811 | 1192771.0644 | 2692398.9512 | 1192768.1248
7 | 2692296.1352 | 1192771.9576 | 2692283.2362 | 1192784.8619
8 | 2692288.9442 | 1192707.29 | 2692297.9825 | 1192691.3681
9 | 2692288.9442 | 1192707.29 | 2692299.3259 | 1192713.3317 | 2692311.6569 | 1192691.369
10 | 2692320.2944 | 1192801.5736 | 2692327.1223 | 1192795.0552
11 | 2692403.3879 | 1192765.4468 | 2692398.9512 | 1192768.1248
12 | 2692270.6714 | 1192797.4319 | 2692283.2362 | 1192784.8619
13 | 2692297.9825 | 1192691.3681 | 2692319.1718 | 1192654.0413
14 | 2692200.3605 | 1192793.7076 | 2692226.6638 | 1192776.6585
15 | 2692171.3661 | 1192812.5011 | 2692200.3605 | 1192793.7076
16 | 2692320.2944 | 1192801.5736 | 2692312.3239 | 1192809.1828 | 2692304.6457 | 1192820.1269 | 2692303.538 | 1192821.1774
17 | 2692403.3879 | 1192765.4468 | 2692404.6238 | 1192764.7008 | 2692415.0893 | 1192754.0403
18 | 2692270.6714 | 1192797.4319 | 2692250.9922 | 1192817.1192
19 | 2692337.1075 | 1192612.205 | 2692338.299 | 1192618.9722 | 2692334.8681 | 1192626.3907 | 2692319.1718 | 1192654.0413
20 | 2692171.3661 | 1192812.5011 | 2692174.9072 | 1192816.2136 | 2692212.5089 | 1192855.6182
21 | 2692430.8981 | 1192737.937 | 2692427.0144 | 1192741.893
22 | 2692434.937 | 1192733.8228 | 2692430.8981 | 1192737.937
23 | 2692415.0893 | 1192754.0403 | 2692427.0144 | 1192741.893
24 | 2692434.937 | 1192733.8228 | 2692439.6346 | 1192729.0377
25 | 2692439.6346 | 1192729.0377 | 2692487.3026 | 1192762.2098
26 | 2692487.3026 | 1192762.2098 | 2692493.1521 | 1192750.2369 | 2692496.4365 | 1192738.9915 | 2692498.9955 | 1192731.2706 | 2692503.3241 | 1192724.4775
27 | 2692278.9616 | 1192844.4827 | 2692303.538 | 1192821.1774
28 | 2692412.2757 | 1192604.1815 | 2692412.9263 | 1192604.3758
29 | 2692430.4071 | 1192557.9993 | 2692439.8092 | 1192571.1975 | 2692420.2487 | 1192606.5626 | 2692412.9263 | 1192604.3758
30 | 2692405.9238 | 1192522.1648 | 2692417.1761 | 1192533.557 | 2692417.0314 | 1192537.0015 | 2692420.1218 | 1192548.6678 | 2692430.4071 | 1192557.9993
31 | 2692405.9238 | 1192522.1648 | 2692404.4986 | 1192527.0682 | 2692396.8533 | 1192550.165 | 2692391.9131 | 1192564.9649 | 2692382.5591 | 1192580.2304 | 2692375.7633 | 1192587.33 | 2692374.9475 | 1192588.0285
32 | 2692337.1075 | 1192612.205 | 2692350.5271 | 1192608.1428 | 2692358.797 | 1192601.8553 | 2692374.9475 | 1192588.0285
33 | 2692337.1075 | 1192612.205 | 2692333.593 | 1192606.2692 | 2692312.2798 | 1192582.5199
34 | 2692310.6636 | 1192580.6394 | 2692296.5748 | 1192563.606
35 | 2692310.6636 | 1192580.6394 | 2692311.5054 | 1192581.6571 | 2692312.2798 | 1192582.5199
36 | 2692296.5748 | 1192563.606 | 2692131.5456 | 1192581.3633
37 | 2692131.5456 | 1192581.3633 | 2692120.7366 | 1192569.1034
38 | 2692237.8299 | 1192830.2868 | 2692250.9922 | 1192817.1192
39 | 2692237.8299 | 1192830.2868 | 2692224.332 | 1192843.7903
40 | 2692212.5089 | 1192855.6182 | 2692224.332 | 1192843.7903
41 | 2692212.5089 | 1192855.6182 | 2692226.1368 | 1192869.4841

## bus_geodata
| x | y | coords
0 | 2692291.0166 | 1192744.7533
1 | 2692311.845 | 1192756.2413
2 | 2692270.9491 | 1192733.685
3 | 2692348.5747 | 1192774.5754
4 | 2692296.1352 | 1192771.9576
5 | 2692288.9442 | 1192707.29
6 | 2692327.1223 | 1192795.0552
7 | 2692398.9512 | 1192768.1248
8 | 2692283.2362 | 1192784.8619
9 | 2692297.9825 | 1192691.3681
10 | 2692311.6569 | 1192691.369
11 | 2692226.6638 | 1192776.6585
12 | 2692200.3605 | 1192793.7076
13 | 2692320.2944 | 1192801.5736
14 | 2692403.3879 | 1192765.4468
15 | 2692270.6714 | 1192797.4319
16 | 2692319.1718 | 1192654.0413
17 | 2692171.3661 | 1192812.5011
18 | 2692430.8981 | 1192737.937
19 | 2692427.0144 | 1192741.893
20 | 2692434.937 | 1192733.8228
21 | 2692415.0893 | 1192754.0403
22 | 2692439.6346 | 1192729.0377
23 | 2692487.3026 | 1192762.2098
24 | 2692503.3241 | 1192724.4775
25 | 2692303.538 | 1192821.1774
26 | 2692412.9263 | 1192604.3758
27 | 2692412.2757 | 1192604.1815
28 | 2692430.4071 | 1192557.9993
29 | 2692405.9238 | 1192522.1648
30 | 2692374.9475 | 1192588.0285
31 | 2692337.1075 | 1192612.205
32 | 2692310.6636 | 1192580.6394
33 | 2692296.5748 | 1192563.606
34 | 2692312.2798 | 1192582.5199
35 | 2692131.5456 | 1192581.3633
36 | 2692120.7366 | 1192569.1034
37 | 2692237.8299 | 1192830.2868
38 | 2692250.9922 | 1192817.1192
39 | 2692224.332 | 1192843.7903
40 | 2692212.5089 | 1192855.6182
41 | 2692226.1368 | 1192869.4841
42 | 2692278.9616 | 1192844.4827
43 | 2692270.9491 | 1192733.685

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99456 | -0.1032 | 0.029929 | 0.0075008
1 | 0.99253 | -0.14201 | 0 | 0
2 | 0.99683 | -0.059934 | 0 | 0
3 | 0.99016 | -0.18777 | 0 | 0
4 | 0.99001 | -0.19002 | 0.0071519 | 0.0017924
5 | 1 | 0 | -0.46521 | -0.11901
6 | 0.98934 | -0.20359 | 0.00099247 | 0.00024874
7 | 0.98857 | -0.21863 | 0.00054774 | 0.00013728
8 | 0.98807 | -0.22729 | 0.0067377 | 0.0016886
9 | 0.99802 | -0.037461 | 0.074812 | 0.01875
10 | 0.99976 | -0.0046683 | 0.0071978 | 0.0018039
11 | 0.97216 | -0.53717 | 0.052215 | 0.013086
12 | 0.97369 | -0.50704 | 0.011575 | 0.0029009
13 | 0.98909 | -0.20846 | 0.00083285 | 0.00020873
14 | 0.98841 | -0.22163 | 0.0050445 | 0.0012643
15 | 0.98629 | -0.2616 | 0.0066575 | 0.0016685
16 | 0.99483 | -0.097554 | 0.00088496 | 0.00022179
17 | 0.97574 | -0.4666 | 0 | 0
18 | 0.98753 | -0.2389 | 0.0053771 | 0.0013476
19 | 0.98763 | -0.2369 | 0.0036332 | 0.00091056
20 | 0.98745 | -0.24043 | 0.0043387 | 0.0010874
21 | 0.988 | -0.22966 | 0.0036322 | 0.00091031
22 | 0.98738 | -0.24168 | 0.0040736 | 0.0010209
23 | 0.98704 | -0.24832 | 0 | 0
24 | 0.9868 | -0.25303 | 0.0063893 | 0.0016013
25 | 0.98842 | -0.22146 | 0.013976 | 0.0035026
26 | 0.98024 | -0.37882 | 0.0092151 | 0.0023095
27 | 0.98021 | -0.37935 | 0.04321 | 0.01083
28 | 0.98335 | -0.3179 | 0 | 0
29 | 0.98556 | -0.27508 | 0 | 0
30 | 0.98914 | -0.20586 | 0.0001158 | 2.9021e-05
31 | 0.99136 | -0.16321 | 0 | 0
32 | 0.98727 | -0.24117 | 0.0086233 | 0.0021612
33 | 0.98526 | -0.27959 | 0.00052815 | 0.00013237
34 | 0.98752 | -0.23649 | 0.00045329 | 0.0001136
35 | 0.97029 | -0.57149 | 0.080429 | 0.020158
36 | 0.97005 | -0.57634 | 0.016027 | 0.0040167
37 | 0.98205 | -0.34351 | 0.0065954 | 0.001653
38 | 0.98366 | -0.31224 | 0.0081635 | 0.002046
39 | 0.98051 | -0.37341 | 0.0079377 | 0.0019894
40 | 0.97929 | -0.39725 | 0 | 0
41 | 0.97902 | -0.40247 | 0.014768 | 0.0037012
42 | 0.98798 | -0.23002 | 0.014161 | 0.0035491
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.18712 | 0.047789 | -0.18677 | -0.047565 | 0.00035034 | 0.0002236 | 0.28027 | 0.28027 | 0.28027 | 0.99456 | -0.1032 | 0.99253 | -0.14201 | 38.4989
1 | -0.21704 | -0.05529 | 0.2175 | 0.05558 | 0.00045401 | 0.00028997 | 0.32505 | 0.32505 | 0.32505 | 0.99456 | -0.1032 | 0.99683 | -0.059934 | 44.6496
2 | 0.063268 | 0.015957 | -0.06313 | -0.015869 | 0.00013829 | 8.7975e-05 | 0.094889 | 0.094889 | 0.094889 | 0.99253 | -0.14201 | 0.99016 | -0.18777 | 26.0684
3 | 0.1235 | 0.031608 | -0.12321 | -0.031425 | 0.00028639 | 0.000183 | 0.18538 | 0.18538 | 0.18538 | 0.99253 | -0.14201 | 0.99001 | -0.19002 | 50.9296
4 | -0.2175 | -0.05558 | 0.21813 | 0.055983 | 0.00063241 | 0.00040391 | 0.32505 | 0.32505 | 0.32505 | 0.99683 | -0.059934 | 1 | 0 | 44.6496
5 | 0.030015 | 0.0075416 | -0.029992 | -0.0075275 | 2.2635e-05 | 1.4105e-05 | 0.045113 | 0.045113 | 0.045113 | 0.99016 | -0.18777 | 0.98934 | -0.20359 | 12.3937
6 | 0.033115 | 0.0083277 | -0.033067 | -0.0082971 | 4.8728e-05 | 3.0513e-05 | 0.049776 | 0.049776 | 0.049776 | 0.99016 | -0.18777 | 0.98857 | -0.21863 | 13.6748
7 | 0.11606 | 0.029633 | -0.11585 | -0.029499 | 0.00020867 | 0.00013331 | 0.17463 | 0.17463 | 0.17463 | 0.99001 | -0.19002 | 0.98807 | -0.22729 | 47.9765
8 | 0.23823 | 0.061226 | -0.23779 | -0.06095 | 0.00043268 | 0.00027644 | 0.35503 | 0.35503 | 0.35503 | 1 | 0 | 0.99802 | -0.037461 | 48.7674
9 | 0.0071994 | 0.0018045 | -0.0071978 | -0.0018039 | 1.601e-06 | 5.3672e-07 | 0.010713 | 0.010713 | 0.010713 | 1 | 0 | 0.99976 | -0.0046683 | 2.9432
10 | 0.028999 | 0.0072787 | -0.028993 | -0.0072745 | 6.7355e-06 | 4.1895e-06 | 0.04362 | 0.04362 | 0.04362 | 0.98934 | -0.20359 | 0.98909 | -0.20846 | 11.9836
11 | 0.032519 | 0.0081599 | -0.032514 | -0.008157 | 4.6568e-06 | 2.9139e-06 | 0.048952 | 0.048952 | 0.048952 | 0.98857 | -0.21863 | 0.98841 | -0.22163 | 13.4483
12 | 0.10911 | 0.027811 | -0.10893 | -0.027695 | 0.00018033 | 0.00011518 | 0.16449 | 0.16449 | 0.16449 | 0.98807 | -0.22729 | 0.98629 | -0.2616 | 45.1889
13 | 0.16298 | 0.0422 | -0.16251 | -0.041896 | 0.00047712 | 0.00030424 | 0.24349 | 0.24349 | 0.24349 | 0.99802 | -0.037461 | 0.99483 | -0.097554 | 33.446
14 | -0.052215 | -0.013086 | 0.05229 | 0.013134 | 7.5081e-05 | 4.7662e-05 | 0.079921 | 0.079921 | 0.079921 | 0.97216 | -0.53717 | 0.97369 | -0.50704 | 21.9564
15 | -0.063865 | -0.016035 | 0.063988 | 0.016113 | 0.00012345 | 7.8579e-05 | 0.09761 | 0.09761 | 0.09761 | 0.97369 | -0.50704 | 0.97574 | -0.4666 | 26.816
16 | 0.02816 | 0.0070658 | -0.028142 | -0.007055 | 1.7444e-05 | 1.0832e-05 | 0.042367 | 0.042368 | 0.042368 | 0.98909 | -0.20846 | 0.98842 | -0.22146 | 11.6394
17 | 0.02747 | 0.0068927 | -0.027459 | -0.0068862 | 1.0508e-05 | 6.5153e-06 | 0.041357 | 0.041358 | 0.041358 | 0.98841 | -0.22163 | 0.988 | -0.22966 | 11.362
18 | 0.10227 | 0.026027 | -0.10203 | -0.025868 | 0.00024899 | 0.000159 | 0.15444 | 0.15444 | 0.15444 | 0.98629 | -0.2616 | 0.98366 | -0.31224 | 42.4296
19 | 0.16162 | 0.041674 | -0.16111 | -0.041346 | 0.00051503 | 0.00032841 | 0.24216 | 0.24216 | 0.24216 | 0.99483 | -0.097554 | 0.99136 | -0.16321 | 33.2642
20 | -0.063988 | -0.016113 | 0.064201 | 0.016249 | 0.00021293 | 0.00013553 | 0.09761 | 0.09761 | 0.09761 | 0.97574 | -0.4666 | 0.97929 | -0.39725 | 26.8159
21 | -0.020184 | -0.0050591 | 0.020186 | 0.0050603 | 1.9229e-06 | 1.1597e-06 | 0.030413 | 0.030413 | 0.030413 | 0.98753 | -0.2389 | 0.98763 | -0.2369 | 8.3553
22 | 0.014807 | 0.0037115 | -0.014806 | -0.0037109 | 1.0762e-06 | 6.1502e-07 | 0.022311 | 0.022311 | 0.022311 | 0.98753 | -0.2389 | 0.98745 | -0.24043 | 6.1294
23 | -0.023819 | -0.0059708 | 0.023827 | 0.0059759 | 8.2212e-06 | 5.0436e-06 | 0.035887 | 0.035887 | 0.035887 | 0.98763 | -0.2369 | 0.988 | -0.22966 | 9.8591
24 | 0.010467 | 0.0026235 | -0.010466 | -0.0026232 | 6.256e-07 | 3.1461e-07 | 0.015773 | 0.015773 | 0.015773 | 0.98745 | -0.24043 | 0.98738 | -0.24168 | 4.3333
25 | 0.0063928 | 0.0016023 | -0.0063907 | -0.0016017 | 2.0214e-06 | 5.5116e-07 | 0.0096341 | 0.0096344 | 0.0096344 | 0.98738 | -0.24168 | 0.98704 | -0.24832 | 2.6468
26 | 0.0063907 | 0.0016017 | -0.0063893 | -0.0016013 | 1.4348e-06 | 3.9156e-07 | 0.0096344 | 0.0096346 | 0.0096346 | 0.98704 | -0.24832 | 0.9868 | -0.25303 | 2.6469
27 | 0.014167 | 0.0035524 | -0.014161 | -0.0035491 | 5.7776e-06 | 3.2637e-06 | 0.021328 | 0.021328 | 0.021328 | 0.98842 | -0.22146 | 0.98798 | -0.23002 | 5.8594
28 | 0.043211 | 0.01083 | -0.04321 | -0.01083 | 1.0957e-06 | 6.9268e-07 | 0.065596 | 0.065596 | 0.065596 | 0.98024 | -0.37882 | 0.98021 | -0.37935 | 18.0208
29 | -0.052427 | -0.01314 | 0.052579 | 0.013237 | 0.00015263 | 9.6869e-05 | 0.079584 | 0.079584 | 0.079584 | 0.98024 | -0.37882 | 0.98335 | -0.3179 | 21.8639
30 | -0.052579 | -0.013237 | 0.052687 | 0.013305 | 0.00010787 | 6.8458e-05 | 0.079584 | 0.079584 | 0.079584 | 0.98335 | -0.3179 | 0.98556 | -0.27508 | 21.8638
31 | -0.052687 | -0.013305 | 0.052862 | 0.013416 | 0.00017539 | 0.0001113 | 0.079584 | 0.079584 | 0.079584 | 0.98556 | -0.27508 | 0.98914 | -0.20586 | 21.8637
32 | -0.052978 | -0.013445 | 0.053087 | 0.013515 | 0.00010895 | 6.9138e-05 | 0.079758 | 0.079758 | 0.079758 | 0.98914 | -0.20586 | 0.99136 | -0.16321 | 21.9115
33 | 0.10802 | 0.027831 | -0.10763 | -0.027586 | 0.00038385 | 0.00024517 | 0.16241 | 0.16241 | 0.16241 | 0.99136 | -0.16321 | 0.98752 | -0.23649 | 44.6171
34 | 0.098534 | 0.025296 | -0.09835 | -0.025178 | 0.00018336 | 0.00011707 | 0.14873 | 0.14873 | 0.14873 | 0.98727 | -0.24117 | 0.98526 | -0.27959 | 40.8589
35 | -0.10716 | -0.027457 | 0.10718 | 0.027472 | 2.4325e-05 | 1.5536e-05 | 0.16172 | 0.16172 | 0.16172 | 0.98727 | -0.24117 | 0.98752 | -0.23649 | 44.4294
36 | 0.097822 | 0.025046 | -0.09646 | -0.024176 | 0.0013621 | 0.00086964 | 0.14793 | 0.14793 | 0.14793 | 0.98526 | -0.27959 | 0.97029 | -0.57149 | 40.6399
37 | 0.016031 | 0.0040189 | -0.016027 | -0.0040167 | 3.7045e-06 | 2.1691e-06 | 0.024585 | 0.024585 | 0.024585 | 0.97029 | -0.57149 | 0.97005 | -0.57634 | 6.7541
38 | -0.093721 | -0.023732 | 0.093862 | 0.023822 | 0.00014097 | 8.9984e-05 | 0.14209 | 0.14209 | 0.14209 | 0.98205 | -0.34351 | 0.98366 | -0.31224 | 39.037
39 | 0.087126 | 0.022079 | -0.087001 | -0.021999 | 0.00012494 | 7.9723e-05 | 0.1321 | 0.1321 | 0.1321 | 0.98205 | -0.34351 | 0.98051 | -0.37341 | 36.2916
40 | 0.079063 | 0.02001 | -0.078973 | -0.019952 | 9.0392e-05 | 5.764e-05 | 0.12006 | 0.12006 | 0.12006 | 0.98051 | -0.37341 | 0.97929 | -0.39725 | 32.9823
41 | 0.014772 | 0.0037033 | -0.014768 | -0.0037012 | 3.6731e-06 | 2.1063e-06 | 0.022446 | 0.022446 | 0.022446 | 0.97929 | -0.39725 | 0.97902 | -0.40247 | 6.1664

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46521 | 0.11901

## res_load
| p_mw | q_mvar
0 | 0.029929 | 0.0075008
1 | 0.0071519 | 0.0017924
2 | 0.00099247 | 0.00024874
3 | 0.00054774 | 0.00013728
4 | 0.0067377 | 0.0016886
5 | 0.074812 | 0.01875
6 | 0.0071978 | 0.0018039
7 | 0.052215 | 0.013086
8 | 0.011575 | 0.0029009
9 | 0.00083285 | 0.00020873
10 | 0.0050445 | 0.0012643
11 | 0.0066575 | 0.0016685
12 | 0.00088496 | 0.00022179
13 | 0.0053771 | 0.0013476
14 | 0.0036332 | 0.00091056
15 | 0.0043387 | 0.0010874
16 | 0.0036322 | 0.00091031
17 | 0.0040736 | 0.0010209
18 | 0.0063893 | 0.0016013
19 | 0.013976 | 0.0035026
20 | 0.0092151 | 0.0023095
21 | 0.04321 | 0.01083
22 | 0.0001158 | 2.9021e-05
23 | 0.0086233 | 0.0021612
24 | 0.00052815 | 0.00013237
25 | 0.00045329 | 0.0001136
26 | 0.080429 | 0.020158
27 | 0.016027 | 0.0040167
28 | 0.0065954 | 0.001653
29 | 0.0081635 | 0.002046
30 | 0.0079377 | 0.0019894
31 | 0.014768 | 0.0037012
32 | 0.014161 | 0.0035491

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1