## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1201-34_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1201-34_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1201-34_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1201-34_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1201-34_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_1201-34_0_4_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_1201-34_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1201-34_0_4_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_1201-34_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1201-34_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1201-34_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1201-34_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1201-34_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1201-34_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1201-34_0_4_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_1201-34_0_4_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1201-34_0_4_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_1201-34_0_4_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_1201-34_0_4_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_1201-34_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1201-34_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1201-34_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1201-34_0_4_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_1201-34_0_4_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1201-34_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1201-34_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1201-34_0_4_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_1201-34_0_4_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_1201-34_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1201-34_0_4_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1201-34_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1201-34_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1201-34_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1201-34_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1201-34_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1201-34_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1201-34_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1201-34_0_4_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_1201-34_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1201-34_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1201-34_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_MV_14_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1201-34_0_4_load_0 | 0 | 0.0062055 | 0.0015552 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1201-34_0_4_load_12 | 4 | 0.011516 | 0.0028861 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1201-34_0_4_load_36 | 5 | 0.01162 | 0.0029122 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1201-34_0_4_load_5 | 8 | 0.017869 | 0.0044784 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1201-34_0_4_load_8 | 11 | 0.010069 | 0.0025236 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1201-34_0_4_load_9 | 12 | 0.012651 | 0.0031706 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1201-34_0_4_load_11 | 13 | 0.012873 | 0.0032262 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1201-34_0_4_load_28 | 14 | 0.012023 | 0.0030132 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1201-34_0_4_load_31 | 15 | 0.0099707 | 0.0024989 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1201-34_0_4_load_26 | 16 | 0.012383 | 0.0031036 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1201-34_0_4_load_32 | 17 | 0.0051815 | 0.0012986 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1201-34_0_4_load_37 | 18 | 0.012942 | 0.0032435 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1201-34_0_4_load_27 | 19 | 0.0040703 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1201-34_0_4_load_10 | 20 | 0.019507 | 0.004889 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1201-34_0_4_load_16 | 21 | 0.011614 | 0.0029107 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1201-34_0_4_load_34 | 22 | 0.0088291 | 0.0022128 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1201-34_0_4_load_38 | 23 | 0.0032418 | 0.00081247 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1201-34_0_4_load_25 | 24 | 0.0056893 | 0.0014259 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1201-34_0_4_load_43 | 27 | 0.019846 | 0.0049739 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1201-34_0_4_load_17 | 28 | 0.0074509 | 0.0018674 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1201-34_0_4_load_14 | 29 | 0.024057 | 0.0060294 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1201-34_0_4_load_15 | 30 | 0.023842 | 0.0059752 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1201-34_0_4_load_18 | 31 | 0.041494 | 0.010399 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1201-34_0_4_load_29 | 32 | 0.013707 | 0.0034353 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1201-34_0_4_load_19 | 33 | 0.024079 | 0.0060347 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1201-34_0_4_load_30 | 34 | 0.014377 | 0.0036032 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1201-34_0_4_load_20 | 35 | 0.010175 | 0.0025502 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1201-34_0_4_load_39 | 37 | 0.023883 | 0.0059856 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1201-34_0_4_load_24 | 38 | 0.021971 | 0.0055065 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1201-34_0_4_load_22 | 39 | 0.016656 | 0.0041744 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1201-34_0_4_load_23 | 40 | 0.0073313 | 0.0018374 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1201-34_0_4_line_0 |  | 0 | 1 | 0.098658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1201-34_0_4_line_1 |  | 1 | 2 | 0.11428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1201-34_0_4_line_2 |  | 2 | 5 | 0.019338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1201-34_0_4_line_3 |  | 2 | 3 | 0.028514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1201-34_0_4_line_4 |  | 3 | 4 | 0.018694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1201-34_0_4_line_5 |  | 4 | 6 | 0.029731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1201-34_0_4_line_6 |  | 5 | 7 | 0.016853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1201-34_0_4_line_7 |  | 6 | 29 | 0.014837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1201-34_0_4_line_8 |  | 6 | 30 | 0.0086485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1201-34_0_4_line_9 |  | 7 | 22 | 0.017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1201-34_0_4_line_10 |  | 8 | 9 | 0.013634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1201-34_0_4_line_11 |  | 8 | 10 | 0.017109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1201-34_0_4_line_12 |  | 9 | 11 | 0.02895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1201-34_0_4_line_13 |  | 9 | 12 | 0.043281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1201-34_0_4_line_14 |  | 10 | 13 | 0.013315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1201-34_0_4_line_15 |  | 11 | 18 | 0.014417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1201-34_0_4_line_16 |  | 12 | 19 | 0.053795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1201-34_0_4_line_17 |  | 13 | 22 | 0.0025146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1201-34_0_4_line_18 |  | 14 | 15 | 0.014606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1201-34_0_4_line_19 |  | 14 | 16 | 0.013959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1201-34_0_4_line_20 |  | 15 | 17 | 0.049891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1201-34_0_4_line_21 |  | 16 | 24 | 0.022862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1201-34_0_4_line_22 |  | 17 | 25 | 0.015987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1201-34_0_4_line_23 |  | 18 | 23 | 7.899e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1201-34_0_4_line_24 |  | 19 | 24 | 0.022155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1201-34_0_4_line_25 |  | 20 | 21 | 0.0046463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1201-34_0_4_line_26 |  | 21 | 28 | 0.016053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1201-34_0_4_line_27 |  | 25 | 26 | 0.013681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1201-34_0_4_line_28 |  | 26 | 27 | 0.028052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1201-34_0_4_line_29 |  | 28 | 35 | 0.010995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1201-34_0_4_line_30 |  | 29 | 31 | 0.010963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1201-34_0_4_line_31 |  | 30 | 32 | 0.0064721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1201-34_0_4_line_32 |  | 31 | 33 | 0.017088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1201-34_0_4_line_33 |  | 32 | 34 | 0.01389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1201-34_0_4_line_34 |  | 33 | 37 | 0.018439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1201-34_0_4_line_35 |  | 35 | 36 | 0.025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1201-34_0_4_line_36 |  | 36 | 38 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1201-34_0_4_line_37 |  | 36 | 37 | 0.0017886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1201-34_0_4_line_38 |  | 38 | 39 | 0.029419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1201-34_0_4_line_39 |  | 39 | 40 | 0.0025971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1201-34_0_4_trafo_16 | 0.63 MVA 20/0.4 kV | 41 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2692417.1761 | 1192533.557 | 2692479.8723 | 1192609.732
1 | 2692417.1761 | 1192533.557 | 2692405.9238 | 1192522.1648 | 2692411.9815 | 1192501.1671 | 2692413.7348 | 1192495.257 | 2692425.3272 | 1192480.6933 | 2692457.4695 | 1192440.286
2 | 2692457.4695 | 1192440.286 | 2692469.1471 | 1192424.8718
3 | 2692457.4695 | 1192440.286 | 2692480.1027 | 1192457.7136
4 | 2692480.1027 | 1192457.7136 | 2692495.5002 | 1192468.315
5 | 2692513.3788 | 1192491.4163 | 2692502.1228 | 1192472.8748 | 2692495.5002 | 1192468.315
6 | 2692479.3239 | 1192411.4385 | 2692469.1471 | 1192424.8718
7 | 2692513.3788 | 1192491.4163 | 2692526.2496 | 1192484.0361
8 | 2692513.3788 | 1192491.4163 | 2692505.8212 | 1192495.621
9 | 2692479.3239 | 1192411.4385 | 2692490.1893 | 1192406.9368 | 2692495.2668 | 1192404.3557
10 | 2692537.3717 | 1192384.4739 | 2692524.9567 | 1192390.1101
11 | 2692509.3775 | 1192397.1827 | 2692524.9567 | 1192390.1101
12 | 2692537.3717 | 1192384.4739 | 2692554.4237 | 1192385.1714 | 2692565.8077 | 1192381.7607
13 | 2692537.3717 | 1192384.4739 | 2692540.5306 | 1192377.9074 | 2692562.1142 | 1192359.207 | 2692568.1391 | 1192354.8483
14 | 2692509.3775 | 1192397.1827 | 2692497.5084 | 1192403.2162
15 | 2692565.8077 | 1192381.7607 | 2692579.6181 | 1192377.623
16 | 2692568.1391 | 1192354.8483 | 2692549.6533 | 1192304.3294
17 | 2692495.2668 | 1192404.3557 | 2692497.5084 | 1192403.2162
18 | 2692490.3189 | 1192316.1744 | 2692496.8805 | 1192329.2236
19 | 2692509.3543 | 1192324.1032 | 2692503.1892 | 1192328.0092 | 2692499.2225 | 1192329.6267 | 2692496.8805 | 1192329.2236 | 2692496.8805 | 1192329.2236
20 | 2692490.3189 | 1192316.1744 | 2692487.8934 | 1192311.3509 | 2692483.0193 | 1192299.1678 | 2692483.6292 | 1192285.8575 | 2692483.9082 | 1192267.8139
21 | 2692509.3543 | 1192324.1032 | 2692520.4057 | 1192317.1016 | 2692529.3079 | 1192313.053
22 | 2692479.8834 | 1192252.4782 | 2692483.9537 | 1192264.8713 | 2692483.9082 | 1192267.8139
23 | 2692579.6181 | 1192377.623 | 2692579.6938 | 1192377.6003
24 | 2692549.6533 | 1192304.3294 | 2692544.8762 | 1192305.9728 | 2692529.3079 | 1192313.053
25 | 2692532.9779 | 1192415.6705 | 2692532.9779 | 1192415.6705 | 2692535.3565 | 1192419.6618
26 | 2692543.5747 | 1192433.4518 | 2692535.3565 | 1192419.6618
27 | 2692479.8834 | 1192252.4782 | 2692493.2077 | 1192249.2153
28 | 2692493.2077 | 1192249.2153 | 2692520.6344 | 1192243.3245
29 | 2692550.5044 | 1192441.8989 | 2692545.6108 | 1192436.8684 | 2692543.5747 | 1192433.4518
30 | 2692535.7602 | 1192478.5827 | 2692526.2496 | 1192484.0361
31 | 2692505.8212 | 1192495.621 | 2692500.1656 | 1192498.7677
32 | 2692550.5844 | 1192470.0825 | 2692535.7602 | 1192478.5827
33 | 2692488.0276 | 1192505.5209 | 2692500.1656 | 1192498.7677
34 | 2692550.5844 | 1192470.0825 | 2692566.5807 | 1192460.9102
35 | 2692568.1323 | 1192460.0205 | 2692550.5044 | 1192441.8989
36 | 2692568.1323 | 1192460.0205 | 2692579.7568 | 1192453.6486
37 | 2692568.1323 | 1192460.0205 | 2692566.5807 | 1192460.9102
38 | 2692579.7568 | 1192453.6486 | 2692605.5543 | 1192439.5079
39 | 2692607.8317 | 1192438.2595 | 2692605.5543 | 1192439.5079

## bus_geodata
| x | y | coords
0 | 2692479.8723 | 1192609.732
1 | 2692417.1761 | 1192533.557
2 | 2692457.4695 | 1192440.286
3 | 2692480.1027 | 1192457.7136
4 | 2692495.5002 | 1192468.315
5 | 2692469.1471 | 1192424.8718
6 | 2692513.3788 | 1192491.4163
7 | 2692479.3239 | 1192411.4385
8 | 2692524.9567 | 1192390.1101
9 | 2692537.3717 | 1192384.4739
10 | 2692509.3775 | 1192397.1827
11 | 2692565.8077 | 1192381.7607
12 | 2692568.1391 | 1192354.8483
13 | 2692497.5084 | 1192403.2162
14 | 2692496.8805 | 1192329.2236
15 | 2692490.3189 | 1192316.1744
16 | 2692509.3543 | 1192324.1032
17 | 2692483.9082 | 1192267.8139
18 | 2692579.6181 | 1192377.623
19 | 2692549.6533 | 1192304.3294
20 | 2692532.9779 | 1192415.6705
21 | 2692535.3565 | 1192419.6618
22 | 2692495.2668 | 1192404.3557
23 | 2692579.6938 | 1192377.6003
24 | 2692529.3079 | 1192313.053
25 | 2692479.8834 | 1192252.4782
26 | 2692493.2077 | 1192249.2153
27 | 2692520.6344 | 1192243.3245
28 | 2692543.5747 | 1192433.4518
29 | 2692526.2496 | 1192484.0361
30 | 2692505.8212 | 1192495.621
31 | 2692535.7602 | 1192478.5827
32 | 2692500.1656 | 1192498.7677
33 | 2692550.5844 | 1192470.0825
34 | 2692488.0276 | 1192505.5209
35 | 2692550.5044 | 1192441.8989
36 | 2692568.1323 | 1192460.0205
37 | 2692566.5807 | 1192460.9102
38 | 2692579.7568 | 1192453.6486
39 | 2692605.5543 | 1192439.5079
40 | 2692607.8317 | 1192438.2595
41 | 2692509.3775 | 1192397.1827

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98293 | -0.32776 | 0.0062055 | 0.0015552
1 | 0.98349 | -0.31672 | 0 | 0
2 | 0.98414 | -0.30394 | 0 | 0
3 | 0.9856 | -0.27567 | 0 | 0
4 | 0.98656 | -0.25719 | 0.011516 | 0.0028861
5 | 0.98319 | -0.32243 | 0.01162 | 0.0029122
6 | 0.98819 | -0.22583 | 0 | 0
7 | 0.98242 | -0.3374 | 0 | 0
8 | 0.98033 | -0.37817 | 0.017869 | 0.0044784
9 | 0.97987 | -0.38709 | 0 | 0
10 | 0.981 | -0.36516 | 0 | 0
11 | 0.97917 | -0.40089 | 0.010069 | 0.0025236
12 | 0.97877 | -0.40854 | 0.012651 | 0.0031706
13 | 0.98151 | -0.35504 | 0.012873 | 0.0032262
14 | 0.97382 | -0.50578 | 0.012023 | 0.0030132
15 | 0.97334 | -0.51518 | 0.0099707 | 0.0024989
16 | 0.97443 | -0.49372 | 0.012383 | 0.0031036
17 | 0.97217 | -0.53818 | 0.0051815 | 0.0012986
18 | 0.97895 | -0.40514 | 0.012942 | 0.0032435
19 | 0.97704 | -0.44245 | 0.0040703 | 0.0010201
20 | 0.99992 | -0.0015799 | 0.019507 | 0.004889
21 | 1 | 0 | -0.43268 | -0.11016
22 | 0.98162 | -0.35293 | 0.0088291 | 0.0022128
23 | 0.97895 | -0.40514 | 0.0032418 | 0.00081247
24 | 0.97569 | -0.46882 | 0.0056893 | 0.0014259
25 | 0.97188 | -0.54403 | 0 | 0
26 | 0.97162 | -0.54904 | 0 | 0
27 | 0.9711 | -0.55933 | 0.019846 | 0.0049739
28 | 0.998 | -0.037947 | 0.0074509 | 0.0018674
29 | 0.98924 | -0.20564 | 0.024057 | 0.0060294
30 | 0.98778 | -0.23384 | 0.023842 | 0.0059752
31 | 0.99009 | -0.18918 | 0.041494 | 0.010399
32 | 0.98761 | -0.23709 | 0.013707 | 0.0034353
33 | 0.99164 | -0.15941 | 0.024079 | 0.0060347
34 | 0.98743 | -0.24066 | 0.014377 | 0.0036032
35 | 0.99665 | -0.063547 | 0.010175 | 0.0025502
36 | 0.99364 | -0.12116 | 0 | 0
37 | 0.99345 | -0.12476 | 0.023883 | 0.0059856
38 | 0.99308 | -0.13192 | 0.021971 | 0.0055065
39 | 0.99243 | -0.1444 | 0.016656 | 0.0041744
40 | 0.99242 | -0.14473 | 0.0073313 | 0.0018374
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0062055 | -0.0015552 | 0.0062087 | 0.0015561 | 3.2649e-06 | 8.3831e-07 | 0.0093943 | 0.0093938 | 0.0093943 | 0.98293 | -0.32776 | 0.98349 | -0.31672 | 2.5808
1 | -0.0062087 | -0.0015561 | 0.0062125 | 0.001557 | 3.7814e-06 | 9.6898e-07 | 0.0093938 | 0.0093933 | 0.0093938 | 0.98349 | -0.31672 | 0.98414 | -0.30394 | 2.5807
2 | 0.16028 | 0.040558 | -0.16014 | -0.040467 | 0.00014213 | 9.0225e-05 | 0.24248 | 0.24248 | 0.24248 | 0.98414 | -0.30394 | 0.98319 | -0.32243 | 22.2051
3 | -0.16649 | -0.042115 | 0.16672 | 0.042258 | 0.00022612 | 0.00014363 | 0.25187 | 0.25187 | 0.25187 | 0.98414 | -0.30394 | 0.9856 | -0.27567 | 23.0653
4 | -0.16672 | -0.042258 | 0.16687 | 0.042353 | 0.00014824 | 9.4161e-05 | 0.25187 | 0.25187 | 0.25187 | 0.9856 | -0.27567 | 0.98656 | -0.25719 | 23.0653
5 | -0.17838 | -0.045239 | 0.17865 | 0.04541 | 0.0002694 | 0.00017128 | 0.26924 | 0.26924 | 0.26924 | 0.98656 | -0.25719 | 0.98819 | -0.22583 | 24.6558
6 | 0.14852 | 0.037555 | -0.14841 | -0.037488 | 0.00010655 | 6.7549e-05 | 0.22489 | 0.22489 | 0.22489 | 0.98319 | -0.32243 | 0.98242 | -0.3374 | 20.5947
7 | -0.2306 | -0.05844 | 0.23083 | 0.058583 | 0.00022392 | 0.00014274 | 0.34747 | 0.34747 | 0.34747 | 0.98819 | -0.22583 | 0.98924 | -0.20564 | 31.8199
8 | 0.051952 | 0.01303 | -0.051932 | -0.013018 | 1.985e-05 | 1.2593e-05 | 0.078233 | 0.078233 | 0.078233 | 0.98819 | -0.22583 | 0.98778 | -0.23384 | 21.4927
9 | 0.14841 | 0.037488 | -0.1483 | -0.037418 | 0.00011037 | 6.9971e-05 | 0.22489 | 0.22489 | 0.22489 | 0.98242 | -0.3374 | 0.98162 | -0.35293 | 20.5947
10 | 0.10858 | 0.027403 | -0.10853 | -0.027374 | 4.6328e-05 | 2.9134e-05 | 0.16487 | 0.16487 | 0.16487 | 0.98033 | -0.37817 | 0.97987 | -0.38709 | 15.0982
11 | -0.12644 | -0.031881 | 0.12652 | 0.031931 | 7.8836e-05 | 4.9808e-05 | 0.192 | 0.192 | 0.192 | 0.98033 | -0.37817 | 0.981 | -0.36516 | 17.582
12 | 0.026273 | 0.0065922 | -0.026256 | -0.0065815 | 1.7284e-05 | 1.0698e-05 | 0.039901 | 0.039901 | 0.039901 | 0.97987 | -0.38709 | 0.97917 | -0.40089 | 10.9619
13 | 0.082255 | 0.020781 | -0.082171 | -0.020729 | 8.4495e-05 | 5.2443e-05 | 0.12497 | 0.12497 | 0.12497 | 0.97987 | -0.38709 | 0.97877 | -0.40854 | 11.4443
14 | -0.12652 | -0.031931 | 0.12658 | 0.03197 | 6.1351e-05 | 3.876e-05 | 0.192 | 0.19199 | 0.192 | 0.981 | -0.36516 | 0.98151 | -0.35504 | 17.582
15 | 0.016187 | 0.0040579 | -0.016184 | -0.004056 | 3.2715e-06 | 1.9125e-06 | 0.024599 | 0.024599 | 0.024599 | 0.97917 | -0.40089 | 0.97895 | -0.40514 | 6.7581
16 | 0.06952 | 0.017558 | -0.069407 | -0.017488 | 0.00011278 | 7.0827e-05 | 0.10574 | 0.10574 | 0.10574 | 0.97877 | -0.40854 | 0.97704 | -0.44245 | 14.5247
17 | -0.13946 | -0.035196 | 0.13947 | 0.035205 | 1.4062e-05 | 8.9042e-06 | 0.21151 | 0.21151 | 0.21151 | 0.98151 | -0.35504 | 0.98162 | -0.35293 | 19.3691
18 | 0.035061 | 0.0088103 | -0.035046 | -0.0088004 | 1.5726e-05 | 9.883e-06 | 0.053583 | 0.053583 | 0.053583 | 0.97382 | -0.50578 | 0.97334 | -0.51518 | 14.7206
19 | -0.047084 | -0.011823 | 0.047111 | 0.011841 | 2.7101e-05 | 1.7171e-05 | 0.071954 | 0.071954 | 0.071954 | 0.97382 | -0.50578 | 0.97443 | -0.49372 | 19.7676
20 | 0.025075 | 0.0063015 | -0.025047 | -0.0062846 | 2.7502e-05 | 1.6982e-05 | 0.03834 | 0.03834 | 0.03834 | 0.97334 | -0.51518 | 0.97217 | -0.53818 | 10.5331
21 | -0.059495 | -0.014944 | 0.059565 | 0.014989 | 7.0784e-05 | 4.5017e-05 | 0.090864 | 0.090864 | 0.090864 | 0.97443 | -0.49372 | 0.97569 | -0.46882 | 24.9627
22 | 0.019866 | 0.0049859 | -0.01986 | -0.0049826 | 5.5441e-06 | 3.35e-06 | 0.030409 | 0.03041 | 0.03041 | 0.97217 | -0.53818 | 0.97188 | -0.54403 | 8.3543
23 | 0.0032418 | 0.00081247 | -0.0032418 | -0.00081247 | 7.1932e-10 | -5.3335e-10 | 0.0049275 | 0.0049275 | 0.0049275 | 0.97895 | -0.40514 | 0.97895 | -0.40514 | 1.3537
24 | 0.065337 | 0.016468 | -0.065255 | -0.016415 | 8.2318e-05 | 5.2407e-05 | 0.099541 | 0.099541 | 0.099541 | 0.97704 | -0.44245 | 0.97569 | -0.46882 | 27.3464
25 | -0.019507 | -0.004889 | 0.019509 | 0.0048899 | 1.4683e-06 | 8.7876e-07 | 0.02903 | 0.02903 | 0.02903 | 0.99992 | -0.0015799 | 1 | 0 | 7.9752
26 | 0.41153 | 0.10527 | -0.41077 | -0.10479 | 0.00075431 | 0.00048213 | 0.61311 | 0.61311 | 0.61311 | 1 | 0 | 0.998 | -0.037947 | 56.1457
27 | 0.01986 | 0.0049826 | -0.019856 | -0.0049797 | 4.7443e-06 | 2.8668e-06 | 0.03041 | 0.03041 | 0.03041 | 0.97188 | -0.54403 | 0.97162 | -0.54904 | 8.3543
28 | 0.019856 | 0.0049797 | -0.019846 | -0.0049739 | 9.7279e-06 | 5.8786e-06 | 0.03041 | 0.03041 | 0.03041 | 0.97162 | -0.54904 | 0.9711 | -0.55933 | 8.3543
29 | 0.40332 | 0.10292 | -0.40282 | -0.1026 | 0.0004981 | 0.00031835 | 0.602 | 0.602 | 0.602 | 0.998 | -0.037947 | 0.99665 | -0.063547 | 55.1284
30 | -0.25488 | -0.064612 | 0.25509 | 0.064741 | 0.00020172 | 0.00012868 | 0.38366 | 0.38366 | 0.38366 | 0.98924 | -0.20564 | 0.99009 | -0.18918 | 35.1338
31 | 0.028091 | 0.0070426 | -0.028086 | -0.0070399 | 4.3463e-06 | 2.6988e-06 | 0.042318 | 0.042318 | 0.042318 | 0.98778 | -0.23384 | 0.98761 | -0.23709 | 11.6258
32 | -0.29658 | -0.07514 | 0.297 | 0.075412 | 0.00042493 | 0.0002713 | 0.44602 | 0.44602 | 0.44602 | 0.99009 | -0.18918 | 0.99164 | -0.15941 | 40.8444
33 | 0.01438 | 0.0036046 | -0.014377 | -0.0036032 | 2.445e-06 | 1.3871e-06 | 0.021666 | 0.021666 | 0.021666 | 0.98761 | -0.23709 | 0.98743 | -0.24066 | 5.9521
34 | -0.32108 | -0.081446 | 0.32162 | 0.081789 | 0.00053583 | 0.00034222 | 0.48215 | 0.48215 | 0.48215 | 0.99164 | -0.15941 | 0.99345 | -0.12476 | 44.1532
35 | 0.39265 | 0.10005 | -0.39156 | -0.099354 | 0.0010882 | 0.00069545 | 0.58681 | 0.58681 | 0.58681 | 0.99665 | -0.063547 | 0.99364 | -0.12116 | 53.7373
36 | 0.045996 | 0.011542 | -0.045973 | -0.011527 | 2.359e-05 | 1.4926e-05 | 0.068887 | 0.068887 | 0.068887 | 0.99364 | -0.12116 | 0.99308 | -0.13192 | 18.9249
37 | 0.34556 | 0.087813 | -0.3455 | -0.087774 | 5.9973e-05 | 3.8313e-05 | 0.51792 | 0.51792 | 0.51792 | 0.99364 | -0.12116 | 0.99345 | -0.12476 | 47.429
38 | 0.024002 | 0.0060205 | -0.023987 | -0.0060118 | 1.427e-05 | 8.7526e-06 | 0.035965 | 0.035966 | 0.035966 | 0.99308 | -0.13192 | 0.99243 | -0.1444 | 9.8807
39 | 0.0073314 | 0.0018374 | -0.0073313 | -0.0018374 | 1.1768e-07 | 4.1757e-08 | 0.010992 | 0.010992 | 0.010992 | 0.99243 | -0.1444 | 0.99242 | -0.14473 | 3.0199

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4443 | 0.11307

## res_load
| p_mw | q_mvar
0 | 0.0062055 | 0.0015552
1 | 0.011516 | 0.0028861
2 | 0.01162 | 0.0029122
3 | 0.017869 | 0.0044784
4 | 0.010069 | 0.0025236
5 | 0.012651 | 0.0031706
6 | 0.012873 | 0.0032262
7 | 0.012023 | 0.0030132
8 | 0.0099707 | 0.0024989
9 | 0.012383 | 0.0031036
10 | 0.0051815 | 0.0012986
11 | 0.012942 | 0.0032435
12 | 0.0040703 | 0.0010201
13 | 0.019507 | 0.004889
14 | 0.011614 | 0.0029107
15 | 0.0088291 | 0.0022128
16 | 0.0032418 | 0.00081247
17 | 0.0056893 | 0.0014259
18 | 0.019846 | 0.0049739
19 | 0.0074509 | 0.0018674
20 | 0.024057 | 0.0060294
21 | 0.023842 | 0.0059752
22 | 0.041494 | 0.010399
23 | 0.013707 | 0.0034353
24 | 0.024079 | 0.0060347
25 | 0.014377 | 0.0036032
26 | 0.010175 | 0.0025502
27 | 0.023883 | 0.0059856
28 | 0.021971 | 0.0055065
29 | 0.016656 | 0.0041744
30 | 0.0073313 | 0.0018374

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1