## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1201-35_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1201-35_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1201-35_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1201-35_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1201-35_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1201-35_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1201-35_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1201-35_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1201-35_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1201-35_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1201-35_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1201-35_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1201-35_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1201-35_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1201-35_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_1201-35_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1201-35_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1201-35_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1201-35_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1201-35_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1201-35_0_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_1201-35_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1201-35_0_4_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_1201-35_0_4_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_1201-35_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1201-35_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1201-35_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1201-35_0_4_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_1201-35_0_4_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_1201-35_0_4_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_1201-35_0_4_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_1201-35_0_4_node_59 | 0.4 | n |  | TRUE
32 | bus_LV_1201-35_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1201-35_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1201-35_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1201-35_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1201-35_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1201-35_0_4_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_1201-35_0_4_node_76 | 0.4 | n |  | TRUE
39 | bus_LV_1201-35_0_4_node_64 | 0.4 | n |  | TRUE
40 | bus_LV_1201-35_0_4_node_78 | 0.4 | n |  | TRUE
41 | bus_LV_1201-35_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_1201-35_0_4_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_1201-35_0_4_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_1201-35_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1201-35_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_1201-35_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_1201-35_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_1201-35_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_1201-35_0_4_node_68 | 0.4 | n |  | TRUE
50 | bus_LV_1201-35_0_4_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_1201-35_0_4_node_56 | 0.4 | n |  | TRUE
52 | bus_LV_1201-35_0_4_node_72 | 0.4 | n |  | TRUE
53 | bus_LV_1201-35_0_4_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_1201-35_0_4_node_80 | 0.4 | n |  | TRUE
55 | bus_LV_1201-35_0_4_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_1201-35_0_4_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_1201-35_0_4_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_1201-35_0_4_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_1201-35_0_4_node_82 | 0.4 | n |  | TRUE
60 | bus_LV_1201-35_0_4_node_81 | 0.4 | n |  | TRUE
61 | bus_LV_1201-35_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_1201-35_0_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_1201-35_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_1201-35_0_4_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_1201-35_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_1201-35_0_4_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_1201-35_0_4_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_1201-35_0_4_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_1201-35_0_4_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_1201-35_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_1201-35_0_4_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_1201-35_0_4_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_1201-35_0_4_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_1201-35_0_4_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_1201-35_0_4_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_1201-35_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_1201-35_0_4_node_71 | 0.4 | n |  | TRUE
78 | bus_LV_1201-35_0_4_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_1201-35_0_4_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_1201-35_0_4_node_83 | 0.4 | n |  | TRUE
81 | bus_MV_14_0_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1201-35_0_4_load_0 | 0 | 0.014754 | 0.0036977 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1201-35_0_4_load_1 | 1 | 0.0044727 | 0.001121 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1201-35_0_4_load_2 | 2 | 0.0092684 | 0.0023229 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1201-35_0_4_load_3 | 3 | 0.0033922 | 0.00085018 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1201-35_0_4_load_4 | 4 | 0.011003 | 0.0027576 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1201-35_0_4_load_5 | 5 | 0.0036023 | 0.00090283 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1201-35_0_4_load_6 | 7 | 0.0036577 | 0.0009167 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1201-35_0_4_load_18 | 8 | 0.0093347 | 0.0023395 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1201-35_0_4_load_7 | 9 | 0.0089772 | 0.0022499 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1201-35_0_4_load_9 | 11 | 0.0061325 | 0.0015369 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1201-35_0_4_load_10 | 12 | 0.0047484 | 0.0011901 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1201-35_0_4_load_20 | 13 | 0.0046201 | 0.0011579 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1201-35_0_4_load_19 | 14 | 0.009512 | 0.0023839 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1201-35_0_4_load_11 | 15 | 0.0069861 | 0.0017509 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1201-35_0_4_load_15 | 18 | 0.01413 | 0.0035412 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1201-35_0_4_load_16 | 19 | 0.0054873 | 0.0013752 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1201-35_0_4_load_46 | 20 | 0.0049388 | 0.0012378 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1201-35_0_4_load_36 | 23 | 0.012214 | 0.003061 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1201-35_0_4_load_23 | 25 | 0.019757 | 0.0049516 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1201-35_0_4_load_22 | 26 | 0.0098751 | 0.0024749 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1201-35_0_4_load_57 | 27 | 0.0078213 | 0.0019602 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1201-35_0_4_load_58 | 29 | 0.016859 | 0.0042254 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1201-35_0_4_load_63 | 30 | 0.0049669 | 0.0012448 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1201-35_0_4_load_59 | 31 | 0.0085329 | 0.0021386 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1201-35_0_4_load_24 | 32 | 0.022811 | 0.005717 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1201-35_0_4_load_25 | 33 | 0.0074847 | 0.0018758 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1201-35_0_4_load_26 | 34 | 0.0084233 | 0.0021111 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1201-35_0_4_load_28 | 36 | 0.0084331 | 0.0021135 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1201-35_0_4_load_49 | 37 | 0.0039041 | 0.00097847 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1201-35_0_4_load_76 | 38 | 0.0083762 | 0.0020993 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1201-35_0_4_load_32 | 41 | 0.0061887 | 0.001551 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1201-35_0_4_load_48 | 42 | 0.0043391 | 0.0010875 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1201-35_0_4_load_75 | 43 | 0.0084081 | 0.0021073 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1201-35_0_4_load_29 | 44 | 0.015189 | 0.0038068 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1201-35_0_4_load_30 | 45 | 0.01544 | 0.0038695 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1201-35_0_4_load_34 | 48 | 0.0063338 | 0.0015874 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1201-35_0_4_load_73 | 50 | 0.0090657 | 0.0022721 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1201-35_0_4_load_56 | 51 | 0.00010555 | 2.6454e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1201-35_0_4_load_72 | 52 | 0.011825 | 0.0029636 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1201-35_0_4_load_77 | 53 | 0.019157 | 0.0048012 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1201-35_0_4_load_80 | 54 | 0.007292 | 0.0018275 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1201-35_0_4_load_37 | 55 | 0.026938 | 0.0067512 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1201-35_0_4_load_82 | 59 | 0.00067082 | 0.00016812 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1201-35_0_4_load_81 | 60 | 0.00052493 | 0.00013156 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1201-35_0_4_load_42 | 61 | 0.0094688 | 0.0023731 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1201-35_0_4_load_43 | 62 | 0.0079231 | 0.0019857 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1201-35_0_4_load_45 | 63 | 0.0078124 | 0.001958 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1201-35_0_4_load_47 | 64 | 0.0052296 | 0.0013107 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1201-35_0_4_load_52 | 65 | 0.0048072 | 0.0012048 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1201-35_0_4_load_51 | 67 | 0.0074633 | 0.0018705 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1201-35_0_4_load_65 | 68 | 0.0073992 | 0.0018544 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1201-35_0_4_load_66 | 69 | 0.0073786 | 0.0018492 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1201-35_0_4_load_53 | 70 | 0.0001354 | 3.3936e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1201-35_0_4_load_54 | 71 | 0.0006728 | 0.00016862 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1201-35_0_4_load_60 | 73 | 0.0132 | 0.0033083 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1201-35_0_4_load_74 | 75 | 0.0049799 | 0.0012481 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1201-35_0_4_load_70 | 76 | 0.0049794 | 0.001248 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1201-35_0_4_load_71 | 77 | 0.0078237 | 0.0019608 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1201-35_0_4_load_67 | 79 | 0.017785 | 0.0044573 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1201-35_0_4_load_83 | 80 | 0.0068025 | 0.0017049 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1201-35_0_4_line_0 |  | 0 | 1 | 0.012652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1201-35_0_4_line_1 |  | 0 | 2 | 0.021248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1201-35_0_4_line_2 |  | 1 | 3 | 0.0057088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1201-35_0_4_line_3 |  | 2 | 4 | 0.004131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1201-35_0_4_line_4 |  | 3 | 5 | 0.006324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1201-35_0_4_line_5 |  | 4 | 6 | 0.016403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1201-35_0_4_line_6 |  | 5 | 7 | 0.0025651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1201-35_0_4_line_7 |  | 6 | 8 | 0.0083533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1201-35_0_4_line_8 |  | 7 | 9 | 1.1416e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1201-35_0_4_line_9 |  | 9 | 10 | 0.021066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1201-35_0_4_line_10 |  | 10 | 11 | 0.035834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1201-35_0_4_line_11 |  | 10 | 12 | 0.0064223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1201-35_0_4_line_12 |  | 11 | 13 | 0.019986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1201-35_0_4_line_13 |  | 13 | 14 | 0.0066159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1201-35_0_4_line_14 |  | 14 | 24 | 0.001674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1201-35_0_4_line_15 |  | 15 | 16 | 0.021638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1201-35_0_4_line_16 |  | 15 | 17 | 0.0061929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1201-35_0_4_line_17 |  | 16 | 18 | 0.019374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1201-35_0_4_line_18 |  | 17 | 19 | 0.035539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1201-35_0_4_line_19 |  | 18 | 20 | 0.022851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1201-35_0_4_line_20 |  | 19 | 21 | 0.020598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1201-35_0_4_line_21 |  | 20 | 22 | 0.015593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1201-35_0_4_line_22 |  | 21 | 23 | 0.047357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1201-35_0_4_line_23 |  | 22 | 64 | 0.004816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1201-35_0_4_line_24 |  | 22 | 61 | 0.012429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1201-35_0_4_line_25 |  | 23 | 54 | 0.02573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1201-35_0_4_line_26 |  | 24 | 25 | 0.026452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1201-35_0_4_line_27 |  | 25 | 28 | 0.010914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1201-35_0_4_line_28 |  | 26 | 27 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1201-35_0_4_line_29 |  | 27 | 29 | 0.0034999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1201-35_0_4_line_30 |  | 28 | 30 | 0.022825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1201-35_0_4_line_31 |  | 28 | 31 | 0.0035755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1201-35_0_4_line_32 |  | 29 | 63 | 0.012045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1201-35_0_4_line_33 |  | 30 | 76 | 0.015647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1201-35_0_4_line_34 |  | 32 | 33 | 0.014057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1201-35_0_4_line_35 |  | 32 | 34 | 0.001649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1201-35_0_4_line_36 |  | 33 | 35 | 0.015868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1201-35_0_4_line_37 |  | 34 | 36 | 0.015513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1201-35_0_4_line_38 |  | 35 | 37 | 0.01953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1201-35_0_4_line_39 |  | 36 | 38 | 0.015515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1201-35_0_4_line_40 |  | 37 | 42 | 0.016209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1201-35_0_4_line_41 |  | 38 | 43 | 0.015575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1201-35_0_4_line_42 |  | 39 | 40 | 0.028514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1201-35_0_4_line_43 |  | 39 | 41 | 0.0059903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1201-35_0_4_line_44 |  | 40 | 78 | 0.048359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1201-35_0_4_line_45 |  | 40 | 53 | 0.028275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1201-35_0_4_line_46 |  | 41 | 45 | 0.027556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1201-35_0_4_line_47 |  | 42 | 66 | 0.0015831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_1201-35_0_4_line_48 |  | 43 | 75 | 0.015653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_1201-35_0_4_line_49 |  | 44 | 45 | 0.015388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1201-35_0_4_line_50 |  | 44 | 46 | 0.0026978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1201-35_0_4_line_51 |  | 46 | 47 | 0.024762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1201-35_0_4_line_52 |  | 46 | 48 | 0.020001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1201-35_0_4_line_53 |  | 47 | 49 | 0.021854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1201-35_0_4_line_54 |  | 47 | 50 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1201-35_0_4_line_55 |  | 49 | 51 | 0.0083857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1201-35_0_4_line_56 |  | 50 | 52 | 0.034227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1201-35_0_4_line_57 |  | 51 | 71 | 0.023301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1201-35_0_4_line_58 |  | 52 | 74 | 0.0050897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_1201-35_0_4_line_59 |  | 55 | 56 | 0.020843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1201-35_0_4_line_60 |  | 56 | 57 | 0.017545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1201-35_0_4_line_61 |  | 57 | 58 | 0.019895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1201-35_0_4_line_62 |  | 58 | 59 | 0.089081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1201-35_0_4_line_63 |  | 59 | 60 | 0.021544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1201-35_0_4_line_64 |  | 60 | 72 | 0.085007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1201-35_0_4_line_65 |  | 61 | 62 | 0.029518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1201-35_0_4_line_66 |  | 62 | 63 | 0.015316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1201-35_0_4_line_67 |  | 64 | 65 | 0.014731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1201-35_0_4_line_68 |  | 65 | 66 | 0.017248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1201-35_0_4_line_69 |  | 66 | 67 | 0.016172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1201-35_0_4_line_70 |  | 67 | 68 | 0.015638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_1201-35_0_4_line_71 |  | 68 | 69 | 0.015567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_1201-35_0_4_line_72 |  | 69 | 79 | 0.0083291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_1201-35_0_4_line_73 |  | 70 | 71 | 0.010811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1201-35_0_4_line_74 |  | 70 | 72 | 0.077016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1201-35_0_4_line_75 |  | 73 | 74 | 0.0066543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1201-35_0_4_line_76 |  | 74 | 75 | 0.015648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_1201-35_0_4_line_77 |  | 76 | 77 | 0.015541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1201-35_0_4_line_78 |  | 77 | 79 | 0.0072488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_1201-35_0_4_line_79 |  | 78 | 80 | 0.041563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1201-35_0_4_trafo_71 | 0.63 MVA 20/0.4 kV | 81 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2692316.576 | 1192327.1335 | 2692308.1274 | 1192336.5519
1 | 2692316.576 | 1192327.1335 | 2692330.7639 | 1192311.3168
2 | 2692308.1274 | 1192336.5519 | 2692304.3154 | 1192340.8015
3 | 2692333.5223 | 1192308.2417 | 2692330.7639 | 1192311.3168
4 | 2692300.0926 | 1192345.5091 | 2692304.3154 | 1192340.8015
5 | 2692344.354 | 1192295.9246 | 2692337.7018 | 1192303.5824 | 2692333.5223 | 1192308.2417
6 | 2692300.0926 | 1192345.5091 | 2692298.3798 | 1192347.4186
7 | 2692344.354 | 1192295.9246 | 2692348.2254 | 1192297.5187 | 2692351.586 | 1192297.6261 | 2692352.3572 | 1192297.3982
8 | 2692298.3798 | 1192347.4186 | 2692298.3722 | 1192347.4271
9 | 2692284.3058 | 1192363.1082 | 2692298.3722 | 1192347.4271
10 | 2692284.3058 | 1192363.1082 | 2692310.5724 | 1192387.483
11 | 2692284.3058 | 1192363.1082 | 2692280.0977 | 1192367.9597
12 | 2692325.2222 | 1192401.0776 | 2692310.5724 | 1192387.483
13 | 2692325.2222 | 1192401.0776 | 2692330.0717 | 1192405.5779
14 | 2692331.2988 | 1192406.7166 | 2692330.0717 | 1192405.5779
15 | 2692398.5974 | 1192273.4251 | 2692411.6076 | 1192269.2677 | 2692419.3553 | 1192267.3592
16 | 2692425.3684 | 1192265.878 | 2692419.3553 | 1192267.3592
17 | 2692398.5974 | 1192273.4251 | 2692408.1462 | 1192290.2819
18 | 2692425.3684 | 1192265.878 | 2692459.8804 | 1192257.3949
19 | 2692408.1462 | 1192290.2819 | 2692419.3488 | 1192310.0579 | 2692419.4093 | 1192310.1647
20 | 2692479.8834 | 1192252.4782 | 2692459.8804 | 1192257.3949
21 | 2692427.0972 | 1192323.7308 | 2692419.4093 | 1192310.1647
22 | 2692479.8834 | 1192252.4782 | 2692483.9537 | 1192264.8713 | 2692483.6292 | 1192285.8575 | 2692483.0193 | 1192299.1678 | 2692483.0193 | 1192299.1678
23 | 2692427.0972 | 1192323.7308 | 2692429.3898 | 1192327.9661
24 | 2692427.0972 | 1192323.7308 | 2692420.525 | 1192329.1661 | 2692417.5184 | 1192331.6511
25 | 2692493.5573 | 1192322.6148 | 2692487.8934 | 1192311.3509 | 2692483.0193 | 1192299.1678
26 | 2692331.2988 | 1192406.7166 | 2692349.5809 | 1192425.8337
27 | 2692357.1239 | 1192433.7213 | 2692349.5809 | 1192425.8337
28 | 2692358.2816 | 1192382.4963 | 2692371.4556 | 1192370.6709
29 | 2692371.4556 | 1192370.6709 | 2692374.0601 | 1192368.333
30 | 2692357.1239 | 1192433.7213 | 2692363.2925 | 1192428.2463 | 2692374.196 | 1192418.5715
31 | 2692357.1239 | 1192433.7213 | 2692359.6235 | 1192436.278
32 | 2692383.0238 | 1192360.2869 | 2692374.0601 | 1192368.333
33 | 2692385.8995 | 1192408.1868 | 2692374.196 | 1192418.5715
34 | 2692452.838 | 1192397.9257 | 2692442.252 | 1192407.1738
35 | 2692441.0101 | 1192408.2586 | 2692442.252 | 1192407.1738
36 | 2692464.7891 | 1192387.4874 | 2692458.5213 | 1192392.9607 | 2692452.838 | 1192397.9257
37 | 2692441.0101 | 1192408.2586 | 2692429.327 | 1192418.4651
38 | 2692464.7891 | 1192387.4874 | 2692454.2311 | 1192371.0567
39 | 2692417.6424 | 1192428.6729 | 2692429.327 | 1192418.4651
40 | 2692445.4689 | 1192357.4207 | 2692454.2311 | 1192371.0567
41 | 2692417.6424 | 1192428.6729 | 2692405.9133 | 1192438.9195
42 | 2692457.4695 | 1192440.286 | 2692480.1027 | 1192457.7136
43 | 2692457.4695 | 1192440.286 | 2692453.7404 | 1192444.9741
44 | 2692480.1027 | 1192457.7136 | 2692502.1228 | 1192472.8748 | 2692513.3788 | 1192491.4163
45 | 2692480.1027 | 1192457.7136 | 2692463.0276 | 1192480.2198 | 2692463.0155 | 1192480.2409
46 | 2692453.7404 | 1192444.9741 | 2692436.5862 | 1192466.5393
47 | 2692444.613 | 1192356.0888 | 2692445.4689 | 1192357.4207
48 | 2692394.1248 | 1192449.218 | 2692405.9133 | 1192438.9195
49 | 2692427.0067 | 1192478.582 | 2692436.5862 | 1192466.5393
50 | 2692425.3272 | 1192480.6933 | 2692427.0067 | 1192478.582
51 | 2692425.3272 | 1192480.6933 | 2692413.7348 | 1192495.257 | 2692411.9815 | 1192501.1671
52 | 2692425.3272 | 1192480.6933 | 2692440.5733 | 1192493.6394
53 | 2692405.9238 | 1192522.1648 | 2692411.9815 | 1192501.1671
54 | 2692411.9815 | 1192501.1671 | 2692405.0405 | 1192493.4772 | 2692403.4508 | 1192489.7171
55 | 2692405.9238 | 1192522.1648 | 2692404.4986 | 1192527.0682 | 2692403.4681 | 1192530.1815
56 | 2692385.7073 | 1192463.3347 | 2692396.496 | 1192475.5782 | 2692394.9486 | 1192480.0016 | 2692401.8042 | 1192485.8223 | 2692403.4508 | 1192489.7171
57 | 2692403.4681 | 1192530.1815 | 2692396.8533 | 1192550.165 | 2692396.1405 | 1192552.3005
58 | 2692382.3424 | 1192459.516 | 2692385.7073 | 1192463.3347
59 | 2692209.7697 | 1192438.9303 | 2692196.3842 | 1192431.8529 | 2692192.3953 | 1192427.7785
60 | 2692225.2811 | 1192437.1793 | 2692222.314 | 1192435.2879 | 2692218.8879 | 1192434.4902 | 2692215.39 | 1192434.881 | 2692212.2328 | 1192436.4222 | 2692209.7697 | 1192438.9303
61 | 2692225.2811 | 1192437.1793 | 2692227.3376 | 1192439.7793 | 2692228.4558 | 1192442.9097 | 2692228.5269 | 1192446.2129 | 2692227.5403 | 1192449.3775 | 2692225.6004 | 1192452.0716 | 2692222.8945 | 1192454.0089
62 | 2692222.8945 | 1192454.0089 | 2692269.2082 | 1192530.1035
63 | 2692282.7286 | 1192546.866 | 2692271.1427 | 1192532.8588 | 2692269.2082 | 1192530.1035
64 | 2692337.1075 | 1192612.205 | 2692282.7286 | 1192546.866
65 | 2692417.5184 | 1192331.6511 | 2692394.7661 | 1192350.4561
66 | 2692383.0238 | 1192360.2869 | 2692384.7916 | 1192358.7001 | 2692394.7661 | 1192350.4561
67 | 2692436.4022 | 1192340.9205 | 2692429.3898 | 1192327.9661
68 | 2692444.613 | 1192356.0888 | 2692436.4022 | 1192340.9205
69 | 2692444.613 | 1192356.0888 | 2692437.8646 | 1192362.0773 | 2692432.5165 | 1192366.8227
70 | 2692420.8196 | 1192377.2016 | 2692432.5165 | 1192366.8227
71 | 2692420.8196 | 1192377.2016 | 2692409.1759 | 1192387.5333
72 | 2692409.1759 | 1192387.5333 | 2692402.9458 | 1192393.0613
73 | 2692392.7176 | 1192562.5548 | 2692396.1405 | 1192552.3005
74 | 2692337.1075 | 1192612.205 | 2692350.5271 | 1192608.1428 | 2692358.797 | 1192601.8553 | 2692375.7633 | 1192587.33 | 2692382.5591 | 1192580.2304 | 2692391.9131 | 1192564.9649 | 2692392.7176 | 1192562.5548
75 | 2692382.3424 | 1192459.516 | 2692377.6905 | 1192454.7579
76 | 2692382.3424 | 1192459.516 | 2692387.2267 | 1192455.2442 | 2692394.1248 | 1192449.218
77 | 2692385.8995 | 1192408.1868 | 2692397.5237 | 1192397.8724
78 | 2692397.5237 | 1192397.8724 | 2692402.9458 | 1192393.0613
79 | 2692513.3788 | 1192491.4163 | 2692476.9813 | 1192511.6668

## bus_geodata
| x | y | coords
0 | 2692316.576 | 1192327.1335
1 | 2692308.1274 | 1192336.5519
2 | 2692330.7639 | 1192311.3168
3 | 2692304.3154 | 1192340.8015
4 | 2692333.5223 | 1192308.2417
5 | 2692300.0926 | 1192345.5091
6 | 2692344.354 | 1192295.9246
7 | 2692298.3798 | 1192347.4186
8 | 2692352.3572 | 1192297.3981
9 | 2692298.3722 | 1192347.4271
10 | 2692284.3058 | 1192363.1082
11 | 2692310.5724 | 1192387.483
12 | 2692280.0977 | 1192367.9597
13 | 2692325.2222 | 1192401.0776
14 | 2692330.0717 | 1192405.5779
15 | 2692419.3553 | 1192267.3592
16 | 2692398.5974 | 1192273.4251
17 | 2692425.3684 | 1192265.878
18 | 2692408.1462 | 1192290.2819
19 | 2692459.8804 | 1192257.3949
20 | 2692419.4093 | 1192310.1647
21 | 2692479.8834 | 1192252.4782
22 | 2692427.0972 | 1192323.7308
23 | 2692483.0193 | 1192299.1678
24 | 2692331.2988 | 1192406.7166
25 | 2692349.5809 | 1192425.8337
26 | 2692358.2816 | 1192382.4963
27 | 2692371.4556 | 1192370.671
28 | 2692357.1239 | 1192433.7213
29 | 2692374.0601 | 1192368.333
30 | 2692374.196 | 1192418.5715
31 | 2692359.6235 | 1192436.278
32 | 2692442.252 | 1192407.1738
33 | 2692452.8381 | 1192397.9257
34 | 2692441.0101 | 1192408.2586
35 | 2692464.7891 | 1192387.4874
36 | 2692429.327 | 1192418.4651
37 | 2692454.2311 | 1192371.0567
38 | 2692417.6424 | 1192428.6729
39 | 2692457.4695 | 1192440.286
40 | 2692480.1027 | 1192457.7136
41 | 2692453.7404 | 1192444.9741
42 | 2692445.4689 | 1192357.4207
43 | 2692405.9133 | 1192438.9196
44 | 2692427.0067 | 1192478.582
45 | 2692436.5862 | 1192466.5393
46 | 2692425.3272 | 1192480.6933
47 | 2692411.9815 | 1192501.1671
48 | 2692440.5733 | 1192493.6394
49 | 2692405.9238 | 1192522.1648
50 | 2692403.4508 | 1192489.7171
51 | 2692403.4681 | 1192530.1815
52 | 2692385.7073 | 1192463.3347
53 | 2692463.0155 | 1192480.2409
54 | 2692493.5573 | 1192322.6148
55 | 2692192.3953 | 1192427.7785
56 | 2692209.7697 | 1192438.9303
57 | 2692225.2811 | 1192437.1793
58 | 2692222.8945 | 1192454.0089
59 | 2692269.2082 | 1192530.1035
60 | 2692282.7286 | 1192546.866
61 | 2692417.5184 | 1192331.6511
62 | 2692394.7661 | 1192350.4561
63 | 2692383.0238 | 1192360.2869
64 | 2692429.3898 | 1192327.9661
65 | 2692436.4022 | 1192340.9205
66 | 2692444.613 | 1192356.0888
67 | 2692432.5165 | 1192366.8227
68 | 2692420.8196 | 1192377.2016
69 | 2692409.1759 | 1192387.5333
70 | 2692392.7176 | 1192562.5548
71 | 2692396.1405 | 1192552.3005
72 | 2692337.1075 | 1192612.205
73 | 2692377.6905 | 1192454.7579
74 | 2692382.3424 | 1192459.516
75 | 2692394.1248 | 1192449.218
76 | 2692385.8995 | 1192408.1868
77 | 2692397.5237 | 1192397.8724
78 | 2692513.3788 | 1192491.4163
79 | 2692402.9458 | 1192393.0613
80 | 2692476.9813 | 1192511.6668
81 | 2692357.1239 | 1192433.7213

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98324 | -0.32255 | 0.014754 | 0.0036977
1 | 0.98376 | -0.31243 | 0.0044727 | 0.001121
2 | 0.98266 | -0.33389 | 0.0092684 | 0.0023229
3 | 0.98402 | -0.30741 | 0.0033922 | 0.00085018
4 | 0.98259 | -0.33541 | 0.011003 | 0.0027576
5 | 0.98432 | -0.30147 | 0.0036023 | 0.00090283
6 | 0.98245 | -0.33818 | 0 | 0
7 | 0.98446 | -0.29889 | 0.0036577 | 0.0009167
8 | 0.98237 | -0.33958 | 0.0093347 | 0.0023395
9 | 0.98446 | -0.29888 | 0.0089772 | 0.0022499
10 | 0.98579 | -0.27298 | 0 | 0
11 | 0.98821 | -0.22604 | 0.0061325 | 0.0015369
12 | 0.98576 | -0.27353 | 0.0047484 | 0.0011901
13 | 0.98967 | -0.19778 | 0.0046201 | 0.0011579
14 | 0.99018 | -0.1879 | 0.009512 | 0.0023839
15 | 0.98647 | -0.25964 | 0.0069861 | 0.0017509
16 | 0.9871 | -0.24726 | 0 | 0
17 | 0.98633 | -0.26242 | 0 | 0
18 | 0.98768 | -0.23618 | 0.01413 | 0.0035412
19 | 0.98551 | -0.27834 | 0.0054873 | 0.0013752
20 | 0.98864 | -0.21737 | 0.0049388 | 0.0012378
21 | 0.98514 | -0.28556 | 0 | 0
22 | 0.98938 | -0.20318 | 0 | 0
23 | 0.98429 | -0.30216 | 0.012214 | 0.003061
24 | 0.99032 | -0.18511 | 0 | 0
25 | 0.9926 | -0.14127 | 0.019757 | 0.0049516
26 | 0.98613 | -0.26623 | 0.0098751 | 0.0024749
27 | 0.98629 | -0.2631 | 0.0078213 | 0.0019602
28 | 0.99374 | -0.11943 | 0 | 0
29 | 0.98635 | -0.26199 | 0.016859 | 0.0042254
30 | 0.99629 | -0.070502 | 0.0049669 | 0.0012448
31 | 0.99371 | -0.11997 | 0.0085329 | 0.0021386
32 | 0.98919 | -0.20626 | 0.022811 | 0.005717
33 | 0.99003 | -0.19011 | 0.0074847 | 0.0018758
34 | 0.98911 | -0.20793 | 0.0084233 | 0.0021111
35 | 0.99102 | -0.1712 | 0 | 0
36 | 0.98833 | -0.22291 | 0.0084331 | 0.0021135
37 | 0.99223 | -0.14798 | 0.0039041 | 0.00097847
38 | 0.98759 | -0.23714 | 0.0083762 | 0.0020993
39 | 0.97728 | -0.43773 | 0 | 0
40 | 0.97659 | -0.45125 | 0 | 0
41 | 0.97742 | -0.43489 | 0.0061887 | 0.001551
42 | 0.99325 | -0.12839 | 0.0043391 | 0.0010875
43 | 0.98689 | -0.25066 | 0.0084081 | 0.0021073
44 | 0.97892 | -0.40541 | 0.015189 | 0.0038068
45 | 0.97824 | -0.41874 | 0.01544 | 0.0038695
46 | 0.97908 | -0.40233 | 0 | 0
47 | 0.98067 | -0.37126 | 0 | 0
48 | 0.97896 | -0.40464 | 0.0063338 | 0.0015874
49 | 0.98007 | -0.38278 | 0 | 0
50 | 0.98199 | -0.3456 | 0.0090657 | 0.0022721
51 | 0.97985 | -0.3872 | 0.00010555 | 2.6454e-05
52 | 0.9854 | -0.27948 | 0.011825 | 0.0029636
53 | 0.97609 | -0.46115 | 0.019157 | 0.0048012
54 | 0.98411 | -0.30554 | 0.007292 | 0.0018275
55 | 0.97041 | -0.57243 | 0.026938 | 0.0067512
56 | 0.97093 | -0.56204 | 0 | 0
57 | 0.97137 | -0.55331 | 0 | 0
58 | 0.97187 | -0.54341 | 0 | 0
59 | 0.97411 | -0.49923 | 0.00067082 | 0.00016812
60 | 0.97467 | -0.48831 | 0.00052493 | 0.00013156
61 | 0.98869 | -0.21642 | 0.0094688 | 0.0023731
62 | 0.98733 | -0.24292 | 0.0079231 | 0.0019857
63 | 0.98673 | -0.25453 | 0.0078124 | 0.001958
64 | 0.98987 | -0.19368 | 0.0052296 | 0.0013107
65 | 0.99144 | -0.16332 | 0.0048072 | 0.0012048
66 | 0.99335 | -0.12643 | 0 | 0
67 | 0.995 | -0.095035 | 0.0074633 | 0.0018705
68 | 0.99662 | -0.064089 | 0.0073992 | 0.0018544
69 | 0.99827 | -0.032713 | 0.0073786 | 0.0018492
70 | 0.97893 | -0.40502 | 0.0001354 | 3.3936e-05
71 | 0.97922 | -0.39946 | 0.0006728 | 0.00016862
72 | 0.97691 | -0.44452 | 0 | 0
73 | 0.9855 | -0.27744 | 0.0132 | 0.0033083
74 | 0.98559 | -0.27586 | 0 | 0
75 | 0.98623 | -0.26349 | 0.0049799 | 0.0012481
76 | 0.99812 | -0.035745 | 0.0049794 | 0.001248
77 | 1 | 0 | -0.51026 | -0.13002
78 | 0.97628 | -0.45727 | 0 | 0
79 | 0.99918 | -0.015609 | 0.017785 | 0.0044573
80 | 0.97602 | -0.46244 | 0.0068025 | 0.0017049
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.04438 | -0.011129 | 0.044401 | 0.011143 | 2.1404e-05 | 1.3538e-05 | 0.067165 | 0.067165 | 0.067165 | 0.98324 | -0.32255 | 0.98376 | -0.31243 | 18.452
1 | 0.029626 | 0.0074318 | -0.02961 | -0.0074218 | 1.6018e-05 | 9.9824e-06 | 0.044837 | 0.044837 | 0.044837 | 0.98324 | -0.32255 | 0.98266 | -0.33389 | 12.3179
2 | -0.048874 | -0.012264 | 0.048885 | 0.012271 | 1.1701e-05 | 7.4162e-06 | 0.073931 | 0.073931 | 0.073931 | 0.98376 | -0.31243 | 0.98402 | -0.30741 | 20.3106
3 | 0.020341 | 0.0050989 | -0.02034 | -0.005098 | 1.4698e-06 | 8.8833e-07 | 0.030802 | 0.030802 | 0.030802 | 0.98266 | -0.33389 | 0.98259 | -0.33541 | 8.4622
4 | -0.052278 | -0.013122 | 0.052292 | 0.013131 | 1.4823e-05 | 9.4065e-06 | 0.07906 | 0.07906 | 0.07906 | 0.98402 | -0.30741 | 0.98432 | -0.30147 | 21.7198
5 | 0.0093366 | 0.0023404 | -0.0093353 | -0.0023398 | 1.2297e-06 | 5.7929e-07 | 0.014139 | 0.014139 | 0.014139 | 0.98259 | -0.33541 | 0.98245 | -0.33818 | 3.8844
6 | -0.055895 | -0.014034 | 0.055902 | 0.014038 | 6.8694e-06 | 4.3638e-06 | 0.084506 | 0.084506 | 0.084506 | 0.98432 | -0.30147 | 0.98446 | -0.29889 | 23.2159
7 | 0.0093353 | 0.0023398 | -0.0093347 | -0.0023395 | 6.2625e-07 | 2.9503e-07 | 0.014139 | 0.014139 | 0.014139 | 0.98245 | -0.33818 | 0.98237 | -0.33958 | 3.8845
8 | -0.059559 | -0.014955 | 0.059559 | 0.014955 | 3.4702e-08 | 2.2066e-08 | 0.090034 | 0.090034 | 0.090034 | 0.98446 | -0.29889 | 0.98446 | -0.29888 | 24.7347
9 | -0.068536 | -0.017205 | 0.068621 | 0.017259 | 8.4792e-05 | 5.3999e-05 | 0.1036 | 0.1036 | 0.1036 | 0.98446 | -0.29888 | 0.98579 | -0.27298 | 28.4625
10 | -0.07337 | -0.018449 | 0.073535 | 0.018554 | 0.00016488 | 0.00010507 | 0.11077 | 0.11077 | 0.11077 | 0.98579 | -0.27298 | 0.98821 | -0.22604 | 30.4316
11 | 0.0047485 | 0.0011901 | -0.0047484 | -0.0011901 | 1.2373e-07 | -2.6863e-09 | 0.0071677 | 0.0071678 | 0.0071678 | 0.98579 | -0.27298 | 0.98576 | -0.27353 | 1.9692
12 | -0.079667 | -0.020091 | 0.079775 | 0.02016 | 0.00010793 | 6.882e-05 | 0.12001 | 0.12001 | 0.12001 | 0.98821 | -0.22604 | 0.98967 | -0.19778 | 32.9684
13 | -0.084395 | -0.021318 | 0.084435 | 0.021343 | 3.9985e-05 | 2.5505e-05 | 0.12695 | 0.12695 | 0.12695 | 0.98967 | -0.19778 | 0.99018 | -0.1879 | 34.8768
14 | -0.093947 | -0.023727 | 0.09396 | 0.023735 | 1.2524e-05 | 7.9939e-06 | 0.14125 | 0.14125 | 0.14125 | 0.99018 | -0.1879 | 0.99032 | -0.18511 | 38.8038
15 | -0.032025 | -0.0080422 | 0.032044 | 0.0080541 | 1.8939e-05 | 1.1845e-05 | 0.048313 | 0.048313 | 0.048313 | 0.98647 | -0.25964 | 0.9871 | -0.24726 | 13.2727
16 | 0.025039 | 0.0062913 | -0.025035 | -0.0062893 | 3.3138e-06 | 2.0418e-06 | 0.037775 | 0.037775 | 0.037775 | 0.98647 | -0.25964 | 0.98633 | -0.26242 | 10.3777
17 | -0.032044 | -0.0080541 | 0.032061 | 0.0080647 | 1.6957e-05 | 1.0605e-05 | 0.048313 | 0.048313 | 0.048313 | 0.9871 | -0.24726 | 0.98768 | -0.23618 | 13.2727
18 | 0.025035 | 0.0062893 | -0.025016 | -0.0062776 | 1.9017e-05 | 1.1718e-05 | 0.037775 | 0.037775 | 0.037775 | 0.98633 | -0.26242 | 0.98551 | -0.27834 | 10.3777
19 | -0.04619 | -0.011606 | 0.046232 | 0.011632 | 4.151e-05 | 2.6274e-05 | 0.0696 | 0.0696 | 0.0696 | 0.98768 | -0.23618 | 0.98864 | -0.21737 | 19.1208
20 | 0.019529 | 0.0049023 | -0.019522 | -0.0048983 | 6.7174e-06 | 4.0368e-06 | 0.02949 | 0.02949 | 0.02949 | 0.98551 | -0.27834 | 0.98514 | -0.28556 | 8.1016
21 | -0.05117 | -0.01287 | 0.051205 | 0.012892 | 3.4699e-05 | 2.2007e-05 | 0.077033 | 0.077033 | 0.077033 | 0.98864 | -0.21737 | 0.98938 | -0.20318 | 21.163
22 | 0.019522 | 0.0048983 | -0.019507 | -0.004889 | 1.5444e-05 | 9.2818e-06 | 0.02949 | 0.02949 | 0.02949 | 0.98514 | -0.28556 | 0.98429 | -0.30216 | 8.1016
23 | -0.1111 | -0.027957 | 0.11116 | 0.02799 | 5.0453e-05 | 3.2228e-05 | 0.16714 | 0.16714 | 0.16714 | 0.98938 | -0.20318 | 0.98987 | -0.19368 | 45.9178
24 | 0.0599 | 0.015066 | -0.059862 | -0.015041 | 3.7844e-05 | 2.4061e-05 | 0.090108 | 0.090108 | 0.090108 | 0.98938 | -0.20318 | 0.98869 | -0.21642 | 24.7549
25 | 0.0072931 | 0.001828 | -0.007292 | -0.0018275 | 1.1729e-06 | 4.2371e-07 | 0.011026 | 0.011026 | 0.011026 | 0.98429 | -0.30216 | 0.98411 | -0.30554 | 3.029
26 | -0.09396 | -0.023735 | 0.094158 | 0.023861 | 0.0001979 | 0.00012631 | 0.14125 | 0.14125 | 0.14125 | 0.99032 | -0.18511 | 0.9926 | -0.14127 | 38.8038
27 | -0.11391 | -0.028813 | 0.11403 | 0.028889 | 0.00011948 | 7.6328e-05 | 0.17086 | 0.17086 | 0.17086 | 0.9926 | -0.14127 | 0.99374 | -0.11943 | 46.9405
28 | -0.0098751 | -0.0024749 | 0.0098765 | 0.0024756 | 1.474e-06 | 7.1747e-07 | 0.014901 | 0.014901 | 0.014901 | 0.98613 | -0.26623 | 0.98629 | -0.2631 | 4.0936
29 | -0.017698 | -0.0044358 | 0.017699 | 0.0044364 | 9.357e-07 | 5.5418e-07 | 0.026701 | 0.026701 | 0.026701 | 0.98629 | -0.2631 | 0.98635 | -0.26199 | 7.3354
30 | -0.12257 | -0.031028 | 0.12286 | 0.031212 | 0.00028865 | 0.00018444 | 0.18364 | 0.18364 | 0.18364 | 0.99374 | -0.11943 | 0.99629 | -0.070502 | 50.4508
31 | 0.0085332 | 0.0021387 | -0.0085329 | -0.0021386 | 2.1891e-07 | 9.3779e-08 | 0.012778 | 0.012778 | 0.012778 | 0.99374 | -0.11943 | 0.99371 | -0.11997 | 3.5103
32 | -0.034558 | -0.0086618 | 0.03457 | 0.0086695 | 1.2277e-05 | 7.7037e-06 | 0.052135 | 0.052135 | 0.052135 | 0.98635 | -0.26199 | 0.98673 | -0.25453 | 14.3228
33 | -0.12782 | -0.032457 | 0.12804 | 0.032594 | 0.00021418 | 0.00013687 | 0.19106 | 0.19106 | 0.19106 | 0.99629 | -0.070502 | 0.99812 | -0.035745 | 52.4888
34 | -0.19513 | -0.04946 | 0.19529 | 0.049556 | 0.0001516 | 9.6483e-05 | 0.29373 | 0.29373 | 0.29373 | 0.98919 | -0.20626 | 0.99003 | -0.19011 | 26.8987
35 | 0.17232 | 0.043743 | -0.17231 | -0.043734 | 1.3872e-05 | 8.8144e-06 | 0.25942 | 0.25942 | 0.25942 | 0.98919 | -0.20626 | 0.98911 | -0.20793 | 23.7564
36 | -0.20277 | -0.051432 | 0.20296 | 0.051549 | 0.00018449 | 0.00011746 | 0.30498 | 0.30498 | 0.30498 | 0.99003 | -0.19011 | 0.99102 | -0.1712 | 27.9288
37 | 0.16389 | 0.041623 | -0.16377 | -0.041548 | 0.00011807 | 7.4965e-05 | 0.24675 | 0.24675 | 0.24675 | 0.98911 | -0.20793 | 0.98833 | -0.22291 | 22.596
38 | -0.20296 | -0.051549 | 0.20318 | 0.051694 | 0.00022708 | 0.00014457 | 0.30498 | 0.30498 | 0.30498 | 0.99102 | -0.1712 | 0.99223 | -0.14798 | 27.9288
39 | 0.15534 | 0.039434 | -0.15523 | -0.039367 | 0.00010624 | 6.7399e-05 | 0.23405 | 0.23405 | 0.23405 | 0.98833 | -0.22291 | 0.98759 | -0.23714 | 21.4333
40 | -0.20709 | -0.052673 | 0.20728 | 0.052797 | 0.00019576 | 0.00012466 | 0.31084 | 0.31084 | 0.31084 | 0.99223 | -0.14798 | 0.99325 | -0.12839 | 28.465
41 | 0.14685 | 0.037268 | -0.14676 | -0.037207 | 9.5456e-05 | 6.0494e-05 | 0.22143 | 0.22143 | 0.22143 | 0.98759 | -0.23714 | 0.98689 | -0.25066 | 20.2776
42 | 0.025989 | 0.0065231 | -0.025972 | -0.0065127 | 1.6747e-05 | 1.0361e-05 | 0.039575 | 0.039575 | 0.039575 | 0.97728 | -0.43773 | 0.97659 | -0.45125 | 10.8722
43 | -0.025989 | -0.0065231 | 0.025992 | 0.0065252 | 3.5181e-06 | 2.1765e-06 | 0.039575 | 0.039575 | 0.039575 | 0.97728 | -0.43773 | 0.97742 | -0.43489 | 10.8721
44 | 0.0068061 | 0.0017061 | -0.0068041 | -0.0017054 | 1.9503e-06 | 6.4333e-07 | 0.01037 | 0.010371 | 0.010371 | 0.97659 | -0.45125 | 0.97628 | -0.45727 | 2.8491
45 | 0.019166 | 0.0048067 | -0.019157 | -0.0048012 | 9.0433e-06 | 5.4341e-06 | 0.029204 | 0.029204 | 0.029204 | 0.97659 | -0.45125 | 0.97609 | -0.46115 | 8.0232
46 | -0.032181 | -0.0080763 | 0.032206 | 0.0080918 | 2.4807e-05 | 1.5531e-05 | 0.048996 | 0.048996 | 0.048996 | 0.97742 | -0.43489 | 0.97824 | -0.41874 | 13.4605
47 | -0.21162 | -0.053885 | 0.21164 | 0.053897 | 1.9928e-05 | 1.2693e-05 | 0.31734 | 0.31734 | 0.31734 | 0.99325 | -0.12839 | 0.99335 | -0.12643 | 29.0602
48 | 0.13835 | 0.0351 | -0.13826 | -0.035046 | 8.5268e-05 | 5.3972e-05 | 0.20875 | 0.20875 | 0.20875 | 0.98689 | -0.25066 | 0.98623 | -0.26349 | 19.1166
49 | 0.047676 | 0.011981 | -0.047646 | -0.011961 | 3.0316e-05 | 1.9209e-05 | 0.072481 | 0.072481 | 0.072481 | 0.97892 | -0.40541 | 0.97824 | -0.41874 | 19.9125
50 | -0.062865 | -0.015787 | 0.062874 | 0.015793 | 9.2403e-06 | 5.8799e-06 | 0.09557 | 0.09557 | 0.09557 | 0.97892 | -0.40541 | 0.97908 | -0.40233 | 26.2555
51 | -0.069209 | -0.017381 | 0.069312 | 0.017446 | 0.00010276 | 6.5455e-05 | 0.1052 | 0.1052 | 0.1052 | 0.97908 | -0.40233 | 0.98067 | -0.37126 | 28.9003
52 | 0.0063345 | 0.0015876 | -0.0063338 | -0.0015874 | 6.9518e-07 | 1.9341e-07 | 0.0096273 | 0.0096274 | 0.0096274 | 0.97908 | -0.40233 | 0.97896 | -0.40464 | 2.6449
53 | 0.029316 | 0.0074472 | -0.0293 | -0.007437 | 1.6242e-05 | 1.012e-05 | 0.044519 | 0.044519 | 0.044519 | 0.98067 | -0.37126 | 0.98007 | -0.38278 | 12.2305
54 | -0.098628 | -0.024893 | 0.098749 | 0.024971 | 0.00012139 | 7.7506e-05 | 0.14972 | 0.14972 | 0.14972 | 0.98067 | -0.37126 | 0.98199 | -0.3456 | 41.1307
55 | 0.0293 | 0.007437 | -0.029294 | -0.0074332 | 6.2324e-06 | 3.8831e-06 | 0.044519 | 0.044519 | 0.044519 | 0.98007 | -0.38278 | 0.97985 | -0.3872 | 12.2305
56 | -0.10781 | -0.027243 | 0.10816 | 0.027462 | 0.00034291 | 0.00021903 | 0.16345 | 0.16345 | 0.16345 | 0.98199 | -0.3456 | 0.9854 | -0.27948 | 44.9047
57 | 0.029188 | 0.0074067 | -0.029171 | -0.007396 | 1.7194e-05 | 1.0711e-05 | 0.044359 | 0.044359 | 0.044359 | 0.97985 | -0.3872 | 0.97922 | -0.39946 | 12.1865
58 | -0.11998 | -0.030426 | 0.12 | 0.030439 | 2.0914e-05 | 1.3191e-05 | 0.18131 | 0.18131 | 0.18131 | 0.9854 | -0.27948 | 0.98559 | -0.27586 | 16.6034
59 | -0.026938 | -0.0067512 | 0.026951 | 0.0067595 | 1.3336e-05 | 8.2773e-06 | 0.041306 | 0.041306 | 0.041306 | 0.97041 | -0.57243 | 0.97093 | -0.56204 | 11.3478
60 | -0.026951 | -0.0067595 | 0.026962 | 0.0067664 | 1.1226e-05 | 6.9673e-06 | 0.041306 | 0.041306 | 0.041306 | 0.97093 | -0.56204 | 0.97137 | -0.55331 | 11.3478
61 | -0.026962 | -0.0067664 | 0.026975 | 0.0067743 | 1.2729e-05 | 7.9002e-06 | 0.041306 | 0.041306 | 0.041306 | 0.97137 | -0.55331 | 0.97187 | -0.54341 | 11.3477
62 | -0.026975 | -0.0067743 | 0.027032 | 0.0068097 | 5.6994e-05 | 3.537e-05 | 0.041306 | 0.041305 | 0.041306 | 0.97187 | -0.54341 | 0.97411 | -0.49923 | 11.3477
63 | -0.027703 | -0.0069778 | 0.027717 | 0.0069868 | 1.4477e-05 | 8.9966e-06 | 0.04233 | 0.04233 | 0.04233 | 0.97411 | -0.49923 | 0.97467 | -0.48831 | 11.6291
64 | -0.028242 | -0.0071184 | 0.028301 | 0.0071553 | 5.9302e-05 | 3.6891e-05 | 0.043131 | 0.043131 | 0.043131 | 0.97467 | -0.48831 | 0.97691 | -0.44452 | 11.8493
65 | 0.050393 | 0.012668 | -0.050329 | -0.012628 | 6.3695e-05 | 4.0387e-05 | 0.075857 | 0.075857 | 0.075857 | 0.98869 | -0.21642 | 0.98733 | -0.24292 | 20.8399
66 | 0.042406 | 0.010642 | -0.042383 | -0.010627 | 2.3464e-05 | 1.4821e-05 | 0.063916 | 0.063916 | 0.063916 | 0.98733 | -0.24292 | 0.98673 | -0.25453 | 17.5594
67 | -0.11638 | -0.0293 | 0.11655 | 0.029408 | 0.00016918 | 0.00010808 | 0.175 | 0.175 | 0.175 | 0.98987 | -0.19368 | 0.99144 | -0.16332 | 48.0775
68 | -0.12136 | -0.030613 | 0.12158 | 0.03075 | 0.00021476 | 0.00013722 | 0.18222 | 0.18222 | 0.18222 | 0.99144 | -0.16332 | 0.99335 | -0.12643 | 50.0596
69 | -0.33322 | -0.084648 | 0.33372 | 0.08497 | 0.00050448 | 0.00032224 | 0.49955 | 0.49955 | 0.49955 | 0.99335 | -0.12643 | 0.995 | -0.095035 | 45.7467
70 | -0.34119 | -0.086841 | 0.3417 | 0.087166 | 0.00050985 | 0.00032569 | 0.51072 | 0.51072 | 0.51072 | 0.995 | -0.095035 | 0.99662 | -0.064089 | 46.7688
71 | -0.34909 | -0.089021 | 0.34962 | 0.089359 | 0.00052972 | 0.00033841 | 0.52176 | 0.52176 | 0.52176 | 0.99662 | -0.064089 | 0.99827 | -0.032713 | 47.7804
72 | -0.357 | -0.091208 | 0.3573 | 0.091397 | 0.00029551 | 0.0001888 | 0.53276 | 0.53276 | 0.53276 | 0.99827 | -0.032713 | 0.99918 | -0.015609 | 48.7876
73 | -0.028491 | -0.0072226 | 0.028498 | 0.0072274 | 7.6135e-06 | 4.7367e-06 | 0.043336 | 0.043336 | 0.043336 | 0.97893 | -0.40502 | 0.97922 | -0.39946 | 11.9056
74 | 0.028355 | 0.0071887 | -0.028301 | -0.0071553 | 5.3727e-05 | 3.3419e-05 | 0.043131 | 0.043131 | 0.043131 | 0.97893 | -0.40502 | 0.97691 | -0.44452 | 11.8492
75 | -0.0132 | -0.0033083 | 0.013201 | 0.0033089 | 9.913e-07 | 5.4964e-07 | 0.019931 | 0.019931 | 0.019931 | 0.9855 | -0.27744 | 0.98559 | -0.27586 | 5.4756
76 | -0.13321 | -0.033748 | 0.13328 | 0.033798 | 7.9216e-05 | 5.0099e-05 | 0.20124 | 0.20124 | 0.20124 | 0.98559 | -0.27586 | 0.98623 | -0.26349 | 18.4286
77 | -0.13302 | -0.033842 | 0.13325 | 0.033989 | 0.00022958 | 0.00014673 | 0.19848 | 0.19848 | 0.19848 | 0.99812 | -0.035745 | 1 | 0 | 54.5281
78 | 0.37537 | 0.096035 | -0.37508 | -0.095854 | 0.00028339 | 0.00018108 | 0.55925 | 0.55925 | 0.55925 | 1 | 0 | 0.99918 | -0.015609 | 51.213
79 | 0.0068041 | 0.0017054 | -0.0068025 | -0.0017049 | 1.6763e-06 | 5.5327e-07 | 0.010371 | 0.010371 | 0.010371 | 0.97628 | -0.45727 | 0.97602 | -0.46244 | 2.8491

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51809 | 0.13199

## res_load
| p_mw | q_mvar
0 | 0.014754 | 0.0036977
1 | 0.0044727 | 0.001121
2 | 0.0092684 | 0.0023229
3 | 0.0033922 | 0.00085018
4 | 0.011003 | 0.0027576
5 | 0.0036023 | 0.00090283
6 | 0.0036577 | 0.0009167
7 | 0.0093347 | 0.0023395
8 | 0.0089772 | 0.0022499
9 | 0.0061325 | 0.0015369
10 | 0.0047484 | 0.0011901
11 | 0.0046201 | 0.0011579
12 | 0.009512 | 0.0023839
13 | 0.0069861 | 0.0017509
14 | 0.01413 | 0.0035412
15 | 0.0054873 | 0.0013752
16 | 0.0049388 | 0.0012378
17 | 0.012214 | 0.003061
18 | 0.019757 | 0.0049516
19 | 0.0098751 | 0.0024749
20 | 0.0078213 | 0.0019602
21 | 0.016859 | 0.0042254
22 | 0.0049669 | 0.0012448
23 | 0.0085329 | 0.0021386
24 | 0.022811 | 0.005717
25 | 0.0074847 | 0.0018758
26 | 0.0084233 | 0.0021111
27 | 0.0084331 | 0.0021135
28 | 0.0039041 | 0.00097847
29 | 0.0083762 | 0.0020993
30 | 0.0061887 | 0.001551
31 | 0.0043391 | 0.0010875
32 | 0.0084081 | 0.0021073
33 | 0.015189 | 0.0038068
34 | 0.01544 | 0.0038695
35 | 0.0063338 | 0.0015874
36 | 0.0090657 | 0.0022721
37 | 0.00010555 | 2.6454e-05
38 | 0.011825 | 0.0029636
39 | 0.019157 | 0.0048012
40 | 0.007292 | 0.0018275
41 | 0.026938 | 0.0067512
42 | 0.00067082 | 0.00016812
43 | 0.00052493 | 0.00013156
44 | 0.0094688 | 0.0023731
45 | 0.0079231 | 0.0019857
46 | 0.0078124 | 0.001958
47 | 0.0052296 | 0.0013107
48 | 0.0048072 | 0.0012048
49 | 0.0074633 | 0.0018705
50 | 0.0073992 | 0.0018544
51 | 0.0073786 | 0.0018492
52 | 0.0001354 | 3.3936e-05
53 | 0.0006728 | 0.00016862
54 | 0.0132 | 0.0033083
55 | 0.0049799 | 0.0012481
56 | 0.0049794 | 0.001248
57 | 0.0078237 | 0.0019608
58 | 0.017785 | 0.0044573
59 | 0.0068025 | 0.0017049

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1